## Service Orders
ID# | Description | Date Opened | Date Done | Asset | Work Order Type | Personnel Assigned to Asset(s) | Actual Hours | Outage Type | Inventory (Parts) Used | Parts Used Quantities | Down Time (hours) | Site | Comments | ID# (for duplicate search)
KRAYN-WKO-NDX-20090111-01 | MI CW Temp L warning | 2009-01-11 | 2009-01-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.3333 | Highland 1 | Arrived with 4 Renew guys to install heater. The turbine was already down due to the cold weather, and remained down after we finished. | KRAYN-WKO-NDX-20090111 | 1
KRAYN-WKO-NDX-20090111-02 | MI CW Temp L warning | 2009-01-11 | 2009-01-11 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.3333 | Highland 1 | Arrived with 2 Renew guys to install heater. The turbine was already down due to the cold weather, and remained down after we finished. | KRAYN-WKO-NDX-20090111 | 1
KRAYN-WKO-NDX-20090111-03 | Manual Stop | 2009-01-11 | 2009-01-11 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.6667 | Forced |  |  | 0.49917 | Highland 1 | 2 Renew guys installed heater. | KRAYN-WKO-NDX-20090111 | 1
KRAYN-WKO-NDX-20090111-04 | Hyd Oil Temp L Warn | 2009-01-11 | 2009-01-11 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 2.6667 | Forced |  |  | 4.8767 | Highland 1 | 2 Renew guys installed heater. The turbine was already down due to cold weather. | KRAYN-WKO-NDX-20090111 | 1
KRAYN-WKO-NDX-20090113-01 | Manual Stop | 2009-01-13 | 2009-01-13 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.9997 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090113 | 1
KRAYN-WKO-NDX-20090113-02 | Manual Stop | 2009-01-13 | 2009-01-13 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.3361 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090113 | 1
KRAYN-WKO-NDX-20090113-03 | Wind Speed unequal Power | 2009-01-13 | 2009-01-13 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 25.6667 | Forced |  |  | 10.9817 | Highland 1 | Renew Subcontractors Replaced Hydraulic Oil. Tower already down for Ice on blades | KRAYN-WKO-NDX-20090113 | 1
KRAYN-WKO-NDX-20090113-04 | Wind Speed unequal Power | 2009-01-13 | 2009-01-14 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 27.6622 | Highland 1 | Renew Subcontractors Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090113 | 1
KRAYN-WKO-NDX-20090113-05 | Manual Stop | 2009-01-13 | 2009-01-13 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 4.5 | Forced |  |  | 1.7006 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090113 | 1
KRAYN-WKO-NDX-20090114-01 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6222 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-02 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6222 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-03 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6222 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-04 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6222 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-05 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.3092 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-06 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 3.9078 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. They found that 10 Cables had Heat Shrink on them. Both Yaw Motors Turned. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-07 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.98278 | Highland 1 | Renew Subcontractors Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-08 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 2.0378 | Highland 1 | Renew Subcontractors Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-09 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 8.1667 | Forced |  |  | 3.6792 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. Found 2 Generator Cables with Heat Shrink on them. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-10 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 8.1667 | Forced |  |  | 3.6792 | Highland 1 | Renew Subcontractors Installed Retrofit Heater and Replaced Hydraulic Oil. Found 2 Generator Cables with Heat Shrink on them. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-11 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 2.2 | Forced |  |  | 0.99 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090114-12 | Manual Stop | 2009-01-14 | 2009-01-14 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 2.2 | Forced |  |  | 0.99 | Highland 1 | Renew Subcontractors Installed retrofit Heater unit and Replaced Hydraulic Oil. | KRAYN-WKO-NDX-20090114 | 1
KRAYN-WKO-NDX-20090511-01 | No work order description provided by contractor | 2009-05-11 |  | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 3.9078 | Highland 1 | Inspected nacelle and hub for defective cone bearings. | KRAYN-WKO-NDX-20090511 | 1
KRAYN-WKO-NDX-20090521-01 | vib y direction eff. Stop | 2009-05-21 | 2009-05-21 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 11.95 | Forced |  |  | 0.18333 | Highland 1 | Inspected vibration sensor, replaced sensor head connector. | KRAYN-WKO-NDX-20090521 | 1
KRAYN-WKO-NDX-20090521-02 | pitchpower volt. Fault | 2009-05-21 | 2009-05-21 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 7.3 | Forced |  |  | 3.9167 | Highland 1 | Troubleshoot and traceback to determine cause of pitch error. Found that problem is slipring, need to order part. | KRAYN-WKO-NDX-20090521 | 1
KRAYN-WKO-NDX-20090521-03 | pitchpower volt. Fault | 2009-05-21 | 2009-05-21 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 7.3 | Forced |  |  | 3.9167 | Highland 1 | Troubleshoot and traceback to determine cause of pitch error. Found that problem is slipring, need to order part. | KRAYN-WKO-NDX-20090521 | 1
KRAYN-WKO-NDX-20090527-01 | Manual stop | 2009-05-27 | 2009-05-27 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.5 | Highland 1 | Turbine was faulting for y axis vibration fault. Re routed the signal cables in top box and cable trays. To see if the signal was being interupted by other cables. | KRAYN-WKO-NDX-20090527 | 1
KRAYN-WKO-NDX-20090529-01 | pitch power volt fault | 2009-05-29 | 2009-05-29 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 6.55 | Forced |  |  | 5.8333 | Highland 1 | Replaced slip ring in hub. | KRAYN-WKO-NDX-20090529 | 1
KRAYN-WKO-NDX-20090529-02 | pitch power volt. Fault | 2009-05-29 | 2009-05-29 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 6.1 | Highland 1 | Reset the pitch 1 converter in the hub. | KRAYN-WKO-NDX-20090529 | 1
KRAYN-WKO-NDX-20090529-03 | pitch power volt. Fault | 2009-05-29 | 2009-05-29 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 6.1 | Highland 1 | Reset the pitch 1 converter in the hub. | KRAYN-WKO-NDX-20090529 | 1
KRAYN-WKO-NDX-20090601-01 | Manual stop | 2009-06-01 | 2009-06-01 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0400 | 1 | 14.55 | Highland 1 | Need to replace gearbox PT, Fuse blew on module. Rotor brake pressure fualt appeared needs more trouble shooting. Do Not put part in SAP!!! | KRAYN-WKO-NDX-20090601 | 1
KRAYN-WKO-NDX-20090601-02 | N/A | 2009-06-01 |  | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0530 | 1 | 4.0667 | Highland 1 | Replace lamp in the bottom box. Did not need to shut the turbine down. DO Not put part in SAP!!! | KRAYN-WKO-NDX-20090601 | 1
KRAYN-WKO-NDX-20090601-03 | N/A | 2009-06-01 | 2009-06-01 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.46667 | Highland 1 | Added grease to yaw system acculube container. | KRAYN-WKO-NDX-20090601 | 1
KRAYN-WKO-NDX-20090603-01 | yaw hyd no open | 2009-06-03 | 2009-06-03 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0480 | 1 | 15.8 | Highland 1 | checked out the yaw convertor and found defective. Removed and replaced yaw convertor. Run tested yaw system all good. DO Not Part in SAP!!! | KRAYN-WKO-NDX-20090603 | 1
KRAYN-WKO-NDX-20090604-01 | lp lightning protection pitch | 2009-06-04 | 2009-06-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 54 | Forced | KRAYN-NDX-PRT-0249,KRAYN-NDX-PRT-0482 | 1,4 | 64.8333 | Highland 1 | replaced litning protection module and found a defective pitch invertor. Removed and replaced and reprogramed. Now there is an I-bus problem. Tried changing digital input module but still has problem. Went up turbine to swap out part but problem is still there. troubleshot more and found the newly replaced pitch invertor defective, removed the defective part and replaced. also slipring needed cleaning so we performed task. Do not put parts in SAP | KRAYN-WKO-NDX-20090604 | 1
KRAYN-WKO-NDX-20090604-02 | lp lightning protection pitch | 2009-06-04 | 2009-06-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 54 | Forced | KRAYN-NDX-PRT-0249,KRAYN-NDX-PRT-0482 | 1,4 | 64.8333 | Highland 1 | replaced litning protection module and found a defective pitch invertor. Removed and replaced and reprogramed. Now there is an I-bus problem. Tried changing digital input module but still has problem. Went up turbine to swap out part but problem is still there. troubleshot more and found the newly replaced pitch invertor defective, removed the defective part and replaced. also slipring needed cleaning so we performed task. Do not put parts in SAP | KRAYN-WKO-NDX-20090604 | 1
KRAYN-WKO-NDX-20090608-01 | dc dc transducer 250w was defective | 2009-06-08 | 2009-06-08 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0464 | 1 | 2.3864 | Highland 1 | the turbine was faulting and was reset the problem was analyzed by the techs listed before we approched the turbine. once at the turbine we tested the faulty part to concure and proceeded to replace the part. Also while in the hub a blade cover was removed from blade 1 to remove excess ressin from the blade and noticed the lightning protection card in the blade 1 was broken. after cleaning up in the hub and exiting we noticed that grease was leaking out of the exterior blade seal and not in the interior catch cups designed to collect this grease, we cleaned up the grease and proceeded down the turbine completing the task. Do not put part in SAP!!! | KRAYN-WKO-NDX-20090608 | 1
KRAYN-WKO-NDX-20090608-02 | Pitch 1 motor sensor disturb | 2009-06-08 | 2009-06-08 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 28 | Forced | KRAYN-NDX-PRT-0076,KRAYN-NDX-PRT-0051 | 1,1 | 43 | Highland 1 | Climbed Wtg. To troubleshoot and cleaned slidering and reset pich convertor. In the process of riding the man lift the cable guide got stuck so while fixing that the turbine ran for about 2 hrs. and faulted again. Called comm. And they said they would provide one the following day. Drove to WTG and was running. Fixed manlift cable guide, and reassigned IP addess on new pitch convertor to have ready just incase the turbine has another problem.swapped pitch convertor and found problem still excists. Do Not Put Parts in SAP!!! | KRAYN-WKO-NDX-20090608 | 1
KRAYN-WKO-NDX-20090608-03 | Pitch 1 motor sensor disturb | 2009-06-08 | 2009-06-08 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 28 | Forced | KRAYN-NDX-PRT-0076,KRAYN-NDX-PRT-0051 | 1,1 | 43 | Highland 1 | Climbed Wtg. To troubleshoot and cleaned slidering and reset pich convertor. In the process of riding the man lift the cable guide got stuck so while fixing that the turbine ran for about 2 hrs. and faulted again. Called comm. And they said they would provide one the following day. Drove to WTG and was running. Fixed manlift cable guide, and reassigned IP addess on new pitch convertor to have ready just incase the turbine has another problem.swapped pitch convertor and found problem still excists. Do Not Put Parts in SAP!!! | KRAYN-WKO-NDX-20090608 | 1
KRAYN-WKO-NDX-20090611-01 | IBS Interbus Stop | 2009-06-11 | 2009-11-06 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.0333 | Highland 1 | WTG went down on a pitch com fault , found faulty slipring. | KRAYN-WKO-NDX-20090611 | 1
KRAYN-WKO-NDX-20090611-02 | No work order description provided by contractor | 2009-06-11 | 2009-06-11 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.75 | Highland 1 | Installed the pitch converter control cabinet door on # 3. | KRAYN-WKO-NDX-20090611 | 1
KRAYN-WKO-NDX-20090612-01 | No work order description provided by contractor | 2009-06-12 | 2009-06-12 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.66667 | Highland 1 | inspection of man lift at turbine, also inspection of hv cables @ yaw deck | KRAYN-WKO-NDX-20090612 | 1
KRAYN-WKO-NDX-20090612-02 | inspection | 2009-06-12 | 2009-06-12 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 2.65 | Highland 1 | repaired a service lift damaged by WES wich was stuck half way up tower. Stoped turbine winds where low at the time proceeded to repair main power cord from mid tower was not able to, removed old power cable then replaced with new one. | KRAYN-WKO-NDX-20090612 | 1
KRAYN-WKO-NDX-20090612-03 | inspection | 2009-06-12 | 2009-06-12 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 2.65 | Highland 1 | repaired a service lift damaged by WES wich was stuck half way up tower. Stoped turbine winds where low at the time proceeded to repair main power cord from mid tower was not able to, removed old power cable then replaced with new one. | KRAYN-WKO-NDX-20090612 | 1
KRAYN-WKO-NDX-20090613-01 | fm744= interbus quality error/XZ vibration fault also occurs | 2009-06-13 | 2009-06-13 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 12 | Forced |  |  | 3 | Highland 1 | Turbine faults occassionally for interbus quality error FM744 and for a problem with the vibration cable. We rerouted this cable due to frequency interference. Interbus quality error was caused by the slipring interbus connection was loose so we added a 2 washers 1 on each side of the connector in the slipring and cleaned affected areas. Returned to service. | KRAYN-WKO-NDX-20090613 | 1
KRAYN-WKO-NDX-20090615-01 | Yaw Hyd Brk not closed | 2009-06-15 | 2009-06-15 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 25.5 | Forced |  |  | 29.0167 | Highland 1 | Swapped out yaw convertor and it did not fix problem. Found that the pressure was bleeding off. Removed Hyd station motor and found that the hose had a hole in it. Had to get a hose made. | KRAYN-WKO-NDX-20090615 | 1
KRAYN-WKO-NDX-20090616-01 | Manual Stop | 2009-06-16 | 2009-06-16 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 12 | Forced |  |  | 2.1167 | Highland 1 | Replaced pitch drive cable on pitch drive number 1. The part was from the commissioning stock. The turbine was faulting every so often for pitch motor sensor error. | KRAYN-WKO-NDX-20090616 | 1
KRAYN-WKO-NDX-20090616-02 | Manual Stop | 2009-06-16 | 2009-06-16 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 12 | Forced |  |  | 2.1167 | Highland 1 | Replaced pitch drive cable on pitch drive number 1. The part was from the commissioning stock. The turbine was faulting every so often for pitch motor sensor error. | KRAYN-WKO-NDX-20090616 | 1
KRAYN-WKO-NDX-20090618-01 | replaced vib sensor | 2009-06-18 | 2009-06-18 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 1 | Highland 1 | turbine 6 has been having a vibration issue for a number of days. we do not have the parts so we replaced the sensor with turbine 5 and changed perameters to adjust the offset to keep the turbine in production until a new DMT sensor arrived from germany. | KRAYN-WKO-NDX-20090618 | 1
KRAYN-WKO-NDX-20090618-02 | Vib. Y direction filtered stop | 2009-06-18 | 2009-06-18 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 3 | Highland 1 | Swapped vibration sensors From different Wtg. Found the ground was not terminated and power supply needed adjusted. | KRAYN-WKO-NDX-20090618 | 1
KRAYN-WKO-NDX-20090619-01 | Manual Stop | 2009-06-19 | 2009-06-19 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0004 | 2 | 1.0333 | Highland 1 | Replaced Lightning brushes on main shaft. | KRAYN-WKO-NDX-20090619 | 1
KRAYN-WKO-NDX-20090619-02 | Manual Stop | 2009-06-19 | 2009-06-19 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0004 | 2 | 1.5 | Highland 1 | Replaced Lightning brushes on main shaft. We also checked generator bearing pt. Found they were good so we swapped anolog output modules. | KRAYN-WKO-NDX-20090619 | 1
KRAYN-WKO-NDX-20090622-01 | yaw motor not open | 2009-06-22 | 2009-06-22 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 9 | Forced | KRAYN-NDX-PRT-0480 | 1 | 4.5 | Highland 1 | changed out yaw convertor. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090622 | 1
KRAYN-WKO-NDX-20090623-01 | No work order description provided by contractor | 2009-06-23 | 2009-06-23 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0030 | 1 | 4 | Highland 1 | Re-routed and landed the vibration sensor. Changed the wind speed sensor,it was missing tip. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090623 | 1
KRAYN-WKO-NDX-20090623-02 | Yaw motor brake not open | 2009-06-23 | 2009-06-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 112.1 | Highland 1 | Yaw convertor keeps getting wet. Checked top cab cooler it was not wet and changed the temp setting. Turbine was left down due to no yaw convertors in stock. | KRAYN-WKO-NDX-20090623 | 1
KRAYN-WKO-NDX-20090625-01 | Pitch angle 1 diff, set-act | 2009-06-25 | 2009-06-25 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0909 | 1 | 24.7 | Highland 1 | Changed out th pitch convertor and did the pitch test all worked fine. Turbine Faulted for the same fault so changed out the pitch cable number 1. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090625 | 1
KRAYN-WKO-NDX-20090625-02 | Pitch angle 1 diff, set-act | 2009-06-25 | 2009-06-25 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0909 | 1 | 24.7 | Highland 1 | Changed out th pitch convertor and did the pitch test all worked fine. Turbine Faulted for the same fault so changed out the pitch cable number 1. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090625 | 1
KRAYN-WKO-NDX-20090627-01 | burnt out hv cables | 2009-06-27 | 2009-06-27 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 19 | Forced |  |  | 49 | Highland 1 | high voltage cables where damaged on the rotor side from over heating or a bad connection at deck number two. these cables where cut out and replaced with approval of engineering, this turbine is currently running at half power. | KRAYN-WKO-NDX-20090627 | 1
KRAYN-WKO-NDX-20090629-01 | vib z and vib y direction eff. Stop | 2009-06-29 | 2009-06-29 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0967 | 1 | 3.8 | Highland 1 | changed out the vibration sensor on the bedplate. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090629 | 1
KRAYN-WKO-NDX-20090630-01 | vib z and vib y direction eff. Stop | 2009-06-30 | 2009-06-30 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0967 | 1 | 1.35 | Highland 1 | changed out the vibration sensor on the bedplate. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090630 | 1
KRAYN-WKO-NDX-20090702-01 | yaw invertor fault | 2009-07-02 | 2009-07-17 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 354 | Highland 1 | the fault was present the yaw convertor was disconected and reconnected to perform a hard reset. The relays had no power and the contactors could not be forced to allow the turbine to yaw the lack of voltage was through the yaw convertor wich will need to be replaced. there is no convertors on site an order was put in for them. | KRAYN-WKO-NDX-20090702 | 1
KRAYN-WKO-NDX-20090706-01 | Wtg was down | 2009-07-06 |  | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 14 | Forced | KRAYN-NDX-PRT-0412 | 1 | 3.6792 | Highland 1 | WTG. Was Down due to gearbox radiator needed replaced and the yaw convertor. Removed and replaced gearbox radiator. Went up the next day and cleaned the oil in the turbine. | KRAYN-WKO-NDX-20090706 | 1
KRAYN-WKO-NDX-20090706-02 | Yaw hydraulic brake not closed | 2009-07-06 | 2009-07-06 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 4.7333 | Highland 1 | Found contactor stuck open for the yaw hydraulic brake. Manually engaged contactor to free from being stuck and cleaned residual dust from points of contact within the contactor itself. Reset turbine and test, ok. | KRAYN-WKO-NDX-20090706 | 1
KRAYN-WKO-NDX-20090707-01 | Manual Stop | 2009-07-07 | 2009-07-07 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 1 | Highland 1 | Had to remove and replace manlift cable. The next day Turbine was allready shut down due to maint. , finished performing task at hand. | KRAYN-WKO-NDX-20090707 | 1
KRAYN-WKO-NDX-20090709-01 | blade seal fix | 2009-07-09 | 2009-07-09 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.3667 | Highland 1 | the turbine had a broken blade seal externaly all grease was cleaned the old section of the seal was cut out and replaced and bonded with new seal | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-02 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 24.7 | Highland 1 | Turbine was down due to coupling bad. Removed the yaw convertor for Wtg. 8.. In the process of leaving turbine found leak on the hydr. Station line , cleaned up and tightned the fitting and will go back for further inspection of fitting. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-03 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 24.7 | Highland 1 | Turbine was down due to coupling bad. Removed the yaw convertor for Wtg. 8.. In the process of leaving turbine found leak on the hydr. Station line , cleaned up and tightned the fitting and will go back for further inspection of fitting. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-04 | Turbine down | 2009-07-09 | 2009-08-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 9 | Forced | 0,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | Checked Brake Disc axel readings with dial indicator and installed covers. Do Not Put in SAP!!! | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-05 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 61 | Forced | 0,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | .Replaced KTR coupling and brake disc. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-06 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 61 | Forced | 0,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | .Replaced KTR coupling and brake disc. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-07 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 24.7 | Highland 1 | Turbine was down due to coupling bad. Removed the yaw convertor for Wtg. 8.. In the process of leaving turbine found leak on the hydr. Station line , cleaned up and tightned the fitting and will go back for further inspection of fitting. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-08 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 24.7 | Highland 1 | Turbine was down due to coupling bad. Removed the yaw convertor for Wtg. 8.. In the process of leaving turbine found leak on the hydr. Station line , cleaned up and tightned the fitting and will go back for further inspection of fitting. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-09 | Turbine down | 2009-07-09 | 2009-08-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 9 | Forced | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | Checked Brake Disc axel readings with dial indicator and installed covers. Do Not Put in SAP!!! | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-10 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 61 | Forced | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | .Replaced KTR coupling and brake disc. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-11 | Turbine down | 2009-07-09 |  | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 61 | Forced | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0720 | 1,1 | 24.7 | Highland 1 | .Replaced KTR coupling and brake disc. | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090709-12 | replaced blockstop | 2009-07-09 | 2009-07-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.7 | Highland 1 | the turbine had a defective blockstop on the man lift this was replaced with a new part | KRAYN-WKO-NDX-20090709 | 1
KRAYN-WKO-NDX-20090713-01 | replaced lift cable | 2009-07-13 | 2009-07-13 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 1.6667 | Highland 1 | the turbine had a torn 400v power cable this cable was removed and replaced with a new cable. | KRAYN-WKO-NDX-20090713 | 1
KRAYN-WKO-NDX-20090714-01 | Manual Stop | 2009-07-14 | 2009-07-14 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6333 | Highland 1 | Stopped wind turbine to show Nordex Personel the cooling unit and some other problems we have with the wtg. | KRAYN-WKO-NDX-20090714 | 1
KRAYN-WKO-NDX-20090715-01 | Yaw Motor BRK Not Open | 2009-07-15 | 2009-07-16 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0486 | 3 | 248.2833 | Highland 1 | Troubleshoot Yaw convertor problem and found bad fuses. Replaced fuses and returned turbine to service. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090715 | 1
KRAYN-WKO-NDX-20090715-02 | No work order description provided by contractor | 2009-07-15 |  | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 9 | Forced |  |  | 5.8333 | Highland 1 | Replaced yaw converter, removed lower set of shrouds over high speed shaft, found coolant leak at pump from bypass pressure valve, too much coolant loss to run turbine at this time, found fuses blown on yaw motor curcuit. | KRAYN-WKO-NDX-20090715 | 1
KRAYN-WKO-NDX-20090715-03 | No Fault | 2009-07-15 | 2009-07-15 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 196.0333 | Highland 1 | Changed Yaw Convertor, The yaw convertor that was in wtg 20 is now in wtg 16. WTG.20 was never faulted, Everpower was performing a punch list inspection and found a leak on the gearbox cooler due to this the turbine was shut down. | KRAYN-WKO-NDX-20090715 | 1
KRAYN-WKO-NDX-20090716-01 | bad 690v | 2009-07-16 | 2009-07-16 | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 499.6167 | Highland 1 | yaw convertor was replaced also 660v fuses where replaced, turbine also needed anti freeze for gen cooling system this was added to proper bar and turbine was started | KRAYN-WKO-NDX-20090716 | 1
KRAYN-WKO-NDX-20090716-02 | yaw moter break not open | 2009-07-16 | 2009-07-15 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0486 | 3 | 127.1667 | Highland 1 | turbine was down for bad yaw convertor went up turbine checked convertor and changed out 660v 40amp fuses turbine is running. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090716 | 1
KRAYN-WKO-NDX-20090716-03 | yaw moter break not open | 2009-07-16 | 2009-07-15 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0486 | 3 | 127.1667 | Highland 1 | turbine was down for bad yaw convertor went up turbine checked convertor and changed out 660v 40amp fuses turbine is running. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090716 | 1
KRAYN-WKO-NDX-20090716-04 | Yaw invertor fault | 2009-07-16 | 2009-07-16 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 6 | Forced |  |  | 346.6333 | Highland 1 | Turbine was down due to no yaw convertors in stock. Replaced yaw convertor and yawed turbine to check, ok. Turbine was not started after job due to WES working in turbine. | KRAYN-WKO-NDX-20090716 | 1
KRAYN-WKO-NDX-20090720-01 | Manual Stop | 2009-07-20 | 2009-07-21 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 48 | Forced | KRAYN-NDX-PRT-0335 | 16 | 31 | Highland 1 | Making Loud squeeling and grinding noises while yawing. Cleaned Brake calipers and Brake disc and changed Brake pads. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090720 | 1
KRAYN-WKO-NDX-20090722-01 | Manual Stop | 2009-07-22 | 2009-07-22 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 15 | Forced |  |  | 6.3667 | Highland 1 | Had to replace 2 of the generator cables in tower. | KRAYN-WKO-NDX-20090722 | 1
KRAYN-WKO-NDX-20090728-01 | low hydraulic oil | 2009-07-28 | 2009-07-28 | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 6.9167 | Highland 1 | turbine 18 faulted due to low hydraulic oil, Refilled oil resevoirwith hydraulic fluid. oil leak is at yaw break caliper new part was ordered and turbine is currently running | KRAYN-WKO-NDX-20090728 | 1
KRAYN-WKO-NDX-20090730-01 | vibration z an y | 2009-07-30 | 2009-07-30 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0172 | 1 | 0.7 | Highland 1 | the turbine had faulted for a vibration problem the vibration sensor was replaced and the values where adjusted to meet the correct settings. Do Not Put Parts in SAP!!! | KRAYN-WKO-NDX-20090730 | 1
KRAYN-WKO-NDX-20090808-01 | Manual stop | 2009-08-08 | 2009-08-09 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.65 | Highland 1 | Wes was performing maint. And the rotor lock out pin was stuck and they could not get it out. The rotor brake was activated and would not release. Removed sensor cover and checked wire connection and checked fuses on mod. 105/A3 . Found loose conn. And put wtg. to run. | KRAYN-WKO-NDX-20090808 | 1
KRAYN-WKO-NDX-20090810-01 | LP (Lightn prot) pwr cab | 2009-08-10 | 2009-08-10 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3.2 | Forced | KRAYN-NDX-PRT-0316 | 1 | 1.0167 | Highland 1 | trouble shot lightning protection fault, returned the next day to trouble shoot warning and found di module 105a3 was only receiving 10.89 volts dc. Removed and replaced power supply. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090810 | 1
KRAYN-WKO-NDX-20090810-02 | LP (Lightn prot) pwr cab | 2009-08-10 | 2009-08-10 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3.2 | Forced | KRAYN-NDX-PRT-0316 | 1 | 1.0167 | Highland 1 | trouble shot lightning protection fault, returned the next day to trouble shoot warning and found di module 105a3 was only receiving 10.89 volts dc. Removed and replaced power supply. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090810 | 1
KRAYN-WKO-NDX-20090810-03 | No work order description provided by contractor | 2009-08-10 | 2009-08-10 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.6 | Forced |  |  | 0.8 | Highland 1 | Taking pictures of yaw ring for oil | KRAYN-WKO-NDX-20090810 | 1
KRAYN-WKO-NDX-20090812-01 | No work order description provided by contractor | 2009-08-12 | 2009-08-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6.3667 | Forced | KRAYN-NDX-PRT-0031 | 1 | 3.1833 | Highland 1 | turbine 5 faulted with a fe500 8-9-09 after resolving the problem, disabling the anemometer solved the problem. 8-12 work performed was replacing anemometer with a new part | KRAYN-WKO-NDX-20090812 | 1
KRAYN-WKO-NDX-20090812-02 | No work order description provided by contractor | 2009-08-12 | 2009-08-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6.3667 | Forced | KRAYN-NDX-PRT-0031 | 1 | 3.1833 | Highland 1 | turbine 5 faulted with a fe500 8-9-09 after resoliving the problem disabling the anemometer solved the problem. 8-12 work performed was replacing anemometer with a new part | KRAYN-WKO-NDX-20090812 | 1
KRAYN-WKO-NDX-20090814-01 | rotor break hold pressure | 2009-08-14 | 2009-08-13 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 5.8667 | Forced |  |  | 2.9333 | Highland 1 | the turbine is faulting out during its rotor brake test phase upon start up, (troubleshooting) parts ordered | KRAYN-WKO-NDX-20090814 | 1
KRAYN-WKO-NDX-20090815-01 | top cabinet overheat | 2009-08-15 |  | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 29.0167 | Highland 1 | turbine had faulted with a top cabinet overheat, went up and turned on air conditioners and fans | KRAYN-WKO-NDX-20090815 | 1
KRAYN-WKO-NDX-20090815-02 | top cabinet overheat | 2009-08-15 | 2009-08-15 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.4 | Forced |  |  | 7 | Highland 1 | turbine had over heated in top cabinet, went up turbine turned on air conditioner and fan | KRAYN-WKO-NDX-20090815 | 1
KRAYN-WKO-NDX-20090815-03 | top cabinet overheat | 2009-08-15 | 2009-08-15 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.1667 | Forced |  |  | 5.9 | Highland 1 | turbine over heated in the top box climbed up turbine turned on breaker for the cooling unit and fans | KRAYN-WKO-NDX-20090815 | 1
KRAYN-WKO-NDX-20090817-01 | Gen RPM monitor cable cut | 2009-08-17 | 2009-08-17 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0571 | 1 | 31.3167 | Highland 1 | Wes damaged rotor speed sensor. Changed sensor but the conn. Was damaged and we have none in stock, so had to tape to hold sensor. Found a way to keep sensor cable on sensor for the time being until new one is ordered. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20090817 | 1
KRAYN-WKO-NDX-20090817-02 | Gen Rot RpmDiff H stop | 2009-08-17 | 2009-08-17 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 38.8 | Forced |  |  | 18.1333 | Highland 1 | Tighten the shield on the generator speed sensor and changed the module, but did not help. Adjusted Rotor sensors and monitored wtg. For one hour all fine. | KRAYN-WKO-NDX-20090817 | 1
KRAYN-WKO-NDX-20090824-01 | ibs com fault | 2009-08-24 | 2009-08-24 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 4.4333 | Highland 1 | turbine faulted out for loss of coms In the hub we checked slipring and added washers at the db connector at the slipring and started turbine back up. | KRAYN-WKO-NDX-20090824 | 1
KRAYN-WKO-NDX-20090824-02 | ibs com fault | 2009-08-24 | 2009-08-24 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 4.4333 | Highland 1 | turbine faulted out for loss of coms In the hub we checked slipring and added washers at the db connector at the slipring and started turbine back up. | KRAYN-WKO-NDX-20090824 | 1
KRAYN-WKO-NDX-20090825-01 | Manual Stop | 2009-08-25 | 2009-08-26 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 53.5 | Forced | 0 | 27 | 26.2833 | Highland 1 | Clean yaw brake disc and calipers and replaced brake pads. | KRAYN-WKO-NDX-20090825 | 1
KRAYN-WKO-NDX-20090825-02 | Manual Stop | 2009-08-25 | 2009-08-26 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 53.5 | Forced | 0 | 27 | 26.2833 | Highland 1 | Clean yaw brake disc and calipers and replaced brake pads. | KRAYN-WKO-NDX-20090825 | 1
KRAYN-WKO-NDX-20090826-01 | ups battery change | 2009-08-26 | 2009-08-26 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 1.2667 | Forced | KRAYN-NDX-PRT-0293 | 1 | 0.63333 | Highland 1 | turbine gave a warning fault saying problem occurred with ups battery, we traded out the battery of the ups and started the turbine up. | KRAYN-WKO-NDX-20090826 | 1
KRAYN-WKO-NDX-20090829-01 | Manual Stop | 2009-08-29 | 2009-08-29 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.1 | Forced | KRAYN-NDX-PRT-0155 | 1 | 0.55 | Highland 1 | Turbine was going down on FM 364 pitch power volt is off fault, Removed and replaced 101k1 contactor. Do Not put Part in SAP!!! | KRAYN-WKO-NDX-20090829 | 1
KRAYN-WKO-NDX-20090830-01 | MI class C fault | 2009-08-30 | 2009-08-31 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 72 | Forced | KRAYN-NDX-PRT-0639,KRAYN-NDX-PRT-0671,KRAYN-NDX-PRT-0644 | 1,1,2 | 39.4333 | Highland 1 | Troubleshoot MI Class C fault and found FIT board defective, removed and replaced fit board. Class C fault went away but Ringline fault is present. Found defective fuses and IGBT Removed and Replaced. Do Not Put Parts in SAP!!! | KRAYN-WKO-NDX-20090830 | 1
KRAYN-WKO-NDX-20090902-01 | Manual stop | 2009-09-02 | 2009-09-02 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 11.4 | Forced |  |  | 2 | Highland 1 | Troubleshoot IBS BUS Quality Warning , needs further troubleshooting possibly slipring or pitch 1 convertor. Ran Diag. plus and found seg.25 had over 1000 transmision faults, Swapped out pitch convertor. | KRAYN-WKO-NDX-20090902 | 1
KRAYN-WKO-NDX-20090902-02 | Manual stop | 2009-09-02 | 2009-09-02 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 11.4 | Forced |  |  | 2 | Highland 1 | Troubleshoot IBS BUS Quality Warning , needs further troubleshooting possibly slipring or pitch 1 convertor. Ran Diag. plus and found seg.25 had over 1000 transmision faults, Swapped out pitch convertor. | KRAYN-WKO-NDX-20090902 | 1
KRAYN-WKO-NDX-20090904-01 | Manual Stop | 2009-09-04 | 2009-09-04 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 9.2333 | Forced |  |  | 4.6167 | Highland 1 | Cleaned yaw brake system and turbine. Installed protectve strip on tube for generator cables. | KRAYN-WKO-NDX-20090904 | 1
KRAYN-WKO-NDX-20090908-01 | Manual Stop | 2009-09-08 | 2009-09-08 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4.2333 | Forced |  |  | 2.1167 | Highland 1 | Replaced Man lift cable and had to adjust power cable guide. Added coolant to generator and installed edge guard around powercable tube. | KRAYN-WKO-NDX-20090908 | 1
KRAYN-WKO-NDX-20090908-02 | Manual Stop | 2009-09-08 | 2009-09-08 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4.2333 | Forced |  |  | 2.1167 | Highland 1 | Replaced Man lift cable and had to adjust power cable guide. Added coolant to generator and installed edge guard around powercable tube. | KRAYN-WKO-NDX-20090908 | 1
KRAYN-WKO-NDX-20090911-01 | Walk Down | 2009-09-11 | 2009-09-11 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.097222 | Forced |  |  | 0.10417 | Highland 1 | Walk down insp. | KRAYN-WKO-NDX-20090911 | 1
KRAYN-WKO-NDX-20090911-02 | Walk down insp. | 2009-09-11 | 2009-09-11 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.14583 | Forced |  |  | 0.048611 | Highland 1 | Walkdown inspection and installed edge guard. | KRAYN-WKO-NDX-20090911 | 1
KRAYN-WKO-NDX-20090912-01 | Manual Stop | 2009-09-12 | 2009-09-12 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 2.3333 | Forced |  |  | 1.1667 | Highland 1 | Walk down inspection for Everpower and installed edge guard for power cable tube. | KRAYN-WKO-NDX-20090912 | 1
KRAYN-WKO-NDX-20090912-02 | Pitch Angle 2 diff.act red act | 2009-09-12 | 2009-09-16 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 5.7333 | Highland 1 | Adjusted the reduntant value and found pitch encoder was jumping so pulled it back from the pitch blade teeth. | KRAYN-WKO-NDX-20090912 | 1
KRAYN-WKO-NDX-20090912-03 | Manual Stop | 2009-09-12 | 2009-09-12 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 2.3667 | Forced |  |  | 1.1833 | Highland 1 | Walk down inspection for Everpower and installed edge guard for power cable tube. | KRAYN-WKO-NDX-20090912 | 1
KRAYN-WKO-NDX-20090913-01 | FM 700 | 2009-09-13 | 2009-09-13 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.020833 | Highland 1 | Found loose fiber in top box. | KRAYN-WKO-NDX-20090913 | 1
KRAYN-WKO-NDX-20090913-02 | Inter-Bus Stop | 2009-09-13 | 2009-09-13 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 9.3 | Forced |  |  | 4.1 | Highland 1 | Troubleshoot inter-bus fault and found loose fibers in the top box. | KRAYN-WKO-NDX-20090913 | 1
KRAYN-WKO-NDX-20090914-01 | Manual Stop | 2009-09-14 | 2009-09-14 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 5.9667 | Forced |  |  | 2.9833 | Highland 1 | Stopped wtg. Because the wind turbine was faulting on pitch 2 battery defect. Swapped battery charger from blade 1 and blade 2 to see if charger is defective. | KRAYN-WKO-NDX-20090914 | 1
KRAYN-WKO-NDX-20090916-01 | Pitch 3 not ready | 2009-09-16 | 2009-09-16 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 30 | Forced |  |  | 26.0167 | Highland 1 | Troubleshoot pitch 3 not ready fault and found pitch convertor faulty, Had to adjust blade reduntant value. | KRAYN-WKO-NDX-20090916 | 1
KRAYN-WKO-NDX-20090920-01 | pitch 2 red. Diff | 2009-09-20 | 2009-09-20 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 8.3167 | Highland 1 | turbine faulted for a encoder diffrence on pitch one, we re adjusted the cam encoder and reset the values on blade 2 | KRAYN-WKO-NDX-20090920 | 1
KRAYN-WKO-NDX-20090920-02 | Pitchangle 2 Diff. Act-Red Act | 2009-09-20 | 2009-09-20 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 7.4333 | Highland 1 | Found Turbine 15 down for FM1142, found Pitch 2 redundant box loose and misaligned. Re adjusted pitch 2 redundant box, Returned turbine to service. Called Dan Ihle to reset MI Class B Fault. | KRAYN-WKO-NDX-20090920 | 1
KRAYN-WKO-NDX-20090926-01 | MI class B | 2009-09-26 | 2009-09-26 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 3.2569 | Forced |  |  | 0 | Highland 1 | Troubleshot SEG coverters and pulled triggers, Had to leave turbine down till next day. | KRAYN-WKO-NDX-20090926 | 1
KRAYN-WKO-NDX-20090928-01 | gearbox fan 2 trip - gearbox sump oil hot | 2009-09-28 | 2009-09-28 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 12.1 | Forced |  |  | 7.1667 | Highland 1 | turbine had falted for fuse tripped on a gearbox radaitor cooling fan bad wire was found | KRAYN-WKO-NDX-20090928 | 1
KRAYN-WKO-NDX-20090929-01 | FM262 rotor break hold pressure fault | 2009-09-29 | 2009-09-29 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 4.0667 | Forced |  |  | 0.9 | Highland 1 | replaced a bad accumulator on the hydraulic station | KRAYN-WKO-NDX-20090929 | 1
KRAYN-WKO-NDX-20090930-01 | MI class B | 2009-09-30 | 2009-09-30 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 15.5 | Forced | KRAYN-NDX-PRT-0639 | 1 | 2.2667 | Highland 1 | SEG informed technicians to change back the flat cables that were swaped prior and to swap 1.2 and 2.1 and to change fit board. Current levels on the grid side look much better. Will swap cables back during maint. Of convertors. 10/01/09 Machine thought the Q 10 breaker was still connected to grid but it was not. we checked the feedback from the Q 10 breaker and there was no signal coming back to the HUR. We took some triggers for SEG and sent them off. Reset the HUR by means of removing the 24 volt power supply and put the turbine to run. DO Not Put PArt in SAP!!! | KRAYN-WKO-NDX-20090930 | 1
KRAYN-WKO-NDX-20090930-02 | 24WEA80816 Gear fan2 fuse trip | 2009-09-30 | 2009-09-30 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.21528 | Forced |  |  | 0.083333 | Highland 1 | Gearbox cooling fan2 fuse trip. | KRAYN-WKO-NDX-20090930 | 1
KRAYN-WKO-NDX-20091001-01 | 16WEA80823 - Bad Slipring | 2009-10-01 | 2009-10-01 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.41667 | Forced |  |  | 0.21528 | Highland 1 | Troubleshot pitch com fault and found faulty slipring. | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-02 | IBS Pitch Com Fault | 2009-10-01 | 2009-10-01 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0725 | 1 | 4.8333 | Highland 1 | Cleaned slipring in hub and tried to reset and all three blades faulted for a com fault, removed and replaced slipring. | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-03 | IBS Pitch Com Fault | 2009-10-01 | 2009-10-01 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0725 | 1 | 4.8333 | Highland 1 | Cleaned slipring in hub and tried to reset and all three blades faulted for a com fault, removed and replaced slipring. | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-04 | maintenance | 2009-10-01 | 2009-10-01 | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 1.45 | Highland 1 | we went up the turbine to complete maintenance | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-05 | maintenance | 2009-10-01 | 2009-10-01 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 1.45 | Highland 1 | complete type 2 maintenance | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-06 | pitch 2 battery defect | 2009-10-01 | 2009-10-01 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.6667 | Forced |  |  | 4.25 | Highland 1 | the turbine went down for pitch 2 battery defect, batteries had been check prior to us going up as well as the charger for that blade. we swaped pitch convertors to narrow down the problem, problem is still there next we will load test the batteries | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091001-07 | pitch 2 battery defect | 2009-10-01 | 2009-10-01 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.6667 | Forced |  |  | 4.25 | Highland 1 | the turbine went down for pitch 2 battery defect, batteries had been check prior to us going up as well as the charger for that blade. we swaped pitch convertors to narrow down the problem, problem is still there next we will load test the batteries | KRAYN-WKO-NDX-20091001 | 1
KRAYN-WKO-NDX-20091002-01 | Pitch1 DC convertor 240v fault | 2009-10-02 | 2009-10-02 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 11 | Forced |  |  | 12.7833 | Highland 1 | Went to the WTG and seen blade 1 was stuck in the 0 pitch postion, in the process of reseting the pitch convertor the blade came back to the 90 degree pitch postion. Checked all fuses and the digital input in cab 3 and all checked fine. Performed a pitch test to see if all stops would be reached and all checked fine. Checked the pitch angle and the reduntant levels were in line with each other and run tested the wind turbine all checks fine. | KRAYN-WKO-NDX-20091002 | 1
KRAYN-WKO-NDX-20091005-01 | interbus stop | 2009-10-05 | 2009-10-05 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 8.6 | Highland 1 | turbine faulted for interbus problems the slipring was giving com loss to top cabinet we removed the slipring checked all connections in hub and reassembled all. | KRAYN-WKO-NDX-20091005 | 1
KRAYN-WKO-NDX-20091005-02 | Manual Stop | 2009-10-05 | 2009-10-05 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 15.8667 | Forced |  |  | 6.0167 | Highland 1 | Type 2 maint. And troubleshot yaw auto lubrication warning, found bad relay. 10/09/09 Performed walkdown insp., and finished type 2 maint.. | KRAYN-WKO-NDX-20091005 | 1
KRAYN-WKO-NDX-20091005-03 | Manual Stop | 2009-10-05 | 2009-10-05 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 15.8667 | Forced |  |  | 6.0167 | Highland 1 | Type 2 maint. And troubleshot yaw auto lubrication warning, found bad relay. 10/09/09 Performed walkdown insp., and finished type 2 maint.. | KRAYN-WKO-NDX-20091005 | 1
KRAYN-WKO-NDX-20091005-04 | yaw motor break not open | 2009-10-05 | 2009-10-05 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 1.2167 | Highland 1 | the turbine faulted for micro switch out of adjusted we cleaned the micro switch put the switch back together back in proper adjustment turbine is running | KRAYN-WKO-NDX-20091005 | 1
KRAYN-WKO-NDX-20091006-01 | LV Diff Curr 400 V stop | 2009-10-06 | 2009-10-06 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 9.3 | Forced | KRAYN-NDX-PRT-0725 | 1 | 8.2667 | Highland 1 | Found Breaker tripped in bottom cab for 400vac for up tower troubleshot 400vac in pitch and found faulty slipring. Removed and replaced slipring | KRAYN-WKO-NDX-20091006 | 1
KRAYN-WKO-NDX-20091006-02 | LV Diff Curr 400 V stop | 2009-10-06 | 2009-10-06 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 9.3 | Forced | KRAYN-NDX-PRT-0725 | 1 | 8.2667 | Highland 1 | Found Breaker tripped in bottom cab for 400vac for up tower troubleshot 400vac in pitch and found faulty slipring. Removed and replaced slipring | KRAYN-WKO-NDX-20091006 | 1
KRAYN-WKO-NDX-20091006-03 | Pitch Angle2 Diff Set Red Act | 2009-10-06 | 2009-10-06 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 7.95 | Forced |  |  | 17.6833 | Highland 1 | Reset the Hub by Shuting of 400vac pitch supply and 230vac supply. Checked reduntant values and pitch tested the blades all checked good. | KRAYN-WKO-NDX-20091006 | 1
KRAYN-WKO-NDX-20091007-01 | safty chain activated | 2009-10-07 | 2009-10-07 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 1.9333 | Forced |  |  | 5.35 | Highland 1 | turbine faulted out for gen speed diff to set, we went up and reset the safty chain then adjusted the prox switches, reset the speed controls checked them for bad fuses and started turbine up | KRAYN-WKO-NDX-20091007 | 1
KRAYN-WKO-NDX-20091007-02 | gen overspeed | 2009-10-07 | 2009-10-07 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.55 | Highland 1 | turbine faulted due to high winds with a gen overspeed we went up tower readjusted the prox sensors at bolth high speed side and low speed side, checked the speed control monitoring system and checked all our shielding terminals, also checked our centa coupling for slips | KRAYN-WKO-NDX-20091007 | 1
KRAYN-WKO-NDX-20091007-03 | gen cooler fuse trip | 2009-10-07 |  | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 5.1667 | Forced |  |  | 1.2167 | Highland 1 | the turbine faulted for gen cooler fuse trip, we found that the cooler pump for the generator has blown a seal, 10-8 removed pump and attempting to get a new seal | KRAYN-WKO-NDX-20091007 | 1
KRAYN-WKO-NDX-20091008-01 | yaw hyd brk not open | 2009-10-08 | 2009-10-08 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3.2 | Forced |  |  | 19.3 | Highland 1 | Ran hydraulic station and heard oil running back to tank found hose off of hyd. Motor defective. Removed and replaced hose and run tested hyd station. The hose was not out of Nordex stock it was bought from local distributor. | KRAYN-WKO-NDX-20091008 | 1
KRAYN-WKO-NDX-20091008-02 | yaw motor breaks not open | 2009-10-08 | 2009-10-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 10.8 | Forced |  |  | 2.4333 | Highland 1 | turbine faulted for wind direction slanting but previous FM on turbine logs showed a problem with yaw motor breaks not open. Yaw motor W123 breaks looked to open less than motor number 2 cleaned bolth breaks from all dust also micro switch. manual yawed the turbine and inspected the invertor for possible problems then started turbine. | KRAYN-WKO-NDX-20091008 | 1
KRAYN-WKO-NDX-20091009-01 | Manual Stop | 2009-10-09 | 2009-10-09 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 5.1333 | Forced |  |  | 2.5667 | Highland 1 | Performed type 2 Maint. | KRAYN-WKO-NDX-20091009 | 1
KRAYN-WKO-NDX-20091012-01 | IBS Inter-bus Stop | 2009-10-12 | 2009-10-12 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 13 | Forced | KRAYN-NDX-PRT-0725 | 1 | 11.6833 | Highland 1 | Troubleshoot WTG and found slipring defective and in the process of changing the slipring we found damage to serial port. | KRAYN-WKO-NDX-20091012 | 1
KRAYN-WKO-NDX-20091012-02 | IBS Inter-bus Stop | 2009-10-12 | 2009-10-12 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 13 | Forced | KRAYN-NDX-PRT-0725 | 1 | 11.6833 | Highland 1 | Troubleshoot WTG and found slipring defective and in the process of changing the slipring we found damage to serial port. | KRAYN-WKO-NDX-20091012 | 1
KRAYN-WKO-NDX-20091013-01 | turbine maintenance | 2009-10-13 | 2009-10-13 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 25.25 | Forced |  |  | 8.3333 | Highland 1 | turbine was down for maintenance | KRAYN-WKO-NDX-20091013 | 1
KRAYN-WKO-NDX-20091015-01 | hydraulic break not closed | 2009-10-15 | 2009-10-16 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 3.8 | Forced |  |  | 23.9167 | Highland 1 | the turbine faulted due to a broken hydraulic line inside the tank the hose was replaced also a yaw convertor problem. the convertor was reprogramed and turbine was started up | KRAYN-WKO-NDX-20091015 | 1
KRAYN-WKO-NDX-20091015-02 | IBS interbus Stop | 2009-10-15 | 2009-10-15 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 7.3333 | Forced | KRAYN-NDX-PRT-0961 | 1 | 3.6667 | Highland 1 | changed the slipring | KRAYN-WKO-NDX-20091015 | 1
KRAYN-WKO-NDX-20091015-03 | yaw hyd brk not open | 2009-10-15 | 2009-10-18 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 17 | Forced | KRAYN-NDX-PRT-0480 | 1 | 90.05 | Highland 1 | Turbine was faulting for YP 250 fault because of the Yaw brk not open fault. Replaced yaw converter due to fault on converter but the problem was that the new one was not programed. Due to this problem we were unable to program until the next day. We reprogramed the new converter and the turbine still would not yaw after troubleshooting found that the timer relay was set wrong. Due to the Ice storm we had to leave the turbine and the turbine was still faulting, The time relay is faulty.The yaw converter was not the problem so we will put the replaced one back in stock. | KRAYN-WKO-NDX-20091015 | 1
KRAYN-WKO-NDX-20091015-04 | IBS interbus Stop | 2009-10-15 | 2009-10-15 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 7.3333 | Forced | KRAYN-NDX-PRT-0961 | 1 | 3.6667 | Highland 1 | changed the slipring. Do Not Put Part in SAP!!! | KRAYN-WKO-NDX-20091015 | 1
KRAYN-WKO-NDX-20091019-01 | LV diff. curr. 400v stop | 2009-10-19 | 2009-10-19 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 18 | Forced |  |  | 87.5 | Highland 1 | We Found that breaker 19F2 was tripped, so we troubleshot the 400v supply from the transformer and found nothing wrong. We have no 63 amp breakers in stock replaced with a 40 amp breaker until we receive the right one. The turbine was still faulted for MI external hardware fault and there was ice falling from turbine. We returned when the site was clear to return and found breaker Q43's feedback was completely disconnected from the breaker and the turbine thought that the breaker was tripped. Reinstalled the feedback and the fault went away. | KRAYN-WKO-NDX-20091019 | 1
KRAYN-WKO-NDX-20091019-02 | pitch 2 battery defect | 2009-10-19 | 2009-10-19 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 29.5167 | Forced |  |  | 5.0333 | Highland 1 | turbine faulted for pitch 2 battery defect, we removed all 36 batteries checked each one for voltage then put them under load and tested them again. all batteries were good so we then swaped out dc-dc link from blade three to blade two, we then swaped a over under battery relay from blade two to blade three, the reason these parts were swaped to another blade attempt to isolate the problem by moving the defect (fm1167) fault to a different blade. this fault is an intermitten fault and the turbine will pass all battery tests durring the turbines start up proceedure,we are still trouble shooting this. | KRAYN-WKO-NDX-20091019 | 1
KRAYN-WKO-NDX-20091020-01 | Manual Stop | 2009-10-20 | 2009-10-20 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 5.7 | Forced |  |  | 2.85 | Highland 1 | Type 2 Maint. | KRAYN-WKO-NDX-20091020 | 1
KRAYN-WKO-NDX-20091020-02 | Manual Stop | 2009-10-20 | 2009-10-20 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 3.7333 | Forced |  |  | 1.8667 | Highland 1 | Type 2 Maint. | KRAYN-WKO-NDX-20091020 | 1
KRAYN-WKO-NDX-20091021-01 | Manual Stop | 2009-10-21 | 2009-10-21 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 2.75 | Highland 1 | Type 2 Maint. | KRAYN-WKO-NDX-20091021 | 1
KRAYN-WKO-NDX-20091021-02 | Manual Stop | 2009-10-21 | 2009-10-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 7.1667 | Forced |  |  | 3.5833 | Highland 1 | Type 2 Maint. | KRAYN-WKO-NDX-20091021 | 1
KRAYN-WKO-NDX-20091021-03 | Manual Stop | 2009-10-21 | 2009-10-21 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 4.6 | Forced |  |  | 2.3 | Highland 1 | Type 2 Maint. | KRAYN-WKO-NDX-20091021 | 1
KRAYN-WKO-NDX-20091021-04 | Manual Stop | 2009-10-21 | 2009-10-21 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3.6333 | Forced |  |  | 1.8167 | Highland 1 | Troubleshot pitch 2 battery defect fault and found loose connection on 51F2 fuse which is the 24 volts dc to 51A1 over - undervoltage relay. | KRAYN-WKO-NDX-20091021 | 1
KRAYN-WKO-NDX-20091021-05 | Manual stop | 2009-10-21 | 2009-10-21 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.1 | Forced | KRAYN-NDX-PRT-0488 | 1 | 1.05 | Highland 1 | Troubleshot yaw brake not open fault and found 124 K2 relay defective. Removed and replaced relay and tested the yaw system. | KRAYN-WKO-NDX-20091021 | 1
KRAYN-WKO-NDX-20091022-01 | No work order description provided by contractor | 2009-10-22 | 2009-10-22 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 2.5203 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091022 | 1
KRAYN-WKO-NDX-20091022-02 | No work order description provided by contractor | 2009-10-22 | 2009-10-22 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 2.8881 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091022 | 1
KRAYN-WKO-NDX-20091022-03 | No work order description provided by contractor | 2009-10-22 | 2009-10-22 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 2.3375 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091022 | 1
KRAYN-WKO-NDX-20091023-01 | IBS Interbus stop | 2009-10-23 | 2009-10-23 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.6667 | Forced | KRAYN-NDX-PRT-0725 | 1 | 8.0333 | Highland 1 | The slipring was defective so removed and replaced and put the turbine back to run mode. | KRAYN-WKO-NDX-20091023 | 1
KRAYN-WKO-NDX-20091023-02 | rotor break not closed | 2009-10-23 | 2009-10-22 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 16.5 | Forced |  |  | 5.2333 | Highland 1 | this turbine has had a clamping delay on rotor break fault, we removed all plugs off hydraulic manifold that were in the loop also accumulators and all hard lines returning to tank and cylinoinds. we followed the hydraulic schematics through the entire rotor breaking system, all parts in junction had previously been checked and checked again for proper functioning, previously a bad accumulator had been replaced on the hydraulic station wich was in line with rotor breaking. this bad accumulator had broken pieces of rubber that got into the tank small pieces made it into the system and had blocked a jet preventing hard breaking on the rotor from reaching its full preasure in the time mannor that the turbine would allow, there fore the fault 262 was present. the jet was removed and the system was flushed out, the jet was cleaned and returned back into the system and turbine is returned to normal opperating state. | KRAYN-WKO-NDX-20091023 | 1
KRAYN-WKO-NDX-20091024-01 | 05WEA80812 FE 419 yaw hyd brk not closed | 2009-10-24 | 2009-10-24 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.1875 | Highland 1 | Replaced hydraulic hose in tank. | KRAYN-WKO-NDX-20091024 | 1
KRAYN-WKO-NDX-20091024-02 | Yaw hyd brk not closed | 2009-10-24 | 2009-10-24 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0968 | 1 | 4.5167 | Highland 1 | Found the hydraulic hose inside hyd. Station defective. | KRAYN-WKO-NDX-20091024 | 1
KRAYN-WKO-NDX-20091026-01 | No work order description provided by contractor | 2009-10-26 | 2009-10-22 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 3.8839 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091026 | 1
KRAYN-WKO-NDX-20091026-02 | No work order description provided by contractor | 2009-10-26 | 2009-10-26 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 5.0333 | Forced |  |  | 2.5167 | Highland 1 | Type 2 maintenance | KRAYN-WKO-NDX-20091026 | 1
KRAYN-WKO-NDX-20091026-03 | No work order description provided by contractor | 2009-10-26 | 2009-10-26 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 5.2667 | Forced |  |  | 2.6333 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091026 | 1
KRAYN-WKO-NDX-20091027-01 | No work order description provided by contractor | 2009-10-27 | 2009-10-26 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.2333 | Forced |  |  | 3.6167 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091027 | 1
KRAYN-WKO-NDX-20091027-02 | No work order description provided by contractor | 2009-10-27 | 2009-10-27 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 10.3333 | Forced |  |  | 5.1667 | Highland 1 | Type 2 Maintenance | KRAYN-WKO-NDX-20091027 | 1
KRAYN-WKO-NDX-20091028-01 | No work order description provided by contractor | 2009-10-28 | 2009-10-28 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 2.9667 | Highland 1 | type 2 maintenance , also vent valves were removed from blades | KRAYN-WKO-NDX-20091028 | 1
KRAYN-WKO-NDX-20091029-01 | No work order description provided by contractor | 2009-10-29 | 2009-10-29 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 2.65 | Highland 1 | type 2 maintenance shutdown | KRAYN-WKO-NDX-20091029 | 1
KRAYN-WKO-NDX-20091029-02 | No work order description provided by contractor | 2009-10-29 | 2009-10-29 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 2.65 | Highland 1 | type 2 maintenance on turbine, also vent valves were removed on turbine | KRAYN-WKO-NDX-20091029 | 1
KRAYN-WKO-NDX-20091029-03 | No work order description provided by contractor | 2009-10-29 | 2009-10-29 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 2.55 | Highland 1 | type 2 maintenance on turbine, vent valves were removed from blades | KRAYN-WKO-NDX-20091029 | 1
KRAYN-WKO-NDX-20091029-04 | No work order description provided by contractor | 2009-10-29 | 2009-10-29 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 2.55 | Highland 1 | type 2 maintenance on turbine, vent valves were removed from blades | KRAYN-WKO-NDX-20091029 | 1
KRAYN-WKO-NDX-20091102-01 | No work order description provided by contractor | 2009-11-02 | 2009-11-02 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.4333 | Highland 1 | removed vent valves from hub | KRAYN-WKO-NDX-20091102 | 1
KRAYN-WKO-NDX-20091102-02 | No work order description provided by contractor | 2009-11-02 | 2009-11-02 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.05 | Highland 1 | removed vent valves from blades | KRAYN-WKO-NDX-20091102 | 1
KRAYN-WKO-NDX-20091102-03 | No work order description provided by contractor | 2009-11-02 | 2009-10-02 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.1667 | Highland 1 | removed vent valves from hub | KRAYN-WKO-NDX-20091102 | 1
KRAYN-WKO-NDX-20091102-04 | No work order description provided by contractor | 2009-11-02 | 2009-11-02 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.4333 | Highland 1 | removed vent valves from hub | KRAYN-WKO-NDX-20091102 | 1
KRAYN-WKO-NDX-20091102-05 | No work order description provided by contractor | 2009-11-02 | 2009-11-02 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.4333 | Highland 1 | removed vent valves from hub | KRAYN-WKO-NDX-20091102 | 1
KRAYN-WKO-NDX-20091103-01 | No work order description provided by contractor | 2009-11-03 |  | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 18 | Forced |  |  | 1.4333 | Highland 1 | turbine was down previously due to bad blade helped wind access set up there platform for blade repairs, and tear the platform down also | KRAYN-WKO-NDX-20091103 | 1
KRAYN-WKO-NDX-20091104-01 | No work order description provided by contractor | 2009-11-04 | 2009-11-04 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.8333 | Forced |  |  | 1.55 | Highland 1 | filled up main bearing grease container for alu system, removed vent valves from the hub | KRAYN-WKO-NDX-20091104 | 1
KRAYN-WKO-NDX-20091104-02 | No work order description provided by contractor | 2009-11-04 | 2009-11-04 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.5333 | Highland 1 | removed vent valves from the blades | KRAYN-WKO-NDX-20091104 | 1
KRAYN-WKO-NDX-20091104-03 | No work order description provided by contractor | 2009-11-04 | 2009-11-04 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.1667 | Forced |  |  | 0.75 | Highland 1 | filled up alu container for yaw tooth greasing system | KRAYN-WKO-NDX-20091104 | 1
KRAYN-WKO-NDX-20091105-01 | No work order description provided by contractor | 2009-11-05 | 2009-11-05 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 16.5 | Forced |  |  | 8.0333 | Highland 1 | repaired HV cables with draka AG at yaw deck | KRAYN-WKO-NDX-20091105 | 1
KRAYN-WKO-NDX-20091105-02 | No work order description provided by contractor | 2009-11-05 | 2009-11-05 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2.3333 | Forced |  |  | 0.95 | Highland 1 | filled grease container on alu for main bearing | KRAYN-WKO-NDX-20091105 | 1
KRAYN-WKO-NDX-20091106-01 | Cable Repair | 2009-11-06 | 2009-11-06 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 12 | Forced |  |  | 2.25 | Highland 1 | UT taught John and AJ how to repair the cables. We also repaired 6 cables. | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-02 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 1.3 | Highland 1 | went up tower to inspect HV cables with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-03 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 1.3 | Highland 1 | went up tower to inspect HV cables with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-04 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1.1667 | Forced |  |  | 0.45 | Highland 1 | went up to yaw deck to inspect cables with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-05 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.6667 | Forced |  |  | 0.48333 | Highland 1 | went with draka AG to inspect cables at yaw deck | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-06 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.46667 | Highland 1 | went up tower with draka to inspect HV cable wear | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-07 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.1667 | Forced |  |  | 0.48333 | Highland 1 | went up tower to inspect HV cables at yaw deck with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-08 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.56667 | Highland 1 | went up tower with draka AG to inspect HV cables at the yaw deck | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-09 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1.2 | Forced |  |  | 0.51667 | Highland 1 | inspection of HV cables at yaw deck with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-10 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.45 | Highland 1 | went up tower to inspect HV cables at yaw deck with draka | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-11 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.6 | Highland 1 | went up tower to inspect HV cables at yaw deck | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-12 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.4 | Highland 1 | went up tower to inspect HV cables at yaw deck | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-13 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 1.1667 | Forced |  |  | 0.6 | Highland 1 | went up tower to inspect cables at yaw deck with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-14 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1.3667 | Forced |  |  | 0.63333 | Highland 1 | inspection of HV cables at yaw deck with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-15 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.1667 | Forced |  |  | 1.0333 | Highland 1 | went up tower to inspect HV cables at yaw deck with draka | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-16 | IBS Interbus Stop | 2009-11-06 | 2009-11-06 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.0333 | Highland 1 | WTG went down on a pitch com fault , found faulty slipring. | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091106-17 | No work order description provided by contractor | 2009-11-06 | 2009-11-06 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.6333 | Forced |  |  | 0.71667 | Highland 1 | went up turbine to inspect HV cables with draka AG | KRAYN-WKO-NDX-20091106 | 1
KRAYN-WKO-NDX-20091107-01 | No work order description provided by contractor | 2009-11-07 | 2009-11-07 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.38333 | Highland 1 | inspection on HV cables at yaw deck with draka | KRAYN-WKO-NDX-20091107 | 1
KRAYN-WKO-NDX-20091107-02 | No work order description provided by contractor | 2009-11-07 | 2009-11-07 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.55 | Highland 1 | went up tower to inspect HV cables with draka AG | KRAYN-WKO-NDX-20091107 | 1
KRAYN-WKO-NDX-20091107-03 | Wire Inspections | 2009-11-07 | 2009-11-07 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1 | Highland 1 | Inspected Generator Cables | KRAYN-WKO-NDX-20091107 | 1
KRAYN-WKO-NDX-20091107-04 | No work order description provided by contractor | 2009-11-07 | 2009-11-07 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 2 | Highland 1 | Inspection of Generator cables | KRAYN-WKO-NDX-20091107 | 1
KRAYN-WKO-NDX-20091109-01 | Rain Deflector Repair | 2009-11-09 | 2009-11-09 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 3.7667 | Planned |  |  | 3.7667 | Highland 1 | Assisted in locking out hub and roof, pitching and yawing of tower to access blades. | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091109-02 | Rain Deflector Repair | 2009-11-09 | 2009-11-09 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 2.6667 | Planned |  |  | 2.6667 | Highland 1 | Assisted in locking hub and pitching blades to access repair. | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091109-03 | Cable Repair | 2009-11-09 | 2009-11-09 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 2.7833 | Highland 1 | Repaired Cables on Yaw Deck | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091109-04 | Manual stop | 2009-11-09 | 2009-11-09 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5.6 | Forced |  |  | 2.8 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091109-05 | Manual stop | 2009-11-09 | 2009-11-09 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5.6 | Forced |  |  | 2.8 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091109-06 | Cable Repair | 2009-11-09 | 2009-11-09 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 6.6667 | Forced |  |  | 2.5167 | Highland 1 | Repaired Cables on Yaw Deck | KRAYN-WKO-NDX-20091109 | 1
KRAYN-WKO-NDX-20091110-01 | Rain Deflector Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 4.1667 | Planned |  |  | 4.1667 | Highland 1 | Assisted in locking hub and pitching blades to access repair. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-02 | Rain Deflector Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 2 | Highland 1 | Assisted in locking hub and pitching blades to access repair. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-03 | No work order description provided by contractor | 2009-11-10 | 2009-11-10 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.6333 | Highland 1 | went up tower to do cable repairs on the yaw deck | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-04 | cable repairs | 2009-11-10 | 2009-11-10 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 9.3333 | Forced |  |  | 4.6667 | Highland 1 | the turbine has had a cable rubbing problem from back durring projects, nordex engineering in has attempted to resolve this. we are putting a patch over the rubbed cables to extend the life of the cable until engineering has a propper fix | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-05 | No work order description provided by contractor | 2009-11-10 | 2009-11-10 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 6.3333 | Forced |  |  | 3.0833 | Highland 1 | removed vent valves from hub @ blades 1,2,3 | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-06 | Manual stop | 2009-11-10 | 2009-11-10 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 6.1667 | Forced |  |  | 3.0833 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-07 | No work order description provided by contractor | 2009-11-10 | 2009-11-10 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 10.6 | Forced |  |  | 5.1833 | Highland 1 | went up turbine to patch cables that have been damaged with rubbing | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-08 | Manual stop | 2009-11-10 | 2009-11-10 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 5.1667 | Forced |  |  | 2.5833 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-09 | Cable Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 2.8167 | Highland 1 | John Huff and Dustin Thill Had Removed Blade Vent Valves. Mark Vasquez and Aaron Edelson Had completed Cable Repairs on Turbine. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-10 | Cable Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 2.8167 | Highland 1 | John Huff and Dustin Thill Had Removed Blade Vent Valves. Mark Vasquez and Aaron Edelson Had completed Cable Repairs on Turbine. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-11 | Rain Deflector Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 3.7667 | Planned |  |  | 4.7667 | Highland 1 | Assisted in locking hub and pitching blades to access repair. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-12 | Cable Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 15.4167 | Forced |  |  | 5.7 | Highland 1 | First Aaron and Mark took out the vent valves in the blades. Then Aaron and Mark repaired the cables. UT took LM up and repaired the root rings. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-13 | Cable Repair | 2009-11-10 | 2009-11-10 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 15.4167 | Forced |  |  | 5.7 | Highland 1 | First Aaron and Mark took out the vent valves in the blades. Then Aaron and Mark repaired the cables. UT took LM up and repaired the root rings. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091110-14 | Hyd Oil Level L Stop | 2009-11-10 | 2009-11-11 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.6667 | Forced | KRAYN-NDX-PRT-0291 | 1.5 gallon | 1.5 | Highland 1 | Added hydraulic oil to hyd. Station. | KRAYN-WKO-NDX-20091110 | 1
KRAYN-WKO-NDX-20091111-01 | Manual stop | 2009-11-11 | 2009-11-11 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 2.5 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-02 | Manual stop | 2009-11-11 | 2009-11-11 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 7.8 | Forced |  |  | 3.9 | Highland 1 | Repaired the generator cables according to Draka instructions. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-03 | Cable Repair | 2009-11-11 | 2009-11-11 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4.1667 | Forced |  |  | 1.65 | Highland 1 | Cable repairs on Yaw deck. Cables were rubbing against side of the tube. We shrink wrapped them with Draka shrinkwrap. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-04 | Cable Repair | 2009-11-11 | 2009-11-11 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.8333 | Forced |  |  | 0.91667 | Highland 1 | Cable repairs on Yaw deck. Cables were rubbing against side of the tube. We shrink wrapped them with Draka shrinkwrap. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-05 | Rain Deflector Repair | 2009-11-11 | 2009-11-11 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 2.8167 | Planned |  |  | 2.8167 | Highland 1 | Assisted in locking hub and pitching blades to access repair. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-06 | Wire Repair | 2009-11-11 | 2009-11-11 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 1.4833 | Highland 1 | Repaired Damaged Cables on yaw deck cables were rubing on side of tube and repaired with Draka Approved Shrink Wrap | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091111-07 | Wire Repairs | 2009-11-11 | 2009-11-11 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.7667 | Forced |  |  | 0.65 | Highland 1 | Repaired Damaged Cables,Damaged Cables damaged due to rubbing on tube. Completed Draka Approved repair with Materials provided by Draka. | KRAYN-WKO-NDX-20091111 | 1
KRAYN-WKO-NDX-20091116-01 | No work order description provided by contractor | 2009-11-16 | 2009-11-16 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 44.8333 | Forced | KRAYN-NDX-PRT-0745,KRAYN-NDX-PRT-0745,KRAYN-NDX-PRT-0745 | 1,1,1 | 8.35 | Highland 1 | went up turbine replaced leaking yaw calipers with new calipers, cleaned up yaw deck and all mess also changed out offline oil filter element | KRAYN-WKO-NDX-20091116 | 1
KRAYN-WKO-NDX-20091116-02 | No work order description provided by contractor | 2009-11-16 | 2009-11-16 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 44.8333 | Forced | KRAYN-NDX-PRT-0745,KRAYN-NDX-PRT-0745,KRAYN-NDX-PRT-0745 | 1,1,1 | 8.35 | Highland 1 | went up turbine replaced leaking yaw calipers with new calipers, cleaned up yaw deck and all mess also changed out offline oil filter element | KRAYN-WKO-NDX-20091116 | 1
KRAYN-WKO-NDX-20091117-01 | No work order description provided by contractor | 2009-11-17 | 2009-11-17 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 0.73333 | Forced |  |  | 0.33333 | Highland 1 | went up turbine to inspect two break calipers for leaks, these calipers had been changed out the previous day. Serial numbers were also taken for further reports | KRAYN-WKO-NDX-20091117 | 1
KRAYN-WKO-NDX-20091120-01 | IBS interbus Stop | 2009-11-20 | 2009-11-20 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 7.1 | Forced |  |  | 2.3667 | Highland 1 | cleaned and tightened slipring wiring | KRAYN-WKO-NDX-20091120 | 1
KRAYN-WKO-NDX-20091124-01 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 1 | Highland 1 | took oil sample and changed offline filter from the gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-02 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 1.4667 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.66667 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-03 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 1.3 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.65 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-04 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 1.3 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.65 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-05 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1.0333 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0962,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.51667 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-06 | maintanence | 2009-11-24 | 2009-11-24 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1.0333 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0962,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.51667 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-07 | maintenance | 2009-11-24 | 2009-11-24 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.3 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.65 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091124-08 | maintenance | 2009-11-24 | 2009-11-24 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.3 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0348 | 1,2,1 | 0.65 | Highland 1 | changed out offline oil filter and took oil sample from gearbox | KRAYN-WKO-NDX-20091124 | 1
KRAYN-WKO-NDX-20091130-01 | Env.Ice Det. | 2009-11-30 | 2009-11-30 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 0.98333 | Forced |  |  | 7.4333 | Highland 1 | Disabled Ice sensor for testing, The turbine was going in and out of ice det. Active and normal. | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091130-02 | Env.Ice Det. | 2009-11-30 | 2009-11-30 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.96667 | Forced |  |  | 4.45 | Highland 1 | Disabled Ice sensor for testing, The turbine was going in and out of ice det. Active and normal. | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091130-03 | Env.Ice Det. | 2009-11-30 | 2009-11-30 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 1.45 | Forced |  |  | 3.2167 | Highland 1 | Disabled Ice sensor for testing, The turbine was going in and out of ice det. Active and normal. | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091130-04 | Env.Ice Det. | 2009-11-30 | 2009-11-30 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1.15 | Forced |  |  | 3.1333 | Highland 1 | Disabled Ice sensor for testing, The turbine was going in and out of ice det. Active and normal. | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091130-05 | No work order description provided by contractor | 2009-11-30 | 2009-11-30 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7.1333 | Forced |  |  | 3.5667 | Highland 1 | SKF monitoring systems received a vibration from the high speed side of the gearbox that was abnormal, we went up tower inspected the coupling to see if it had slipped, the coupling has not slipped. ran the turbine up to 800 rpm and checked for vibration also adjusted the cover on the low speed side. alignment may be bad on generator or further inspection of gearbox will be needed | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091130-06 | Env.Ice Det. | 2009-11-30 | 2009-11-30 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.65 | Forced |  |  | 5.4833 | Highland 1 | Disabled Ice sensor for testing, The turbine was going in and out of ice det. Active and normal. | KRAYN-WKO-NDX-20091130 | 1
KRAYN-WKO-NDX-20091201-01 | IBS Interbus Stop | 2009-12-01 | 2009-12-01 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2.4333 | Forced | KRAYN-NDX-PRT-0172 | 1 | 3.9333 | Highland 1 | Turbine was also faulting on vibration fault. We replaced the vibration sensor and monitored Y and Z levels. | KRAYN-WKO-NDX-20091201 | 1
KRAYN-WKO-NDX-20091201-02 | MI Ext. Hardware Error | 2009-12-01 | 2009-12-01 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0.61667 | Forced |  |  | 8.9333 | Highland 1 | Reset the turbine | KRAYN-WKO-NDX-20091201 | 1
KRAYN-WKO-NDX-20091202-01 | fm420 yaw hyd. Not open | 2009-12-02 | 2009-12-02 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 3.8667 | Forced |  |  | 1.9333 | Highland 1 | Technician Information the turbine has gone down number of times on yp 50, due to yaw hydraulic break not open. We checked a pressure transducer for proper function, cleaned and checked shielding on cabling also cleaned contacts before reasembling checked contacts in hydraulic box and at the top box terminal blocks. further more emails have been sent out to help resolve the issue | KRAYN-WKO-NDX-20091202 | 1
KRAYN-WKO-NDX-20091205-01 | IBS Interbus Stop | 2009-12-05 | 2009-12-06 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 14.45 | Highland 1 | Turbine was faulting on a pitch com fault. We tested the turbine and manualy ran in thru the day and the turbine would not run past 300 rpms. Removed and replaced slipring. | KRAYN-WKO-NDX-20091205 | 1
KRAYN-WKO-NDX-20091205-02 | interbus stop | 2009-12-05 |  | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0725 | 1 | 5.4833 | Highland 1 | turbine went down on an interbus stop we replaced the slipring we are still having com. Problems with the turbine | KRAYN-WKO-NDX-20091205 | 1
KRAYN-WKO-NDX-20091205-03 | interbus stop | 2009-12-05 | 2009-12-08 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 36 | Forced | KRAYN-NDX-PRT-0725 | 1 | 77.35 | Highland 1 | turbine went down on an interbus stop we replaced the slipring we are still having com. Problems with the turbine 12/07/09 Troubleshot com. Problem with all the blades. Swapped out pitch convertor on blade 3 and in the process found that blade 3 wasn't communicating with the turbine due to ethernet cable connection , removed and replaced ethernet cable and adjusted the redundant value. Serial number of the new pitch conv. 084150397 and we put the old one back in stock 082650628. | KRAYN-WKO-NDX-20091205 | 1
KRAYN-WKO-NDX-20091206-01 | mi class b fault | 2009-12-06 |  | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5.3333 | Forced |  |  | 3.1833 | Highland 1 | turbine went down on an mi class b and c fault safty chain was activated we cleared faults and left problems are SEG triggers have been recorded from turbine and sent out, 10-7 checked all shielding wires checked all prox sensors and checked centa coupling for sliping | KRAYN-WKO-NDX-20091206 | 1
KRAYN-WKO-NDX-20091207-01 | Yaw Senstrack 1(90) Defect, (20) Defect, Tooth Timeout | 2009-12-07 | 2009-12-08 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 25 | Forced | KRAYN-NDX-PRT-0043 | 1 | 51.7625 | Highland 1 | Commence troubleshooting on 12/07/09 & 12/08/09 for FM 490, 492 and 493. Found {azimuth} yaw motor #2 not Terminated since the Turbine was Commissioned. No connection at the bottom of Terminal block X22 pin 4, 5 and 6. Reconnected wiring and place turbine online. Site will monitor yaw motor for any signs of Damage. | KRAYN-WKO-NDX-20091207 | 1
KRAYN-WKO-NDX-20091208-01 | yaw hydraulic not open | 2009-12-08 | 2009-12-07 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 15 | Forced |  |  | 42 | Highland 1 | checked hydraulics for a stuck mechanical valve cleared blockage and returned turbine back to service | KRAYN-WKO-NDX-20091208 | 1
KRAYN-WKO-NDX-20091213-01 | turbine lpc broke | 2009-12-13 | 2009-12-13 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 100.8 | Highland 1 | turbines lpc power supply was found to be bad by techs a new lpc was brought from germany to usa by a tech returning to the states that weekend the new lpc was instaled as soon as it got here on site and turbine was put back online. parts were ordered for Bad lpc it was fixed and an extra lpc is now onsite | KRAYN-WKO-NDX-20091213 | 1
KRAYN-WKO-NDX-20091214-01 | Gear BypFilterPmp FuseTrip | 2009-12-14 | 2009-12-14 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.63333 | Forced |  |  | 0.31667 | Highland 1 | reset breaker 112AQ1 | KRAYN-WKO-NDX-20091214 | 1
KRAYN-WKO-NDX-20091217-01 | yaw hyd brakes not open | 2009-12-17 | 2009-12-17 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 15.75 | Forced |  |  | 4.75 | Highland 1 | turbine had gone down multiple time prior for the same fault outside tempetures where very cold hydraulics where not functioning correctly went up turbine checked out all electro valves in the yaw hydraulic brake loop for proper function, droped power to our hyd station and bled off all pressure in the lines then took checked the mechanical valves for proper functioning put everything back together yawed the turbine and put it back online. | KRAYN-WKO-NDX-20091217 | 1
KRAYN-WKO-NDX-20091226-01 | pitch 2 angle fault | 2009-12-26 | 2009-12-27 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 18.3 | Forced | KRAYN-NDX-PRT-0969 | 1 | 33.8333 | Highland 1 | turbine faulted with blade two position stuck at 41.4 degrees went to the turbine attempted to drop power and reboot the hub, checked out battery contactors, checked out battery fuses, checked dc/dc link on pitch two , hard reset convertor for pitch two still blade two remained stuck at 41.4 degrees we then went and programed a new pitch convertor replaced the convertor on pitch two and fixed the problem then put the turbine back online | KRAYN-WKO-NDX-20091226 | 1
KRAYN-WKO-NDX-20091229-01 | yaw hydraulic break not open | 2009-12-29 | 2009-12-30 | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 30.6 | Forced |  |  | 44.1 | Highland 1 | turbine door was popped open through the high winds of the night causing the yaw brake calipers to seize up causing the fm420, the door lock was adjusted and door bump bar was loobed so it will not open accidently again, also insulation was added to the hard lines of the yaw calipers, an oil change to a synthetic oil was performed at the hydraulic station however calipers are still at a non opperating tempeture a heater is installed at the yaw deck to warm up the tempeture.10-30 went up turbine removed insulation off hydraulic lines and applied a warming cord, took apart hydraulic manifold looking for problems, after we made a tool to remove a valve inside the manifold we then removed the valve replacing it with a new valve, durring this process found particals of matter which should not have been inside the hydraulic loop for yaw brakes, cleaned it out and reassembled the manifold then put the turbine back online. | KRAYN-WKO-NDX-20091229 | 1
KRAYN-WKO-NDX-20100105-01 | pitch3 not ready | 2010-01-05 | 2010-01-05 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0686 | 1 | 68.4833 | Highland 1 | turbine faulted for pitch three not ready, winds were to high to acess the hub (unsafe wind speeds) when we were able to acess the hub safely we went into pitch three box read the error faults on the convertor and then replaced the faulty convertor to clear present faults for blade three on the turbine then returning turbine back into service. | KRAYN-WKO-NDX-20100105 | 1
KRAYN-WKO-NDX-20100106-01 | interbus stop | 2010-01-06 | 2010-02-06 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 4.1333 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.85 | Highland 1 | replaced slipring in the hub slipring was an older model however it was a 100 watt, due to internal problems with slipring data transmition was lost so slipring was replaced and turbine was put back online. | KRAYN-WKO-NDX-20100106 | 1
KRAYN-WKO-NDX-20100112-01 | IBS stop | 2010-01-12 | 2010-01-12 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 4.6333 | Forced | KRAYN-NDX-PRT-0725 | 1 | 54.15 | Highland 1 | Changed out the slip ring | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-02 | N/A | 2010-01-12 | 2010-01-12 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 6.35 | Forced | KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 1,1 | 2.1167 | Highland 1 | INSTALLED HEATER NEAR HYDRAULIC STATION. REPLACED HYDRAULIC FLUID IN THE HYDRAULIC RESEVOIR WITH NEW SYNTHETIC. BLED SYSTEM. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-03 | IBS stop | 2010-01-12 | 2010-01-12 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 4.6333 | Forced | KRAYN-NDX-PRT-0725 | 1 | 54.15 | Highland 1 | Changed out the slip ring | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-04 | Pitch 2 not ready | 2010-01-12 | 2010-01-13 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 29 | Forced |  |  | 60.3914 | Highland 1 | troubleshot Turbine for FM- Pitch 2 not ready.. blade 2 stuck at 87 Deg. Reset pitch by powering down for 10 mins. Possible momentary communication interruption. Place Turbine back in operation. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-05 | N/A | 2010-01-12 | 2010-01-12 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced | KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 1,1 | 2.5 | Highland 1 | INSTALLED HEATER NEAR HYDRAULIC STATION. REPLACED HYDRAULIC FLUID IN THE HYDRAULIC RESEVOIR WITH NEW SYNTHETIC. BLED SYSTEM. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-06 | N/A | 2010-01-12 | 2010-01-12 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced | KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 1,1 | 2.5 | Highland 1 | INSTALLED HEATER NEAR HYDRAULIC STATION. REPLACED HYDRAULIC FLUID IN THE HYDRAULIC RESEVOIR WITH NEW SYNTHETIC. BLED SYSTEM. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-07 | Pitch2 DC.link Overcurrent | 2010-01-12 | 2010-01-12 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 15 | Forced |  |  | 10.9961 | Highland 1 | Collected all screen shots, error and parameter files for Engineering RCA on Blade 1, 2 and 3. Troubleshot turbine for FM 1108 found PITCH OVERCURRENT on Blade 2 and 3 internal fault U5. Reset pitch converter by removing power to system for 10 mins. Turbine was placed back online. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-08 | N/A | 2010-01-12 | 2010-01-12 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 1,1 | 1.3 | Highland 1 | INSTALLED HEATER NEAR HYDRAULIC STATION. REPLACED HYDRAULIC FLUID IN THE HYDRAULIC RESEVOIR WITH NEW SYNTHETIC. BLED SYSTEM. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100112-09 | N/A | 2010-01-12 | 2010-01-12 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 1,1 | 1.3 | Highland 1 | INSTALLED HEATER NEAR HYDRAULIC STATION. REPLACED HYDRAULIC FLUID IN THE HYDRAULIC RESEVOIR WITH NEW SYNTHETIC. BLED SYSTEM. | KRAYN-WKO-NDX-20100112 | 1
KRAYN-WKO-NDX-20100113-01 | Interbus Stop | 2010-01-13 | 2010-01-14 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 33 | Forced | KRAYN-NDX-PRT-0725 | 1 | 24.6511 | Highland 1 | Install new PM firmware version V2-01-01. Upate was sucessful. Also replaced new 100watts SLIPRING due to the interbus stop FM700 | KRAYN-WKO-NDX-20100113 | 1
KRAYN-WKO-NDX-20100113-02 | Interbus Stop | 2010-01-13 | 2010-01-14 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 33 | Forced | KRAYN-NDX-PRT-0725 | 1 | 24.6511 | Highland 1 | Install new PM firmware version V2-01-01. Upate was sucessful. Also replaced new 100watts SLIPRING due to the interbus stop FM700 | KRAYN-WKO-NDX-20100113 | 1
KRAYN-WKO-NDX-20100116-01 | Yaw Drive Change Out | 2010-01-16 | 2009-12-17 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 51.5 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0959 | 2,2 | 71.5667 | Highland 1 | Both Yaw drives were changed out and the yaw converter was reprogrammed for the new type of Remme motors over the course of 1-14-10 through 1-17-10. On the evening of 1/16/10 at approximately 17:00 Mustafa Elzein and Derek Johnson arrived on site to assist with programming the yaw converter. They ended up returning to the turbine on the 17th and placed it back online with the new software uploaded onto the yaw converter. | KRAYN-WKO-NDX-20100116 | 1
KRAYN-WKO-NDX-20100117-01 | Yaw SensTrack 1(90°) Defect | 2010-01-17 | 2010-01-17 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 34.5 | Forced | KRAYN-NDX-PRT-0781 | 2 | 674.9497 | Highland 1 | Turbine went offline from 12/20/09-01/17/10 for FM-490, 492 and 494 Yaw sensor defect. Service Team found both yaw drives damage due to one motor not terminated during commissioning, therefore leaving one motor to yaw the turbine. Crane crew installed 2 new RAMME Yaw motor/drive. Master Technicians uploaded new parameter files and Terminated the motors. Operational testing was sucessful. Turbine placed online 1/17/10. | KRAYN-WKO-NDX-20100117 | 1
KRAYN-WKO-NDX-20100120-01 | No work order description provided by contractor | 2010-01-20 | 2010-01-20 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 18.75 | Planned |  |  | 6.2167 | Highland 1 | SEG Maintenance | KRAYN-WKO-NDX-20100120 | 1
KRAYN-WKO-NDX-20100120-02 | No work order description provided by contractor | 2010-01-20 | 2010-01-20 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 18.75 | Planned |  |  | 6.2167 | Highland 1 | SEG Maintenance | KRAYN-WKO-NDX-20100120 | 1
KRAYN-WKO-NDX-20100120-03 | Yaw SensTrack 2(0°) Defect FM492 | 2010-01-20 |  | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 40 | Forced | KRAYN-NDX-PRT-0563 | 1 | 5.6167 | Highland 1 | First day was spent troubleshooting yaw converter issues and installing a new cam switch in the yaw system. Second day I received a new file to upload onto the yaw converter which worked. It was determined that the old data file was corrupt. | KRAYN-WKO-NDX-20100120 | 1
KRAYN-WKO-NDX-20100121-01 | WEA03-80810_1-22-10_pitch firmware-RW | 2010-01-21 | 2010-01-22 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.33333 | Forced |  |  | 0.21319 | Highland 1 | Went to WT 3 to update firmware on pitch converters. Turbine was already down for FE 1208. Turbine stayed down because of problem | KRAYN-WKO-NDX-20100121 | 1
KRAYN-WKO-NDX-20100121-02 | WEA12-80819 Pitch firmware_ 1-21-10_RW | 2010-01-21 | 2010-01-29 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.125 | Highland 1 | Went to WT 12 to update firmware on pitch converters. | KRAYN-WKO-NDX-20100121 | 1
KRAYN-WKO-NDX-20100121-03 | Firmware Update | 2010-01-21 | 2010-01-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.5 | Highland 1 | Performed firmware update. | KRAYN-WKO-NDX-20100121 | 1
KRAYN-WKO-NDX-20100121-04 | maintenance | 2010-01-21 | 2010-01-21 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 26 | Planned |  |  | 5.0167 | Highland 1 | seg maintenance | KRAYN-WKO-NDX-20100121 | 1
KRAYN-WKO-NDX-20100122-01 | Manual Stop | 2010-01-22 | 2010-01-22 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 21 | Forced |  |  | 5.0272 | Highland 1 | SEG Maintenance with Instructor for SEG Class. Kai-Peter Glesmann was the instructor and Brad Foy shut down the Pad mount for us. | KRAYN-WKO-NDX-20100122 | 1
KRAYN-WKO-NDX-20100125-01 | firmware update on pitchmaster | 2010-01-25 | 2010-01-25 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 10 | Forced |  |  | 9.0333 | Highland 1 | firmware updates applied to the pitch masters along with new parameters for each blade, also a pick up list was completed. The turbine was then handed over to Todd Wrigglesworth and his class for saftey training, turbine time for training was 18:30 to 22:36 then turbine was put back into run | KRAYN-WKO-NDX-20100125 | 1
KRAYN-WKO-NDX-20100125-02 | No work order description provided by contractor | 2010-01-25 | 2010-01-25 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 25.55 | Forced |  |  | 8.5167 | Highland 1 | Blade firmware update and checklist | KRAYN-WKO-NDX-20100125 | 1
KRAYN-WKO-NDX-20100126-01 | firmware updates | 2010-01-26 | 2010-01-26 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 24.25 | Forced | KRAYN-NDX-PRT-0325 | 1 | 7.0167 | Highland 1 | Firmware was Updated on pitchmasters, Confirmed 100W Slipring Installed, Confirmed Both Yaw Motors Running Properly, Rerouted Induction Sensor Cables on Low Speed Shaft, Installed Temporary Cable Chaffing Guard, Unable to Secure Kelms Grips - No Wear Indicated, Confirmed Heater is Bolted Down, Confirmed Nacelle Crane Secured, Found Wrong Parameters in Yaw Converter - Installed Correct Parameters. Removed Vent Valves from Blade Bearings, and Changed GB Oil Filter | KRAYN-WKO-NDX-20100126 | 1
KRAYN-WKO-NDX-20100127-01 | SEG maintenance | 2010-01-27 | 2010-01-27 | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 26 | Forced |  |  | 6.1333 | Highland 1 | Perform SEG maintenance as per nordex instruction I401_658_x_EN revision 5. | KRAYN-WKO-NDX-20100127 | 1
KRAYN-WKO-NDX-20100127-02 | No work order description provided by contractor | 2010-01-27 | 2010-01-27 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0325 | 1 | 1.25 | Highland 1 | Changed in line oil filter. | KRAYN-WKO-NDX-20100127 | 1
KRAYN-WKO-NDX-20100128-01 | No work order description provided by contractor | 2010-01-28 | 2010-01-28 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 25.5 | Forced |  |  | 6 | Highland 1 | Performed SEG Maintenance | KRAYN-WKO-NDX-20100128 | 1
KRAYN-WKO-NDX-20100128-02 | No work order description provided by contractor | 2010-01-28 | 2010-01-28 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 25.5 | Forced |  |  | 6 | Highland 1 | Performed SEG Maintenance | KRAYN-WKO-NDX-20100128 | 1
KRAYN-WKO-NDX-20100128-03 | pitch angle | 2010-01-28 | 2010-01-30 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 35 | Forced |  |  | 42.9167 | Highland 1 | 1-29-10 PitchMaster Firmware Update Complete, Confirmed 100W Slipring Installed, Confirmed Both Yaw Drives Operating Properly, Rerouting of Induction Sensor Cables Not Possible-Too Short, Installation of Upper & Lower Cable Chaffing Guards Complete, Kelms Grips Secured, Confirmed-Heater Bolted Down, Confirmed-Nacelle Crane Secured, Confirmed-Correct Yaw Converter Parameters Installed, and Confirmed Rerouting of GB Cooling Fan Power Cable. 1-30-10 went up tower to troubleshoot yaw problems fixed tower and put it back into operation. | KRAYN-WKO-NDX-20100128 | 1
KRAYN-WKO-NDX-20100130-01 | IBS Interbus Stop | 2010-01-30 | 2010-01-30 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 6.8667 | Forced | KRAYN-NDX-PRT-0725 | 1 | 10.05 | Highland 1 | Changed out the slip ring due to fault and it being 50 watt heater | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-02 | IBS Interbus Stop | 2010-01-30 | 2010-01-30 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 6.8667 | Forced | KRAYN-NDX-PRT-0725 | 1 | 10.05 | Highland 1 | Changed out the slip ring due to fault and it being 50 watt heater | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-03 | IBS Interbus Stop | 2010-01-30 | 2010-01-31 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 9.3 | Forced | KRAYN-NDX-PRT-0725 | 1 | 34.25 | Highland 1 | Due to this slipring being 100 watt we Disconnected slip to discharge static build up. Discharging the system did not fix it,had to put in new slip ring on the next day | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-04 | IBS Interbus stop | 2010-01-30 | 2010-01-31 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 14 | Forced | KRAYN-NDX-PRT-0725 | 1 | 7.2594 | Highland 1 | Installed new Pitch Firmware and 100watts USDK 248.1 slipring. | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-05 | IBS Interbus stop | 2010-01-30 | 2010-01-31 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 14 | Forced | KRAYN-NDX-PRT-0725 | 1 | 7.2594 | Highland 1 | Installed new Pitch Firmware and 100watts USDK 248.1 slipring. | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-06 | interbus error | 2010-01-30 | 2010-01-30 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0725 | 1 | 10.0667 | Highland 1 | went up tower to replace a slipring, which was bad and the origanal fault on turbine. While we where in the hub we updated pitch convertors on all the blades while in the hub then returned the turbine back into service | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100130-07 | interbus error | 2010-01-30 | 2010-01-30 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0725 | 1 | 10.0667 | Highland 1 | went up tower to replace a slipring, which was bad and the origanal fault on turbine. While we where in the hub we updated pitch convertors on all the blades while in the hub then returned the turbine back into service | KRAYN-WKO-NDX-20100130 | 1
KRAYN-WKO-NDX-20100201-01 | Pitch Power Volt Fault | 2010-02-01 | 2010-02-03 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 56.5 | Forced | KRAYN-NDX-PRT-0725,KRAYN-NDX-PRT-0480 | 1,1 | 31.2717 | Highland 1 | Troubleshot FM-1172 pitch power voltage fault discovered defective slipring. Replaced with a new 100watt SERIAL NO 29-1463-0313. Also performed daily checklist*please refer to checklist. | KRAYN-WKO-NDX-20100201 | 1
KRAYN-WKO-NDX-20100201-02 | scheduled listed items | 2010-02-01 | 2010-02-01 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 16.8 | Planned | KRAYN-NDX-PRT-0725 | 1 | 4.2 | Highland 1 | Firmware was Updated on pitchmasters, 100W Slipring Installed, Confirmed Both Yaw Motors Running Properly, Installed Temporary Cable Chaffing Guard, Unable to Secure Kelms Grips - No Wear Indicated, Confirmed Heater is Bolted Down, Confirmed Nacelle Crane Secured,assured correct Parameters in Yaw Converter. | KRAYN-WKO-NDX-20100201 | 1
KRAYN-WKO-NDX-20100201-03 | Pitch Power volt | 2010-02-01 | 2010-02-01 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 6.85 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.9167 | Highland 1 | Wtg faulted 3 times for a pitch power volt fault and the reason being is a faulty slipring, Removed and replaced the slipring. | KRAYN-WKO-NDX-20100201 | 1
KRAYN-WKO-NDX-20100202-01 | Manual Stop | 2010-02-02 | 2010-02-02 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 3.8 | Forced | KRAYN-NDX-PRT-0725 | 1 | 1.9 | Highland 1 | Changed 50 watt slipring to a 100 watt slipring. Operating hrs 8173.71 | KRAYN-WKO-NDX-20100202 | 1
KRAYN-WKO-NDX-20100202-02 | No work order description provided by contractor | 2010-02-02 | 2010-02-02 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 30 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.5167 | Highland 1 | Changed out the slip ring, install mudflaps on cables, bolt down heater, update parameters in yaw converter and all 3 pitch converters. | KRAYN-WKO-NDX-20100202 | 1
KRAYN-WKO-NDX-20100203-01 | PITCH Power Volt.Fault | 2010-02-03 | 2010-02-03 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 19.9 | Forced | KRAYN-NDX-PRT-0725 | 1 | 8.6333 | Highland 1 | Breaker 100F1 was tripping do to a overcurrent of 85 amps. Changed out the 100watt slipring back to a 50 watt slipring out of turbine 3 which was still good | KRAYN-WKO-NDX-20100203 | 1
KRAYN-WKO-NDX-20100203-02 | Checklist | 2010-02-03 | 2010-02-03 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 10.5 | Forced | KRAYN-NDX-PRT-0325 | 1 | 3.6333 | Highland 1 | Checked Parameter files on the yaw and pitch inverters, checked that the crane was seated properly, installed mudflaps on cables, could not check on sliprings due to winds being too high. Replaced Gearbox inline oil filter. | KRAYN-WKO-NDX-20100203 | 1
KRAYN-WKO-NDX-20100204-01 | No work order description provided by contractor | 2010-02-04 | 2010-02-04 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 20.2 | Forced | KRAYN-NDX-PRT-0725 | 1 | 5.1667 | Highland 1 | 7246.49 op hrs. Installed Updated Firmware, Installed 100W Slipring, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Confirmed Correct Parameters were Installed in Yaw Converter, Replaced GB Oil Filter, and Removed Vent Valves from Turbine Blade Bearings. | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100204-02 | No work order description provided by contractor | 2010-02-04 | 2010-02-04 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 20.2 | Forced | KRAYN-NDX-PRT-0725 | 1 | 5.1667 | Highland 1 | 7246.49 op hrs. Installed Updated Firmware, Installed 100W Slipring, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Confirmed Correct Parameters were Installed in Yaw Converter, Replaced GB Oil Filter, and Removed Vent Valves from Turbine Blade Bearings. | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100204-03 | No work order description provided by contractor | 2010-02-04 | 2010-02-04 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 20.2 | Forced | KRAYN-NDX-PRT-0725 | 1 | 5.1667 | Highland 1 | 7246.49 op hrs. Installed Updated Firmware, Installed 100W Slipring, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Confirmed Correct Parameters were Installed in Yaw Converter, Replaced GB Oil Filter, and Removed Vent Valves from Turbine Blade Bearings. | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100204-04 | No work order description provided by contractor | 2010-02-04 | 2010-02-04 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 20.2 | Forced | KRAYN-NDX-PRT-0725 | 1 | 5.1667 | Highland 1 | 7246.49 op hrs. Installed Updated Firmware, Installed 100W Slipring, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Confirmed Correct Parameters were Installed in Yaw Converter, Replaced GB Oil Filter, and Removed Vent Valves from Turbine Blade Bearings. | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100204-05 | firmware update | 2010-02-04 | 2010-02-04 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 11 | Planned |  |  | 3.4833 | Highland 1 | Updated Firmware, Confirmed 100W Slipring Installed, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Found Wrong Parameters in Yaw Converter-Installed Correct Parameters | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100204-06 | firmware update | 2010-02-04 | 2010-02-04 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 11 | Planned |  |  | 3.4833 | Highland 1 | Updated Firmware, Confirmed 100W Slipring Installed, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secured, Found Wrong Parameters in Yaw Converter-Installed Correct Parameters | KRAYN-WKO-NDX-20100204 | 1
KRAYN-WKO-NDX-20100205-01 | firmware update | 2010-02-05 | 2010-02-05 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 16 | Planned | KRAYN-NDX-PRT-0725 | 1 | 3.8 | Highland 1 | Updated Firmware, 100W Slipring Installed, Confirmed Both Yaw Motors Working Properly, Could not Reroute Induction Sensor Cable-Too Short, Installed Upper & Lower Cable Chaffing Guards, Secured Kelms Grips, Confirmed Heater Bolted Down, Confirmed Nacelle Crane Secure | KRAYN-WKO-NDX-20100205 | 1
KRAYN-WKO-NDX-20100210-01 | 400 volt | 2010-02-10 | 2010-02-13 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 72 | Forced | KRAYN-NDX-PRT-0725 | 1 | 90.6167 | Highland 1 | energized triped breakers and read faults problems are in the hub winds are to high to get in hub and winter warning blizzard was present. 2/12/10 Went up the turbine to change out the slipring and perform the check list. After the slipring change out we still had a pitch problem. The renew techs. put the mud flap on the hv cables. We were told to come down because of training purposes. Aroun 16:30 returned to the turbine and tried to get the blades to pitch because there were no faults. Bought some ethernet cables to see if there maybe a communication problem but found there was no problem there. Had to leave turbine down because it got to late. After the pitch boxes warmed up the turbine was started. Operation Hrs. 6216.64 | KRAYN-WKO-NDX-20100210 | 1
KRAYN-WKO-NDX-20100212-01 | hyd pump fuse fault | 2010-02-12 | 2010-02-13 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 12.3 | Forced | KRAYN-NDX-PRT-0259 | 1 | 11.35 | Highland 1 | turbine faulted for fuse trips we went up to find hyd motor was not working properly went through wiring checked our contacts and checked our breaker all appeared ok proceeded to change out motor and problem went away. | KRAYN-WKO-NDX-20100212 | 1
KRAYN-WKO-NDX-20100222-01 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.8 | Forced |  |  | 0.4 | Highland 1 | changed out upper fire extinguisher for type 3 annual maintenance | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-02 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 13 | Forced |  |  | 6.75 | Highland 1 | Performed SEG Maintanence in accordance with the procedures provided by Woodward SEG. I will be sending the triggers to SEG. Operating hrs. 8007.42 | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-03 | gearbox oil filter change out | 2010-02-22 | 2010-02-22 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.8667 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.93333 | Highland 1 | the turbine had a warning present that the gearbox oil filter needed changed it was 75 percent clogged this task was performed as well as a fire extinguisher change out | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-04 | gearbox oil filter change out | 2010-02-22 | 2010-02-22 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.8667 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.93333 | Highland 1 | the turbine had a warning present that the gearbox oil filter needed changed it was 75 percent clogged this task was performed as well as a fire extinguisher change out | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-05 | manaul stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.8667 | Forced |  |  | 0.93333 | Highland 1 | went up tower to exchange the fire extinguisher for annual type three maint. | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-06 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.6 | Forced |  |  | 0.8 | Highland 1 | went up tower to change out upper fire extinguiser for type three maintenance | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-07 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.76667 | Forced |  |  | 0.38333 | Highland 1 | went up tower to change out fire extinguisher for type three maint. | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-08 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.66667 | Forced |  |  | 0.33333 | Highland 1 | went up tower to exchange fir extinguisher for type three maintenance | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100222-09 | manual stop | 2010-02-22 | 2010-02-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.8 | Forced |  |  | 0.4 | Highland 1 | went up tower to exchange fire extinguisher for type three annual maintenance | KRAYN-WKO-NDX-20100222 | 1
KRAYN-WKO-NDX-20100223-01 | manual stop | 2010-02-23 | 2010-02-23 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0351 | 6 | 3.25 | Highland 1 | Performed SEG Maintanence in accordance with the procedures provided by Woodward SEG. I will be sending the triggers to SEG. Operating hrs. 5352.05 | KRAYN-WKO-NDX-20100223 | 1
KRAYN-WKO-NDX-20100223-02 | manual stop | 2010-02-23 | 2010-02-23 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0351 | 6 | 3.25 | Highland 1 | Performed SEG Maintanence in accordance with the procedures provided by Woodward SEG. I will be sending the triggers to SEG. Operating hrs. 5352.05 | KRAYN-WKO-NDX-20100223 | 1
KRAYN-WKO-NDX-20100224-01 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.73333 | Highland 1 | Rerouted and zip tied heater cable. Inspected cable mud flaps. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-02 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.86667 | Highland 1 | Rerouted and zip tied heater cable. Inspected cable mud flaps. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-03 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.86667 | Highland 1 | Rerouted and zip tied heater cable. Inspected cable mud flaps. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-04 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 5.9833 | Highland 1 | Installed cable mud flaps. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-05 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 5.9833 | Highland 1 | Installed cable mud flaps. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-06 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 0.93333 | Highland 1 | Installed cable mud flaps. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-07 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 0.93333 | Highland 1 | Installed cable mud flaps. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-08 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 0.68333 | Highland 1 | Installed cable mud flaps to prevent further cable chaffing. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-09 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 0.68333 | Highland 1 | Installed cable mud flaps to prevent further cable chaffing. Rerouted and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-10 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.4167 | Highland 1 | Installed mud flaps to prevent cable chaffing. Reroute and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-11 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.4167 | Highland 1 | Installed mud flaps to prevent cable chaffing. Reroute and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-12 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 2.0667 | Highland 1 | Installed mud flaps to prevent cable chaffing. Reroute and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-13 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 2.0667 | Highland 1 | Installed mud flaps to prevent cable chaffing. Reroute and zip tied heater cable. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-14 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.55 | Highland 1 | Rerouted and zip tied heater cable. Checked and photo documented cable mud flaps. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100224-15 | Manual Stop | 2010-02-24 | 2010-02-24 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.55 | Highland 1 | Rerouted and zip tied heater cable. Checked and photo documented cable mud flaps. | KRAYN-WKO-NDX-20100224 | 1
KRAYN-WKO-NDX-20100225-01 | IBS interbus stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 12.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 32.5 | Highland 1 | Changed out a 100 watt slipring due to a interbus stop.Changed the slipring to a 50 watt one taken from turbine 19. Operating hrs. 8007.3 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-02 | IBS interbus stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 12.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 32.5 | Highland 1 | Changed out a 100 watt slipring due to a interbus stop.Changed the slipring to a 50 watt one taken from turbine 19. Operating hrs. 8007.3 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-03 | IBS interbus stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 12.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 32.5 | Highland 1 | Changed out a 100 watt slipring due to a interbus stop.Changed the slipring to a 50 watt one taken from turbine 19. Operating hrs. 8007.3 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-04 | N/A | 2010-02-25 |  | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 6.75 | Highland 1 | Had to go back to the wind turbine to pull the Trigger files for the SEG maint. Because they were never pulled, Everpower wanted to leave the turbine down because of ice conditions and the wind turbine has to be running to pull triggers. There's no stop and start times because you have to have the wind turbine running. The operating hours are 8089.31 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-05 | IBS interbus stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 12.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 32.5 | Highland 1 | Changed out slipring due to an interbus stop | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-06 | IBS Interbus Stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0725 | 1 | 22.15 | Highland 1 | The slipring that was put in this turbine was a used slipring so there is no need to pull from stock but I included the serial numbers so we know what slipring is in this turbine. There is a 50 watt slipring installed in this turbine. The operating hours are 7012.12 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100225-07 | IBS Interbus Stop | 2010-02-25 | 2010-02-25 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0725 | 1 | 22.15 | Highland 1 | The slipring that was put in this turbine was a used slipring so there is no need to pull from stock but I included the serial numbers so we know what slipring is in this turbine. There is a 50 watt slipring installed in this turbine. The operating hours are 7012.12 | KRAYN-WKO-NDX-20100225 | 1
KRAYN-WKO-NDX-20100227-01 | Vib Y-direction eff stop | 2010-02-27 | 2010-02-27 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 10.5 | Forced | KRAYN-NDX-PRT-0416 | 1 | 17.25 | Highland 1 | Check vibration sensor on the bedplate. Found a bad module 174U2, changed it out and adjusted the set points on nc2 Operating hours.7511.60 | KRAYN-WKO-NDX-20100227 | 1
KRAYN-WKO-NDX-20100228-01 | Dicon. Dispite release for op. | 2010-02-28 | 2010-03-01 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 31 | Forced | KRAYN-NDX-PRT-0683,KRAYN-NDX-PRT-0682 | 1,2 | 22.5667 | Highland 1 | 2/28/10- Went to WTG and Powered down the Ground Cabinet to reset the Safety Chain Fault and checked the SEG convertor Faults and found that the generator Rpms were not registering on the Main Invertor. Because of the bad weather and drifting snow we left down till the next day. 3/01/10 Changed out the Generator encoder and in the process checked the generator slipring and found the generator grounding brushes were completely worn down and the grounding ring had some significant damage and there was movement of the brush while the ring spins. There was a generator brush warning on this turbine prior. The service techs informed the master tech and the acting manager of the problem and were told to clean and run the turbine. We also need a micro limit swith for the generator brush wear. | KRAYN-WKO-NDX-20100228 | 1
KRAYN-WKO-NDX-20100301-01 | Manual Stop | 2010-03-01 | 2010-03-01 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 1.1333 | Forced | KRAYN-NDX-PRT-0964 | 3.4Kg | 0.56667 | Highland 1 | Filled yaw gear auto luber with 3.4 Kg of cepplatyn, due to auto luber low warning. (Operation Hours:8179.68h) | KRAYN-WKO-NDX-20100301 | 1
KRAYN-WKO-NDX-20100301-02 | Manual Stop | 2010-03-01 | 2010-03-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0587 | 4 tubes | 0.66667 | Highland 1 | Filled generator auto luber with 1600 grams of Kluberlex, due to low auto luber. (Operation Hours: 6901.69h) | KRAYN-WKO-NDX-20100301 | 1
KRAYN-WKO-NDX-20100301-03 | Manual Stop | 2010-03-01 | 2010-03-01 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.36667 | Highland 1 | Reset auxillary oil filter breaker. Returned turnine to operation. (Operation Hours: 6901.69h) | KRAYN-WKO-NDX-20100301 | 1
KRAYN-WKO-NDX-20100302-01 | Manual Stop | 2010-03-02 | 2010-03-03 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0325 | 1 | 8.1333 | Highland 1 | Operation hours: 7597.69h. Replaced the in line oil filter, due to a clogged filter. (Operation Hours:7620.61h) | KRAYN-WKO-NDX-20100302 | 1
KRAYN-WKO-NDX-20100302-02 | Dicon. Dispite release for op. | 2010-03-02 | 2010-03-02 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3 | Highland 1 | Changed out Slipring due to it being damaged…..Example | KRAYN-WKO-NDX-20100302 | 1
KRAYN-WKO-NDX-20100302-03 | Manual Stop | 2010-03-02 | 2010-03-03 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 15 | Forced |  |  | 8.1333 | Highland 1 | Performed SEG maintenance according to the maintenance documents provided from SEG. We were not able to pull the trigger files needed for the Maint. Because either the HUR board's memory card is faulty or our company laptops are given the problem. We were directed to try to format the card and if that did not work change out the HUR board. We tried formating the card and it did not work and because of the low winds on site we were not able to change out the HUR board, because you have to re-commision the HUR board and to do that the turbine needs to be run up and the low winds prevented us from doing this. Nordex techs. will try again when the winds come up. Ater the maint. we were instructed to clean the generator micro switch to stop the generator brush warning and to take pictures of the slipring. The operation Hrs. are 7597.69.. | KRAYN-WKO-NDX-20100302 | 1
KRAYN-WKO-NDX-20100302-04 | Manual Stop | 2010-03-02 | 2010-03-02 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0167 | 1 | 2 | Highland 1 | Operation hours: 7244.79. Replaced emrgency stop above yaw deck, after finding broken cover on the old emergency stop. | KRAYN-WKO-NDX-20100302 | 1
KRAYN-WKO-NDX-20100303-01 | Manual Stop | 2010-03-03 | 2010-03-03 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 3.1667 | Highland 1 | Commisioned ice sensor and changed settings to match turbine one. Will await results before moving on to another turbine. Brought down U/H forward high-speed shroud and took to welding shop to be repaired. (Operation Hours: 7260.61h) | KRAYN-WKO-NDX-20100303 | 1
KRAYN-WKO-NDX-20100303-02 | Manual Stop | 2010-03-03 | 2010-03-03 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 4.3833 | Highland 1 | While performing the SEG maint. The turbine faulted with a FM 1172 Pitch Power Volt Fault because of the grid disconnect. The service techs went up turbine and had to reset pitch box number 1. Operating hours are 7860.04 | KRAYN-WKO-NDX-20100303 | 1
KRAYN-WKO-NDX-20100303-03 | Manual Stop | 2010-03-03 | 2010-03-03 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.2167 | Highland 1 | Inspected auxillary filter to find were leak was coming from. Found leak at coupler between the moter and pump. The seal in the coupler needs to be replace when the seal is in stock. The oil under the auxillary filter was cleaned along with the oil on the yaw deck. (Operation Hours: 7210.3h) | KRAYN-WKO-NDX-20100303 | 1
KRAYN-WKO-NDX-20100304-01 | Manual Stop | 2010-03-04 | 2010-03-04 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0325 | 1 | 1.1667 | Highland 1 | Replaced the in line oil filter, due to a clogged filter. (Operation Hours: 8179.68h) | KRAYN-WKO-NDX-20100304 | 1
KRAYN-WKO-NDX-20100304-02 | Manual Stop | 2010-03-04 | 2010-03-04 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0634 | 1 | 6.5667 | Highland 1 | Changed out the HUR board because while doing maint. On the SEG convertor we were unable to pull triggers. SEG told us to change out the HUR because that the memory card could not be reformated. So the service techs were directed to go back and finish the maint. operating hours are 7597.69 | KRAYN-WKO-NDX-20100304 | 1
KRAYN-WKO-NDX-20100304-03 | Yaw hyd brk not closed | 2010-03-04 | 2010-03-04 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.68333 | Highland 1 | Rerouted hydraulic heater cable and zip tied. Jumped out terminal X25 to activate yaw brake cylenoid. (Operation hours: 7891.09h) | KRAYN-WKO-NDX-20100304 | 1
KRAYN-WKO-NDX-20100304-04 | IBS Interbus Stop | 2010-03-04 | 2010-03-05 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 10.0667 | Highland 1 | Took apart old slipring and cleaned fingers and rings. Reassembled slip ring. Removed slip ring form 19. Installed slip ring that was refurbished in the shop. Returned turbine back to service. (Operation Hours: 7185.77h) | KRAYN-WKO-NDX-20100304 | 1
KRAYN-WKO-NDX-20100308-01 | Manual Stop | 2010-03-08 | 2010-03-08 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 14 | Forced | KRAYN-NDX-PRT-0666 | 1 | 1.7 | Highland 1 | Went to perform the SEG maint. On the 8th of March and was told by everpower that it was to late to power the pad mount down and were instructed to wait to the next day. On the 9th of March finished the SEG convertor maint and in the process of starting the wind turbine found that the aux.contact was bad on Q43P breaker. removed and replaced the contactor. Operation hrs are 8466.87 | KRAYN-WKO-NDX-20100308 | 1
KRAYN-WKO-NDX-20100308-02 | Pitchangle 2 Diff. Set-Act | 2010-03-08 | 2010-03-08 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 28.25 | Forced |  |  | 19.35 | Highland 1 | Rerouted hydraulic heater cable. Completed turbine checklist. Troubleshot Pitchnangle 2 dii. Set-act fault and Pitch power volt fault. Found broken blade bolt that was bouncing around in the hub. Found depressed emergency stop and broken pitch encoder gear form the bolt hitting them. Installed new gear on on pitch encoder and dialed in correct pitch angle the pitch encoder. The emergency stop was reset and the turbine was returned to service. (Operation Hours: 7018.34) | KRAYN-WKO-NDX-20100308 | 1
KRAYN-WKO-NDX-20100308-03 | Manual Stop | 2010-03-08 | 2010-03-08 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0031 | 1 | 3.15 | Highland 1 | Performed WTG checklist from 12:30 to 14:30 replaced the Aneometer and from 14:30 to 15:30 did the firmware update on the blades the SO number is 600013465 and from 15:30 to 16:00 checked the yaw convertor and yaw drives. The operation hours are 6638.39 | KRAYN-WKO-NDX-20100308 | 1
KRAYN-WKO-NDX-20100309-01 | Pitch Batt. Temp error | 2010-03-09 | 2010-03-09 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 16.5 | Forced |  |  | 15.2833 | Highland 1 | Troubleshot Pitch Batt. Temp error. Checked battery cabinet heater circuit. Found loose temperature sensor wire at the battery charger. Updated Firmware all three blades,confirmed yaw parameters were correct, confirmed both yaw motors working. Repaired wire and reinstalled back into the terminal block on the battery charger. Also completed turbine check list and rerouted hydraulic heater cable. (Operation Hours: 6861.83h) | KRAYN-WKO-NDX-20100309 | 1
KRAYN-WKO-NDX-20100310-01 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.21667 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8514.73 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-02 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.21667 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8758.48 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-03 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.16667 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8993.66 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-04 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.13333 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 7740.51 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-05 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.18333 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 7991.08 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-06 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.16667 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8377.17 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-07 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.15 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8011.09 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-08 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.18333 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 7915.42 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-09 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.13333 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 5695.09 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100310-10 | Manual Stop | 2010-03-10 | 2010-03-10 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.15 | Highland 1 | Had to Meg the stator cables to check the insulation value of the cables to finish the SEG maint. Operation hours are 8993.66 | KRAYN-WKO-NDX-20100310 | 1
KRAYN-WKO-NDX-20100311-01 | manual stop bad blade seal | 2010-03-11 | 2010-03-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 28.05 | Forced |  |  | 9.35 | Highland 1 | turbine was reported by the customer via email of grease on the outside of the blade, we prepared the tools we needed to fix the blade seal that was damaged. After inspection of the turbine the seal had 90 percent damage aroud the entire blade this is a very time consumming process to replace this seal. also while up tower we reinstalled the high speed cover on the turbine that had been removed and taken to a machine shop for repairsdue to cracks being on the cover | KRAYN-WKO-NDX-20100311 | 1
KRAYN-WKO-NDX-20100311-02 | No work order description provided by contractor | 2010-03-11 | 2010-03-11 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 3.25 | Highland 1 | Performed a SEG maintenance. 7065.46 operating hrs | KRAYN-WKO-NDX-20100311 | 1
KRAYN-WKO-NDX-20100311-03 | No work order description provided by contractor | 2010-03-11 | 2010-03-11 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 3.25 | Highland 1 | Performed a SEG maintenance. 7065.46 operating hrs | KRAYN-WKO-NDX-20100311 | 1
KRAYN-WKO-NDX-20100315-01 | ice dectection | 2010-03-15 | 2010-03-15 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3.2 | Forced |  |  | 4.5167 | Highland 1 | the tower faulted prematurely for ice, this is the second ice sensor on the farm that is bieng commissioned correctly. We went up tower and lowerd parameter settings to P00=040 / P01=060 these are the new settings. Also we had to perform an inspection on a blade seal that was worked on the previous week, to assure correct sealing of the blade bearing was met (7869.54) | KRAYN-WKO-NDX-20100315 | 1
KRAYN-WKO-NDX-20100315-02 | Manual Stop | 2010-03-15 | 2010-03-15 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0351 | 6 | 4.2 | Highland 1 | Performed SEG maint. According to the maint. Procedures provided by SEG Kemp services. 2 air filters on the IGBT's convertor cabinet had to be replaced. Also performed the pitch firmware update and the service report number is 600013461. | KRAYN-WKO-NDX-20100315 | 1
KRAYN-WKO-NDX-20100316-01 | Manual Stop | 2010-03-16 | 2010-03-16 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.2167 | Highland 1 | Checked the yaw motors and installed the mud flap on the generator cables.operation hrs are 8443.51 and the up tower time 1.5 hrs. | KRAYN-WKO-NDX-20100316 | 1
KRAYN-WKO-NDX-20100316-02 | Manual Stop | 2010-03-16 | 2010-03-16 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.68333 | Highland 1 | Installed the mud flap on the generator cables.operation hrs are 2662.05 and the up tower time .75 hrs. | KRAYN-WKO-NDX-20100316 | 1
KRAYN-WKO-NDX-20100316-03 | Manual Stop | 2010-03-16 | 2010-03-16 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.73333 | Highland 1 | Installed the mud flap on the generator cables.operation hrs are 5887.97and the up tower time .75 hrs. | KRAYN-WKO-NDX-20100316 | 1
KRAYN-WKO-NDX-20100316-04 | Manual Stop | 2010-03-16 | 2010-03-16 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.3833 | Highland 1 | Performed the firmware update on the pitch system. The operation hrs. are 7942.26, the up tower time is 1hr.. | KRAYN-WKO-NDX-20100316 | 1
KRAYN-WKO-NDX-20100317-01 | Pitch1 DC/DC link converter defect | 2010-03-17 | 2010-03-17 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.2667 | Forced |  |  | 0.63333 | Highland 1 | Went up tower and had to reset pitch converters, then came down and returned turbine to service. (opperating hours 8197) | KRAYN-WKO-NDX-20100317 | 1
KRAYN-WKO-NDX-20100317-02 | Grid Disconnect | 2010-03-17 | 2010-03-18 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 5.8667 | Forced |  |  | 2.9333 | Highland 1 | Went to turbine tried to power up got there and breakers where tripped. Went up tower and traced the line got to the hub then got called down for the night and the turbine was handed over to the next team on 3/18/10 | KRAYN-WKO-NDX-20100317 | 1
KRAYN-WKO-NDX-20100317-03 | Manual Stop | 2010-03-17 | 2010-03-17 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.56667 | Highland 1 | Installed mud flap on generator cables. Operation hrs are 7189.46 | KRAYN-WKO-NDX-20100317 | 1
KRAYN-WKO-NDX-20100317-04 | manual stop | 2010-03-17 | 2010-03-17 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 3.5667 | Forced |  |  | 1.7833 | Highland 1 | went up tower to replace an ultra sonic however our alignment tool did not fit proparly. We checked all cabling and cleaned off micro phones, then returned turbine to service (opperating hours 6829.07) | KRAYN-WKO-NDX-20100317 | 1
KRAYN-WKO-NDX-20100318-01 | LV Diff. Curr. 400v Stop | 2010-03-18 | 2010-03-18 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 9 | Forced | KRAYN-NDX-PRT-0725 | 1 | 23.5333 | Highland 1 | 8172.14 Operation Hours..On 3-17-10 techs. Came to the windturbine and found 34 F2,19 F2, 102 F3 was tripped.The techs. were instructed by the site supervisor to leave down till the next day because the techs. that were on site were at there 12 hr. mark. On 3-18-10 the techs. returned to the turbine and found that the all thread that holds the slipring in place while the turbine is running fell off. So the cables where the only means of stabalization for the slipring. Because of the slipring turning freely it caused a short on the 230Vac supply in which caused the breakers to trip. The techs. removed and replaced the damaged slipring. | KRAYN-WKO-NDX-20100318 | 1
KRAYN-WKO-NDX-20100318-02 | Right Anmo. Not reading | 2010-03-18 | 2010-03-18 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 13 | Forced | KRAYN-NDX-PRT-0603 | 1 | 6.3 | Highland 1 | Trouble shoot Ultra Sonic wind sensor issue. Checked voltages at at termial X8 33 and 34 brown and white wires from sensor. No voltage indicated, proceeded on changing wind sensor. Checked voltages again with new sensor, voltages at .5 VDC to 1.0 VDC. | KRAYN-WKO-NDX-20100318 | 1
KRAYN-WKO-NDX-20100319-01 | No work order description provided by contractor | 2010-03-19 | 2010-03-19 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 24 | Planned |  |  | 6.8 | Highland 1 | Performed a Seg maintenance operation hrs7518.71 | KRAYN-WKO-NDX-20100319 | 1
KRAYN-WKO-NDX-20100319-02 | No work order description provided by contractor | 2010-03-19 | 2010-03-19 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 24 | Planned |  |  | 6.8 | Highland 1 | Performed a Seg maintenance operation hrs7518.71 | KRAYN-WKO-NDX-20100319 | 1
KRAYN-WKO-NDX-20100319-03 | Manual Stop | 2010-03-19 | 2010-03-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 18 | Forced |  |  | 4.5333 | Highland 1 | Performed SEG maint. According to SEG procedures. | KRAYN-WKO-NDX-20100319 | 1
KRAYN-WKO-NDX-20100320-01 | Rotor Brake Pressure Fault | 2010-03-20 | 2010-03-21 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 2.5667 | Forced |  |  | 1.2833 | Highland 1 | We trouble shoot the rotor brake and found that the brake was clamping as soon as it would open. The hydraulic system checked out fine so we started working on the service hatch switch and found that it is making intermitten contacts. | KRAYN-WKO-NDX-20100320 | 1
KRAYN-WKO-NDX-20100321-01 | Manual Stop | 2010-03-21 | 2010-03-21 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 4.1333 | Forced | KRAYN-NDX-PRT-0011 | 1 | 2.0667 | Highland 1 | chaged out switch on service hatch cleaned the plunger and test the function of the switch.( Operating hours 8771.99) | KRAYN-WKO-NDX-20100321 | 1
KRAYN-WKO-NDX-20100322-01 | MI Class B Fault | 2010-03-22 | 2010-03-22 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0052,KRAYN-NDX-PRT-0260,KRAYN-NDX-PRT-0651,KRAYN-NDX-PRT-0052,KRAYN-NDX-PRT-0260 | 1,1,1,1,1 | 2.8833 | Highland 1 | Operation hours:5979.47 Came to wind turbine and found F 62V had blown. The techs pulled the trigger files to send to SEG and checked if there were any short to ground present. 3-23-10 the turbine faulted again for a MI class B fault and this time blew F 62 U fuse. Pulled the trigger files and sent to Kemp services and were instructed to change K 22 contactor. The technicians changed the F 62 U fuse and the contactor and put the turbine to run.Sure. If K22 does not work, then the current that would normally flow into the filter behind it now flows into the other one behind F62. And the addition of these two currents is too high for the F62 fuses. | KRAYN-WKO-NDX-20100322 | 1
KRAYN-WKO-NDX-20100322-02 | Pitch 3 Output stage temp stop | 2010-03-22 | 2010-03-22 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 9 | Forced |  |  | 42.2 | Highland 1 | operation hours: 8792.24 The problem started on the 11th of March and hard faulted on the 20th of March. The techs climbed the wind turbine and found the cooling fan defective in pitch 3, removed and replaced the defective cooling fan. Checked all the PT sensors and cables in pitch box 3. With NC2 checked the outstage temps and box temps and were all comparable to the other pitch boxes. We pulled the fan off of a new pitch convertor because the old convertor was operational. Repaired the new convertor with one that the fan was operational but the convertor was faulty. Up tower time:2 hrs | KRAYN-WKO-NDX-20100322 | 1
KRAYN-WKO-NDX-20100323-01 | Mannual Stop | 2010-03-23 | 2010-03-23 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3.2667 | Forced |  |  | 1.6333 | Highland 1 | Performed follow up gen grounding brush inspection took pictures which were sent to derek. ( Operating Hours 8051.80) | KRAYN-WKO-NDX-20100323 | 1
KRAYN-WKO-NDX-20100323-02 | Mannual Stop | 2010-03-23 | 2010-03-23 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3.2667 | Forced |  |  | 1.6333 | Highland 1 | Performed follow up gen grounding brush inspection took pictures which were sent to derek. ( Operating Hours 8051.80) | KRAYN-WKO-NDX-20100323 | 1
KRAYN-WKO-NDX-20100324-01 | No work order description provided by contractor | 2010-03-24 | 2010-03-24 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 0.28333 | Highland 1 | op hrs. 2852.64. Perform SEG maint. Pulled triggers. Called out of turbine due production requirements. | KRAYN-WKO-NDX-20100324 | 1
KRAYN-WKO-NDX-20100325-01 | gearbox oil filter | 2010-03-25 | 2010-03-25 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 8.4333 | Forced |  |  | 2.45 | Highland 1 | a gearbox oil filter was changed out also a noise was investagated inside the hub, nothing was found to be loose inside the hub returned turbine to service | KRAYN-WKO-NDX-20100325 | 1
KRAYN-WKO-NDX-20100325-02 | IBS Interbus stop | 2010-03-25 | 2010-03-26 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 15.75 | Forced |  |  | 23.2333 | Highland 1 | Turbine faulting on IBS interbus stop. Trouble shoot fault found slip ring in hub to be faulty. Replaced slip ring with a refurbished slip ring. | KRAYN-WKO-NDX-20100325 | 1
KRAYN-WKO-NDX-20100325-03 | No work order description provided by contractor | 2010-03-25 | 2010-03-25 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0351 | 4 | 4.1 | Highland 1 | Performed SEG Maint. 8522.30 op hrs | KRAYN-WKO-NDX-20100325 | 1
KRAYN-WKO-NDX-20100325-04 | Manual Stop | 2010-03-25 | 2010-03-25 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0351 | 2 | 4.4333 | Highland 1 | Performing SEG maintenance according to SEG protocol. Operation Hours:8858.37 While performing the SEG maint. Everpower found a blade bearing bolt on the ground beside the windturbine. Was instructed by the site supervisor to inspect the blade bearing bolts.Found only one bolt missing because it was never torqed. Uptower time is 1 hour. We also changed 2 filters for the SEG maint. on cab 1S2.. | KRAYN-WKO-NDX-20100325 | 1
KRAYN-WKO-NDX-20100325-05 | Manual Stop | 2010-03-25 | 2010-03-25 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0351 | 2 | 4.4333 | Highland 1 | Performing SEG maintenance according to SEG protocol. Operation Hours:8858.37 While performing the SEG maint. Everpower found a blade bearing bolt on the ground beside the windturbine. Was instructed by the site supervisor to inspect the blade bearing bolts.Found only one bolt missing because it was never torqed. Uptower time is 1 hour. We also changed 2 filters for the SEG maint. on cab 1S2.. | KRAYN-WKO-NDX-20100325 | 1
KRAYN-WKO-NDX-20100326-01 | Manual Stop | 2010-03-26 | 2010-03-26 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0980 | 2 | 2.4 | Highland 1 | Operation hours:7400.35 Climbed WTG 20 to inspect the vibration problem that SKF had reported to Everpower. Found missing bolts on the high speed shroud and checked the generator brushes. Run up the turbine to monitor the encoder readings and the rotor to see if there is a difference. Found that the generator slide ring on the grounding brushes has been worn.The technicians changed the 2 generator grounding brushes. | KRAYN-WKO-NDX-20100326 | 1
KRAYN-WKO-NDX-20100327-01 | Q43 Cool Water heater trip | 2010-03-27 | 2010-03-27 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.95 | Highland 1 | op.hrs8412.97. Called out to turbine. Found Q43 breaker for cool water heating was tripped. Resest breaker. Put turbine online monitored turbine for faults. | KRAYN-WKO-NDX-20100327 | 1
KRAYN-WKO-NDX-20100328-01 | Interbus stop | 2010-03-28 |  | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 19 | Forced | KRAYN-NDX-PRT-0323 | 1 | 23.2333 | Highland 1 | op hrs. 8413.34. Called out to turbine for FM 700 fault. Replaced 16X2 phoenix module for stripped out connections. Started turbine, turbine faulted on FM700 fault again. Contacted site lead for a slip ring. could not install slip ring due to bad weather(wind gusts to 17 m/s,high winds rain,and freezing rain). Monitored weather. Was called off site by site lead for weather conditions. | KRAYN-WKO-NDX-20100328 | 1
KRAYN-WKO-NDX-20100329-01 | No work order description provided by contractor | 2010-03-29 | 2010-03-29 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.5 | Highland 1 | op.hrs9208.45 Assisting SEG tech. with Q10P breaker retro. Fit. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-02 | No work order description provided by contractor | 2010-03-29 | 2010-03-29 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 1.9 | Highland 1 | Asisting SEG Tech with. Q15P breaker retro fit. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-03 | No work order description provided by contractor | 2010-03-29 | 2010-03-29 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.5 | Highland 1 | op.hrs9208.45 Assisting SEG tech. with Q10P breaker retro. Fit. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-04 | Pitch Comm Flt | 2010-03-29 | 2010-03-29 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 9.3 | Forced | KRAYN-NDX-PRT-0725 | 1 | 35.6667 | Highland 1 | Replaced slip ring, checked connections in hub and top box. Need to monitor slipring to see if further troubleshooting is needed for other possible cause of Comm failure. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-05 | interbus stop | 2010-03-29 | 2010-03-29 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 7.2333 | Forced | KRAYN-NDX-PRT-0725 | 1 | 29.9 | Highland 1 | turbine faulted for fm750 fm700 we checked multiple points through out turbines interbus and rnr slipring repaired problem (run time 8608.23) | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-06 | Yaw HYD Brake not Closed | 2010-03-29 | 2010-03-29 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0073 | 1 | 4.0667 | Highland 1 | Changed out hose insite Hydraulic tank due to a rurture in line. Problem was found due to slow rise is pressure in Yaw Brake during Wtg test. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-07 | Yaw HYD Brake not Closed | 2010-03-29 | 2010-03-29 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0073 | 1 | 4.0667 | Highland 1 | Changed out hose insite Hydraulic tank due to a rurture in line. Problem was found due to slow rise is pressure in Yaw Brake during Wtg test. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-08 | Yaw HYD Brake not Closed | 2010-03-29 | 2010-03-29 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0073 | 1 | 4.0667 | Highland 1 | Changed out hose insite Hydraulic tank due to a rurture in line. Problem was found due to slow rise is pressure in Yaw Brake during Wtg test. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100329-09 | Manual Stop | 2010-03-29 | 2010-03-29 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 9.5 | Forced | KRAYN-NDX-PRT-0634 | 1 | 3.8333 | Highland 1 | Operation Hours :7780.36 Performed SEG maintenance according to SEG protocol. While pulling trigger files could not connect to the HUR. The technicians tried re-formating the memory card but the problem still was there, Directed by SEG to change the HUR board. No up tower time on this turbine. | KRAYN-WKO-NDX-20100329 | 1
KRAYN-WKO-NDX-20100330-01 | interbus stop | 2010-03-30 | 2010-03-30 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 5.1333 | Forced |  |  | 3.5833 | Highland 1 | replaced a slipring in hub (run hours 3016.88) | KRAYN-WKO-NDX-20100330 | 1
KRAYN-WKO-NDX-20100330-02 | blade seal repair | 2010-03-30 | 2010-03-31 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 7.4667 | Forced |  |  | 3.3167 | Highland 1 | went up tower to repair a section of blade seal that had pulled out of the bearings exterior setting point (run hours 3016.88) | KRAYN-WKO-NDX-20100330 | 1
KRAYN-WKO-NDX-20100331-01 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 4.3333 | Forced |  |  | 1.2733 | Highland 1 | Went to Turbine 3 to perform Q15P retrofit. Production Hours were 9494.34 Hours. | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-02 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2.6667 | Forced |  |  | 1.0333 | Highland 1 | Went to Turbine 5 to perform Q15P retrofit. Production Hours were 8215 Hours. | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-03 | Mannual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 7.1 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0351 | 3,3 | 3.55 | Highland 1 | completed the SEG maint. Operation Hours 8996.30 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-04 | Mannual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 7.1 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0351 | 3,3 | 3.55 | Highland 1 | completed the SEG maint. Operation Hours 8996.30 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-05 | Mannual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 7.1 | Planned | KRAYN-NDX-PRT-0351 | 3 | 3.55 | Highland 1 | completed the SEG maint. Operation Hours 8996.30 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-06 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 0.92806 | Highland 1 | Went to Turbine 6 to perform Q15P retrofit. Production Hours were 7722 Hours. | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-07 | Manual Stop | 2010-03-31 | 2010-04-01 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 8.3333 | Forced | KRAYN-NDX-PRT-0260,KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0475 | 1,1,1 | 18.5567 | Highland 1 | Went to Turbine 8 to perform Q15P retrofit. Production Hours were 6246.8 Hours. Finished retrofit at 4:30, connected the turbine to the grid, but turbine faulted after a few minutes of grid connection. It Faulted for MI Class B error, ringline shutdown on the main inverter. We troubleshot and found the two Fuses F62U were blown. We called the shop to have new ones brought out. We replaced the fuses at 6:00. We tried to find the cause of the blown fuses but could not find anything. We tried to start the turbine again at 6:30. The turbine faulted this time before it even connected to the grid. This time the NC2 error was also MI class B, but the SEG error was Stator Contactor error. SEG personnel decided to send trigger files to Germany and try to fix again tomorrow. Turbine is still down. | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-08 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 14 | Forced |  |  | 5.8667 | Highland 1 | Performed SEG maintenance according to SEG protocol and updated the pitch firmware. The operation hours are :8464.75 Up tower time : 2hrs the SO number for the firmware update is: 600013456 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-09 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 14 | Forced |  |  | 5.8667 | Highland 1 | Performed SEG maintenance according to SEG protocol and updated the pitch firmware. The operation hours are :8464.75 Up tower time : 2hrs the SO number for the firmware update is: 600013456 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-10 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 14 | Forced |  |  | 5.8667 | Highland 1 | Performed SEG maintenance according to SEG protocol and updated the pitch firmware. The operation hours are :8464.75 Up tower time : 2hrs the SO number for the firmware update is: 600013456 | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100331-11 | Manual Stop | 2010-03-31 | 2010-03-31 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 4.1333 | Forced |  |  | 0.98333 | Highland 1 | Went to Turbine 4 to perform Q15P retrofit. Production Hours were 8797.41 Hours. | KRAYN-WKO-NDX-20100331 | 1
KRAYN-WKO-NDX-20100401-01 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.0667 | Highland 1 | Was told by the SEG rep. that the cooling fans were inop.. The technicians on site waited to see if the turbine needed to run a while until the maxium temp was reached for the thermostat to switch the fans on. When the techs. Came to inspect the fans they were still inop.. Troubleshot the cooling fans and found that the Z-8 filter has a bad phase and the fans were only receiving 180Vac instead of the 230Vac. The technicians wired into E11 Thermostat instead of the E4 thermostat because it was receiving the 230Vac that was needed to run the cooling fans because there is no Z-8 filters in stock. Both of the thermostats are set at 35 c.. The operation hours are:6275.42 | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-02 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3.3333 | Forced |  |  | 1.2989 | Highland 1 | Went to Turbine 9 to perform Q15P retrofit. Production Hours were 6842 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-03 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3.3333 | Forced |  |  | 1.2989 | Highland 1 | Went to Turbine 9 to perform Q15P retrofit. Production Hours were 6842 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-04 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 5.3333 | Forced |  |  | 2.7561 | Highland 1 | Went to Turbine 10 to perform Q15P retrofit. Turbine was already down for FE866 "Air Temp CtrlCab H Stop". Turbine failed for FE866 at 16:09:40. Q15P was installed before temp problem was fixed, so turbine remained down. At 3:00 PM, Mark V and UT arrived to flip breaker in top cabinet to fix temp problem. Turbine was restarted at 19:37 Turbine time. Production Hours were 8468 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-05 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 2.3333 | Forced |  |  | 0.84 | Highland 1 | Went to Turbine 11 to perform Q15P retrofit. Production Hours were 8319 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-06 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2.0333 | Forced |  |  | 0.84361 | Highland 1 | Went to Turbine 12 to perform Q15P retrofit. Production Hours were 8901 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-07 | Manual Stop | 2010-04-01 | 2010-04-01 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 8.4 | Forced |  |  | 2.4419 | Highland 1 | Went to Turbine 13 to perform Q15P retrofit. When retrofit was finished at 6:00 PM, Turbine would not restart due to Pitch converter faults. Dustin and Eric came to go up tower and fix the problem because Paul had to leave. Production Hours were 8530 Hours. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-08 | top box overheat | 2010-04-01 | 2010-04-01 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 5.9 | Forced |  |  | 2.95 | Highland 1 | work Performed up tower was a breaker needed to be switched bak on on the top box cooler (run hours 8714.44) | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100401-09 | MI class B fault | 2010-04-01 | 2010-04-01 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0012 | 2 | 4.6667 | Highland 1 | The turbine was faulting for a MI Temp H stop in which was giving the class B fault. The operation hours are:7398.26 Checked the cooling Fans and pump all checked good. The pressure of the cooling system was 2.5 bar which is good. Cleaned the SEG cab filters because there was a significant amount of dirt on them, which could have been the root of the problem. | KRAYN-WKO-NDX-20100401 | 1
KRAYN-WKO-NDX-20100402-01 | mi class b | 2010-04-02 | 2010-04-02 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 11.1333 | Forced |  |  | 4.55 | Highland 1 | this turbine had an over tempature on the top box before we could get to the turbine it had faulted for a mi class b fm1208. we have had previous problems with this convertor system we pulled triggers on convertor and checked previous known errors for problems and for errors, none where present returned turbine to service. (run hours 6319.84) | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100402-02 | mi class b | 2010-04-02 | 2010-02-04 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 11.1333 | Forced |  |  | 4.55 | Highland 1 | this turbine had an over tempature on the top box before we could get to the turbine it had faulted for a mi class b fm1208. we have had previous problems with this convertor system we pulled triggers on convertor and checked previous known errors for problems and for errors, none where present returned turbine to service. (run hours 6319.84) | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100402-03 | manual stop | 2010-04-02 | 2010-04-02 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.73333 | Forced |  |  | 0.36667 | Highland 1 | we went up turbine to adjust the ac units up tower in the top box (run hours 8510.98) | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100402-04 | Pitchangle 2 Diff Set- RedAct | 2010-04-02 | 2010-04-03 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0558 | 1 | 3.6 | Highland 1 | At 6 PM turbine 15 went down for FE1142, Pitch 2 Different actual-redundant. Turbine was reset and worked for a few minutes but then went down again. After analyzing fast logs, it was decided the Cam 2 switch was bad. We went to the shop to get a replacement, and pick up tools, then went and replaced the Cam switch. Turbine was brought back online at 10:09 and has been working since. Production hours 6250 Hours. | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100402-05 | manual stop | 2010-04-02 | 2010-04-02 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.5 | Highland 1 | work Performed up tower was a breaker needed to be switched bak on on the top box cooler (run hours 8058.22) | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100402-06 | manual stop | 2010-04-02 | 2010-04-02 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.43333 | Forced |  |  | 0.21667 | Highland 1 | work Performed up tower was a breaker needed to be switched bak on on the top box cooler (run hours 7385.84) | KRAYN-WKO-NDX-20100402 | 1
KRAYN-WKO-NDX-20100404-01 | no communicatiuon | 2010-04-04 |  | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 3.3167 | Highland 1 | this turbine never faulted but had lost communication through NC2 we went to the turbine and reset the LPC communication came back and turbine was fine. (run hours 6139.84) | KRAYN-WKO-NDX-20100404 | 1
KRAYN-WKO-NDX-20100404-02 | no communicatiuon | 2010-04-04 |  | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 3.3167 | Highland 1 | this turbine never faulted but had lost communication through NC2 we went to the turbine and reset the LPC communication came back and turbine was fine. (run hours 6139.84) | KRAYN-WKO-NDX-20100404 | 1
KRAYN-WKO-NDX-20100406-01 | Manual Stop | 2010-04-06 | 2010-04-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 9.7 | Planned | KRAYN-NDX-PRT-0351 | 2 | 3.2167 | Highland 1 | Stopped Turbine to perform SEG Maintenance. operation hours 6367.80hrs | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-02 | Manual Stop | 2010-04-06 | 2010-04-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 9.7 | Planned | KRAYN-NDX-PRT-0351 | 2 | 3.2167 | Highland 1 | Stopped Turbine to perform SEG Maintenance. operation hours 6367.80hrs | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-03 | SEG MAINTENANCE | 2010-04-06 | 2010-04-06 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 9.7 | Forced |  |  | 3.2167 | Highland 1 | operation hours 6367.80hrs | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-04 | Vib Vdir Eff Stop | 2010-04-06 | 2010-04-06 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0172 | 1 | 6.1 | Highland 1 | Ophrs. 6164.68 Turbine faulting on FE57 Vib V Eff Stop. Tried to recalibrate vibration sensor via NC2, sensor would not calibrate. Replaced sensor. | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-05 | Vib V Dir Eff. Stop | 2010-04-06 | 2010-04-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0172 | 1 | 4.5667 | Highland 1 | Ophrs. 6164.68 Turbine faulted on FE 57 Vib V Dif Eff. Stop. Tried to recalibrate vibration sensor via NC2 sensor would not calibrate. Replaced sensor. | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-06 | Vib V Dir Eff. Stop | 2010-04-06 | 2010-04-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0172 | 1 | 4.5667 | Highland 1 | Ophrs. 6164.68 Turbine faulted on FE 57 Vib V Dif Eff. Stop. Tried to recalibrate vibration sensor via NC2 sensor would not calibrate. Replaced sensor. | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100406-07 | MI Class B Fault | 2010-04-06 | 2010-04-06 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 19 | Forced |  |  | 8.0833 | Highland 1 | The technicians arrived at the turbine to perform SEG maint. And while pulling the trigger files the turbine faulted for a MI class B fault. The Class B fault is due to a high temperature problem. Troubleshot the high temperature problem and found the fan for the water cooler was inop.. The technicians were unable to perform the SEG maintenance due to this problem. Changed the cooling fan motor and the motor was a used motor from another turbine so there for no sap number is needed. Operation hrs: 7513.65 | KRAYN-WKO-NDX-20100406 | 1
KRAYN-WKO-NDX-20100407-01 | Manual Stop | 2010-04-07 | 2010-04-07 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 16 | Planned | KRAYN-NDX-PRT-0682 | 2 | 6.4908 | Highland 1 | Replaced Generator Grounding Brush, per SKF indications. Gen.bush wear warning not active on the turbine. Excessive and asymetrical wear was noted on the grounding ring. Inspected rotor slipring per EverPower. At 4:30PM Thill and Edelson left the turbine as Haller, Bartee, and Wigglesworth arrived for uptower saftey training. | KRAYN-WKO-NDX-20100407 | 1
KRAYN-WKO-NDX-20100407-02 | Manual Stop | 2010-04-07 | 2010-04-07 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 16 | Planned |  |  | 2.2667 | Highland 1 | operation hrs: 6184.27 The technicians stopped the wind turbine to perform a yaw brake pad removal and instalation. Cleaned the yaw brake disc and calipers. Unable to perform the task due to a faulty hytorq pump. The up tower time is 2 hrs.. | KRAYN-WKO-NDX-20100407 | 1
KRAYN-WKO-NDX-20100408-01 | Manual Stop | 2010-04-08 | 2010-04-08 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0043 | 1 | 3.1264 | Highland 1 | Replaced Fuse in the inter bus ST module 105A2 in the top box. 8405 Hours | KRAYN-WKO-NDX-20100408 | 1
KRAYN-WKO-NDX-20100408-02 | Gen Rot Rpm Diff H Stop | 2010-04-08 | 2010-04-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0351 | 4 | 2.1833 | Highland 1 | Adjusted Rotor sensors on the low speed shaft. Op Hrs 8606.79 | KRAYN-WKO-NDX-20100408 | 1
KRAYN-WKO-NDX-20100408-03 | Manual Stop | 2010-04-08 | 2010-04-08 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0325 | 1 | 2.25 | Highland 1 | operation hrs:8016.82 Shut the WTG down because of the gearbox oil filter 75% clogged warning. Changed out the gearbox oil filter. Up tower Time:1 hr the service lifts cable guide fell off the ladder. The technicians had to reinstall the cable guide. | KRAYN-WKO-NDX-20100408 | 1
KRAYN-WKO-NDX-20100409-01 | No work order description provided by contractor | 2010-04-09 | 2010-04-09 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.6333 | Forced |  |  | 2.3333 | Highland 1 | the turbine faulted for ice detection, there are no more parameters to change to lesson sensitivity Nordex service team was instructed to dissconnect the sensor for time being until ice sensor issue is resolved. Operation hours 8537.40 | KRAYN-WKO-NDX-20100409 | 1
KRAYN-WKO-NDX-20100409-02 | Ice Detection | 2010-04-09 | 2010-04-09 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.6333 | Forced |  |  | 2.3333 | Highland 1 | the turbine faulted for ice detection, there are no more parameters to change to lesson sensitivity Nordex service team was instructed to dissconnect the sensor for time being until ice sensor issue is resolved. Operation hours 8537.40 | KRAYN-WKO-NDX-20100409 | 1
KRAYN-WKO-NDX-20100409-03 | Manual Stop | 2010-04-09 | 2010-04-09 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 57 | Forced |  |  | 10.4167 | Highland 1 | Went to Turbine 18 to do a complete brake job since the yaw brakes were sqealing. Sean, BJ, AJ and Mark left the shop at 730 am. Got to turbine at 8:30. We were up tower the entire time. Eric and Dustin left the shop at 11 to bring us supplies. Eric stayed with us until 6, dustin went to get us more supplies, brought it back, and then went back to the shop. Aj, Sean, BJ and Mark were uptower from 9 AM to 6:30 PM. Eric was up tower 12pm to 5 pm Turbine hours 6229 | KRAYN-WKO-NDX-20100409 | 1
KRAYN-WKO-NDX-20100410-01 | Yaw Hyd Brk not closed | 2010-04-10 | 2010-04-10 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.1333 | Highland 1 | The technicians went to the down turbine to troubleshot the yaw break fault and found that the valve was stuck for the yaw brake. We jumped the valve out at the yaw convertor to acctuate the sticky valve. Up tower time: .5 Operation hrs:9100.20 | KRAYN-WKO-NDX-20100410 | 1
KRAYN-WKO-NDX-20100410-02 | Yaw Hyd Brk not closed | 2010-04-10 | 2010-04-10 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.1333 | Highland 1 | The technicians went to the down turbine to troubleshot the yaw break fault and found that the valve was stuck for the yaw brake. We jumped the valve out at the yaw convertor to acctuate the sticky valve. Up tower time: .5 Operation hrs:9100.20 | KRAYN-WKO-NDX-20100410 | 1
KRAYN-WKO-NDX-20100412-01 | Manual Stop | 2010-04-12 | 2010-04-12 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 7.5667 | Planned |  |  | 2.8667 | Highland 1 | Performed SEG maintenance on WTG09. Did not complete due to not able to pull trigers per SEG manual due to no wind. After completing the SEG Maintenance and attempted to pull triggers the HUR does not function properly due to bad memmory card.m The Turbine is operating properly other than that problem with the memmory of the HUR. No Climbing hours all work performed down tower. 7104.22 operation hours. no partrs used. | KRAYN-WKO-NDX-20100412 | 1
KRAYN-WKO-NDX-20100412-02 | Manual Stop | 2010-04-12 | 2010-04-12 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 7.5667 | Planned |  |  | 2.8667 | Highland 1 | Performed SEG maintenance on WTG09. Did not complete due to not able to pull trigers per SEG manual due to no wind. After completing the SEG Maintenance and attempted to pull triggers the HUR does not function properly due to bad memmory card.m The Turbine is operating properly other than that problem with the memmory of the HUR. No Climbing hours all work performed down tower. 7104.22 operation hours. no partrs used. | KRAYN-WKO-NDX-20100412 | 1
KRAYN-WKO-NDX-20100412-03 | Manual Stop | 2010-04-12 | 2010-04-12 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 0.92222 | Highland 1 | Sean and Aaron went to turbine 23 to perform SEG maintenance. We asked John Bennet several times before leaving the shop if he had everything we needed for the work, he said yes and that he wanted the maintenance done. We shut down the turbine around 8:50 and prepared it for disconnection from the grid, and then waited for John. After waiting about a half hour John got in touch with us and told us he did not have enough grounding cables to shut off the pad mount, and we could not perform the maintenance. We went to turn the turbine back on but the server was down and we could not access the turbine. We had to wait for the Server to be reset, and then we restarted the turbine at 9:45. Turbine hours 7649 | KRAYN-WKO-NDX-20100412 | 1
KRAYN-WKO-NDX-20100412-04 | Manual Stop | 2010-04-12 | 2010-04-12 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 0.92222 | Highland 1 | Sean and Aaron went to turbine 23 to perform SEG maintenance. We asked John Bennet several times before leaving the shop if he had everything we needed for the work, he said yes and that he wanted the maintenance done. We shut down the turbine around 8:50 and prepared it for disconnection from the grid, and then waited for John. After waiting about a half hour John got in touch with us and told us he did not have enough grounding cables to shut off the pad mount, and we could not perform the maintenance. We went to turn the turbine back on but the server was down and we could not access the turbine. We had to wait for the Server to be reset, and then we restarted the turbine at 9:45. Turbine hours 7649 | KRAYN-WKO-NDX-20100412 | 1
KRAYN-WKO-NDX-20100413-01 | Manual Stop | 2010-04-13 | 2010-04-13 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 50.5 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 6.8597 | Highland 1 | Went to turbine 5 to replace old yaw motors with 2 new motors. All of us went so we could see the process, make sure we had enough help, and make sure we are prepared to do many more. We left the shop at 10:30, got to the turbine at 11. Eric and Aj went up tower at 11, everyone else came up at 11:30. Mark and BJ left at 4, everyone else left at 5. We returned to the shop at 6, home at 6:30. An error in the parameter file caused a delay, as well as a problematic wire. Turbine was yawing correctly both directlions when we left. 8520 Hours. | KRAYN-WKO-NDX-20100413 | 1
KRAYN-WKO-NDX-20100413-02 | Manual Stop | 2010-04-13 | 2010-04-13 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0399 | 1 | 1.1333 | Highland 1 | Operation Hours:9168.99 The windturbine was faulting for a yaw brake not closed fault prior. The technicians changed electro valve position 210, ran some tests and all checked good. Uptower time is 1 hr.. | KRAYN-WKO-NDX-20100413 | 1
KRAYN-WKO-NDX-20100414-01 | Manual Stop | 2010-04-14 | 2010-04-14 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 7.0339 | Highland 1 | Changed out Ywa Drive Motors 1 / 2. Problem was found with the Wiring of Brake Feedback Micro Switch in the Motor Junction Box from factory. | KRAYN-WKO-NDX-20100414 | 1
KRAYN-WKO-NDX-20100414-02 | Manual Stop | 2010-04-14 | 2010-04-14 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 7.0339 | Highland 1 | Changed out Ywa Drive Motors 1 / 2. Problem was found with the Wiring of Brake Feedback Micro Switch in the Motor Junction Box from factory. | KRAYN-WKO-NDX-20100414 | 1
KRAYN-WKO-NDX-20100414-03 | MANUAL STOP | 2010-04-14 | 2010-04-14 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 21 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 6.6461 | Highland 1 | 9132 hrs Replaced 2 yaw motors on turbine per corporate office. Followed procedures and jcompleted job In Acordinance with AWP. Programmed ABB Yaw converter and tested. Climbing hours for all techs = | KRAYN-WKO-NDX-20100414 | 1
KRAYN-WKO-NDX-20100414-04 | MANUAL STOP | 2010-04-14 | 2010-04-14 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 21 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 6.6461 | Highland 1 | 9132 hrs Replaced 2 yaw motors on turbine per corporate office. Followed procedures and jcompleted job In Acordinance with AWP. Programmed ABB Yaw converter and tested. Climbing hours for all techs = | KRAYN-WKO-NDX-20100414 | 1
KRAYN-WKO-NDX-20100415-01 | No work order description provided by contractor | 2010-04-15 | 2010-04-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 36.75 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 21.9667 | Highland 1 | Replaced yaw motors. Had problem with the mirco switch for the brake in on the motor took awhile to adjust. Hit our 12 hr mark had to come back in the day day to finnish adjustment 9350.21 op hrs | KRAYN-WKO-NDX-20100415 | 1
KRAYN-WKO-NDX-20100415-02 | MANUAL STOP | 2010-04-15 | 2010-04-15 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 14.25 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 4.4725 | Highland 1 | 9614hrs. Replaced 2 yaw motors on turbine per corporate office. Followed procedures and jcompleted job In Acordinance with AWP. Programmed ABB Yaw converter and tested. Upon making repairs on WTG found roof latch in botom of Nacelle and had been reinstalled. Climbing hours for all techs Hours uptower form 9am to 13:15= 4hr15min | KRAYN-WKO-NDX-20100415 | 1
KRAYN-WKO-NDX-20100415-03 | Yaw motor brake not closed | 2010-04-15 | 2010-04-15 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.3494 | Highland 1 | 9149.57 hours Yaw motor brake closed fault caused by microswitch not funcioning properly. Microswitch has a weather boot that was preventing microswitch to funtion properly. Reconfigured weather boot and tested. WTG in operation upon departure. 1hr per technician for climb time. | KRAYN-WKO-NDX-20100415 | 1
KRAYN-WKO-NDX-20100415-04 | Yaw motor brake not closed | 2010-04-15 | 2010-04-15 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.3494 | Highland 1 | 9149.57 hours Yaw motor brake closed fault caused by microswitch not funcioning properly. Microswitch has a weather boot that was preventing microswitch to funtion properly. Reconfigured weather boot and tested. WTG in operation upon departure. 1hr per technician for climb time. | KRAYN-WKO-NDX-20100415 | 1
KRAYN-WKO-NDX-20100416-01 | FM415 Yaw brake not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.5667 | Highland 1 | adjusted micro switch and checked wire connections. Op hrs 9407.54 | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100416-02 | Yaw break not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 2.7167 | Highland 1 | 9364.05 HOURS OF OPERATION. Replaced faulty microswitch on Yaw Motor #1 and tested. Switch was sticking. Tested switch. Turbine in operation upon leaving. Climbing time 2hours for each technician. | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100416-03 | Yaw break not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 2.7167 | Highland 1 | 9364.05 HOURS OF OPERATION. Replaced faulty microswitch on Yaw Motor #1 and tested. Switch was sticking. Tested switch. Turbine in operation upon leaving. Climbing time 2hours for each technician. | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100416-04 | FM415 Yaw brake not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.5667 | Highland 1 | adjusted micro switch and checked wire connections. Op hrs 9407.54 | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100416-05 | FM 414 Yaw brake not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 4.3333 | Highland 1 | went up investigated problem, found wires were not fully landed on strip. Relanded all wires turbine went online. Op Hrs 9237.75 We had 1 Hr of up tower time | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100416-06 | FM 414 Yaw brake not closed | 2010-04-16 | 2010-04-16 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 4.3333 | Highland 1 | went up investigated problem, found wires were not fully landed on strip. Relanded all wires turbine went online. Op Hrs 9237.75 We had 1 Hr of up tower time | KRAYN-WKO-NDX-20100416 | 1
KRAYN-WKO-NDX-20100419-01 | Manual Stop | 2010-04-19 | 2010-04-19 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 8.1333 | Forced | KRAYN-NDX-PRT-0782 | 1 | 4.0667 | Highland 1 | Changed out Yaw Motor Due to Repeated Yaw Mtr Brake Errors. | KRAYN-WKO-NDX-20100419 | 1
KRAYN-WKO-NDX-20100419-02 | Manual Stop | 2010-04-19 | 2010-04-19 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 8.1333 | Forced | KRAYN-NDX-PRT-0782 | 1 | 4.0667 | Highland 1 | Changed out Yaw Motor Due to Repeated Yaw Mtr Brake Errors. | KRAYN-WKO-NDX-20100419 | 1
KRAYN-WKO-NDX-20100419-03 | Manual Stop | 2010-04-19 | 2010-04-19 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 0.66667 | Forced | KRAYN-NDX-PRT-0172 | 1 | 0.33333 | Highland 1 | changed vibe switch opperating hours (6450.18) | KRAYN-WKO-NDX-20100419 | 1
KRAYN-WKO-NDX-20100419-04 | PITCH 1 ANGLE DIFFERENCE | 2010-04-19 | 2010-04-19 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 9 | Forced | KRAYN-NDX-PRT-0725 | 1 | 51.5167 | Highland 1 | 8297.03 HOURS OF OPERATION.Troubleshot Wind turbine and found yet another bad slipring. Replaced Slipring in WTG and tested per AWP. Also while on WTG extracted the broken screw for the vibration sensor near the service hatch and installed a new screw. WTG Running upon Departure. Climbing hours 4 hours each for both technicians. | KRAYN-WKO-NDX-20100419 | 1
KRAYN-WKO-NDX-20100419-05 | PITCH 1 ANGLE DIFFERENCE | 2010-04-19 | 2010-04-19 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 9 | Forced | KRAYN-NDX-PRT-0725 | 1 | 51.5167 | Highland 1 | 8297.03 HOURS OF OPERATION.Troubleshot Wind turbine and found yet another bad slipring. Replaced Slipring in WTG and tested per AWP. Also while on WTG extracted the broken screw for the vibration sensor near the service hatch and installed a new screw. WTG Running upon Departure. Climbing hours 4 hours each for both technicians. | KRAYN-WKO-NDX-20100419 | 1
KRAYN-WKO-NDX-20100420-01 | manual stop | 2010-04-20 | 2010-04-20 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.1333 | Highland 1 | turbine has had multiple 744 warnings and has faulted for fm 700 and fm750 in the last week. We went up to inspect the turbine we where accompinied by Everpower John Bennett. | KRAYN-WKO-NDX-20100420 | 1
KRAYN-WKO-NDX-20100423-01 | No work order description provided by contractor | 2010-04-23 | 2010-04-23 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.6 | Highland 1 | Window at the top of the naccelle had a hole in it had to make a quick repair until maintenance. op hrs 9490.26. All technician hrs are uptower hours | KRAYN-WKO-NDX-20100423 | 1
KRAYN-WKO-NDX-20100426-01 | Maintenance | 2010-04-26 | 2010-04-26 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 35.25 | Planned |  |  | 6.7 | Highland 1 | 8822.65 op hrs | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100426-02 | Manual Stop | 2010-04-26 | 2010-04-26 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 4.3333 | Forced |  |  | 1.0372 | Highland 1 | Went to Turbine 7 to perform Q15P retrofit. Left shop at 9am arrived at turbine at 9:40. Production Hours were 3632 Hours. | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100426-03 | Manual Stop | 2010-04-26 | 2010-04-26 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.90139 | Highland 1 | Went to Turbine 14 to perform Q15P retrofit. Production Hours were 9034 Hours. | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100426-04 | Manual Stop | 2010-04-26 | 2010-04-26 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 2.3333 | Forced |  |  | 0.8675 | Highland 1 | Went to Turbine 15 to perform Q15P retrofit. Production Hours were 6795 Hours. | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100426-05 | Manual Stop | 2010-04-26 | 2010-04-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 0.83333 | Highland 1 | Went to Turbine 16 to perform Q15P retrofit. Production Hours were 9073 Hours. | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100426-06 | Manual Stop | 2010-04-26 | 2010-04-26 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 0.89 | Highland 1 | Went to Turbine 17 to perform Q15P retrofit. Personnel hours include drive back to shop. Production Hours were 9253 Hours. | KRAYN-WKO-NDX-20100426 | 1
KRAYN-WKO-NDX-20100427-01 | Maintenance | 2010-04-27 | 2010-04-27 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 42.25 | Planned |  |  | 7.7667 | Highland 1 | 8839.96 op hrs | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-02 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.3333 | Forced |  |  | 0.96306 | Highland 1 | Went to Turbine 18 to perform Q15P retrofit. Production Hours were 6633 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-03 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2.6667 | Forced |  |  | 0.90194 | Highland 1 | Went to Turbine 19 to perform Q15P retrofit. Production Hours were 8385 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-04 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.94667 | Highland 1 | Went to Turbine 20 to perform Q15P retrofit. Production Hours were 8161 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-05 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.1667 | Forced |  |  | 0.85694 | Highland 1 | Went to Turbine 21 to perform Q15P retrofit. Personnel hours include drive from the shop. Production Hours were 8471 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-06 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.82139 | Highland 1 | Went to Turbine 22 to perform Q15P retrofit. Production Hours were 8466 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-07 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 0.92639 | Highland 1 | Went to Turbine 23 to perform Q15P retrofit. Production Hours were 8004 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-08 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2.1667 | Forced |  |  | 0.77861 | Highland 1 | Went to Turbine 24 to perform Q15P retrofit. Production Hours were 8183 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100427-09 | Manual Stop | 2010-04-27 | 2010-04-27 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 0.90333 | Highland 1 | Went to Turbine 25 to perform Q15P retrofit. Personnel time includes drive back to the shop. Production Hours were 7766 Hours. | KRAYN-WKO-NDX-20100427 | 1
KRAYN-WKO-NDX-20100428-01 | Maintenance | 2010-04-28 | 2010-04-28 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 29.25 | Planned |  |  | 5.4 | Highland 1 | 8855.81 Op hrs | KRAYN-WKO-NDX-20100428 | 1
KRAYN-WKO-NDX-20100429-01 | Manual Stop | 2010-04-29 | 2010-04-29 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2.55 | Forced |  |  | 2.55 | Highland 1 | Working with LM to repair blade tips work was not performed due to high winds. | KRAYN-WKO-NDX-20100429 | 1
KRAYN-WKO-NDX-20100429-02 | Maintenance | 2010-04-29 | 2010-04-29 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 55 | Planned |  |  | 9.5167 | Highland 1 | 8864.62 op hrs | KRAYN-WKO-NDX-20100429 | 1
KRAYN-WKO-NDX-20100429-03 | IBS ibterbus stop | 2010-04-29 | 2010-04-29 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 15 | Forced |  |  | 6.3839 | Highland 1 | Production HRS 7832.17. Investigate and troubleshoot FM700 -IBS interbus stop. On initial entrance to the Hub discover broken bolt from Blade 3. Damages include: pitch gear piping bent, several grease bottle broken off, dents on all 3 pitch boxes and cosmetic damage to hub paint. Clean and repair faulty slipring USDK 248.1 {29-1846-0839}. | KRAYN-WKO-NDX-20100429 | 1
KRAYN-WKO-NDX-20100429-04 | IBS ibterbus stop | 2010-04-29 | 2010-04-29 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 15 | Forced |  |  | 6.3839 | Highland 1 | Production HRS 7832.17. Investigate and troubleshoot FM700 -IBS interbus stop. On initial entrance to the Hub discover broken bolt from Blade 3. Damages include: pitch gear piping bent, several grease bottle broken off, dents on all 3 pitch boxes and cosmetic damage to hub paint. Clean and repair faulty slipring USDK 248.1 {29-1846-0839}. | KRAYN-WKO-NDX-20100429 | 1
KRAYN-WKO-NDX-20100430-01 | Manual Stop | 2010-04-30 | 2010-04-30 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.6667 | Forced |  |  | 3.6667 | Highland 1 | Working with LM to repair blade tips went up tower then LM went down the bladed and performed there repair. | KRAYN-WKO-NDX-20100430 | 1
KRAYN-WKO-NDX-20100430-02 | Maintenance | 2010-04-30 | 2010-04-30 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 57.3667 | Planned |  |  | 10.4167 | Highland 1 | 8902.16 op hrs | KRAYN-WKO-NDX-20100430 | 1
KRAYN-WKO-NDX-20100430-03 | Manual Stop | 2010-04-30 | 2010-04-30 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3.5833 | Forced |  |  | 3.5833 | Highland 1 | Working with LM to repair blade tips went up tower then LM went down the bladed and performed there repair on two blades. | KRAYN-WKO-NDX-20100430 | 1
KRAYN-WKO-NDX-20100501-01 | Manual Stop | 2010-05-01 | 2010-05-01 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 4.3 | Forced |  |  | 4.3 | Highland 1 | Working with LM to repair blade tips went up tower then LM went down the bladed and performed there repair. | KRAYN-WKO-NDX-20100501 | 1
KRAYN-WKO-NDX-20100501-02 | Air Cabinet Control Cabinet H stop | 2010-05-01 | 2010-05-01 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 3.6767 | Highland 1 | Turbine faulted for over temperature in top control cabinet. We went up tower and found that although the temperature settings had been adjusted correctly, the breaker for the cooler on the left side of the cabinet was never switched on. We switched on the breaker and reset the alarm. The turbine was then placed back online. | KRAYN-WKO-NDX-20100501 | 1
KRAYN-WKO-NDX-20100502-01 | IBS Interbus stop | 2010-05-02 | 2010-05-02 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 2.7861 | Highland 1 | Turbine faulted for Interbus failure, we went to the turbine and cleaned the slip ring assembly inside the hub. After cleaning, the fault cleared and the turbine was placed back online. | KRAYN-WKO-NDX-20100502 | 1
KRAYN-WKO-NDX-20100503-01 | Maintenance | 2010-05-03 | 2010-05-03 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 59 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0356 | 7,2,1 | 8.3333 | Highland 1 | 9731.28 OP HRS | KRAYN-WKO-NDX-20100503 | 1
KRAYN-WKO-NDX-20100504-01 | Maintenance | 2010-05-04 | 2010-05-04 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 57 | Planned |  |  | 10.8833 | Highland 1 | 9586.59 OP hrs | KRAYN-WKO-NDX-20100504 | 1
KRAYN-WKO-NDX-20100505-01 | Maintenance | 2010-05-05 | 2010-05-05 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 33 | Planned |  |  | 9.2667 | Highland 1 | 8301.24 Op hrs | KRAYN-WKO-NDX-20100505 | 1
KRAYN-WKO-NDX-20100505-02 | Manual Stop | 2010-05-05 | 2010-05-05 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 4.15 | Forced |  |  | 4.15 | Highland 1 | Working with LM to repair blade spinner rings completed turbine 5 and it remained down while Dan and Bj finished there work. | KRAYN-WKO-NDX-20100505 | 1
KRAYN-WKO-NDX-20100505-03 | Manual Stop | 2010-05-05 | 2010-05-05 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 20 | Planned |  |  | 9.3833 | Highland 1 | Type 3 Maint. Generator Alighnment and hub torques. Operation Hours: 8992.21Still have to go back for the generator alighnment due to the high winds. | KRAYN-WKO-NDX-20100505 | 1
KRAYN-WKO-NDX-20100505-04 | Manual Stop | 2010-05-05 | 2010-05-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 2.9333 | Forced |  |  | 2.9333 | Highland 1 | Working with LM to repair blade spinner rings completed turbine 6 and put it back online. | KRAYN-WKO-NDX-20100505 | 1
KRAYN-WKO-NDX-20100506-01 | Maintenance | 2010-05-06 | 2010-05-06 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 28.8333 | Planned |  |  | 7.3 | Highland 1 | 10104.05 Op hrs | KRAYN-WKO-NDX-20100506 | 1
KRAYN-WKO-NDX-20100506-02 | Maintenance | 2010-05-06 | 2010-05-06 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 28.8333 | Planned |  |  | 7.3 | Highland 1 | 10104.05 Op hrs | KRAYN-WKO-NDX-20100506 | 1
KRAYN-WKO-NDX-20100506-03 | Manual stop | 2010-05-06 | 2010-05-06 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 24.75 | Planned |  |  | 8.3333 | Highland 1 | 10336.13 Operation Hours The technicians performed type 3 maintenance which includes hytorque of the tower and nacelle, generator slipring cleaning and grease of the turbine and oilfilter change outs. | KRAYN-WKO-NDX-20100506 | 1
KRAYN-WKO-NDX-20100506-04 | Manual Stop | 2010-05-06 | 2010-05-06 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 5.0833 | Forced |  |  | 5.0833 | Highland 1 | Working with LM repairing spinner rings went to turbine 4 which needed 2 rings repaired also I had to add oil to the hydraulic station. | KRAYN-WKO-NDX-20100506 | 1
KRAYN-WKO-NDX-20100507-01 | Maintenance | 2010-05-07 | 2010-05-07 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 23.25 | Planned |  |  | 7.9 | Highland 1 | 10120.75 Op hrs | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100507-02 | Manual Stop | 2010-05-07 | 2010-05-07 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 2.0167 | Highland 1 | The Nordex technicians performed the generator alighnment portion of the type three maintenance. Operatio Hours: 9633.33 | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100507-03 | Manual Stop | 2010-05-07 | 2010-05-07 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 3.9667 | Highland 1 | Performed the generator alignment and the speed sensor portion of the type 3 maintenance. | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100507-04 | Manual Stop | 2010-05-07 | 2010-05-07 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.8 | Forced |  |  | 3.8 | Highland 1 | Working with LM to repair blade spinner rings completed turbine 7 and put it back online. | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100507-05 | Manual Stop | 2010-05-07 | 2010-05-07 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3.1833 | Forced |  |  | 3.1833 | Highland 1 | Working with LM to repair blade spinner rings completed turbine 8 and put it back online. | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100507-06 | Pitch Batt Contactor Error | 2010-05-07 | 2010-05-07 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 9.5 | Forced |  |  | 25.2864 | Highland 1 | Production HRS 8235.43h. Investigate and troubleshoot Turbine for FE1173. On initial entrance to the Hub discover broken bolt from Blade 3. Damages include: Pitch gear piping bent, several grease bottle broken off, dents on all 3 pitch boxes and cosmetic damage to hub paint. Clean and repair pitch slipring as part of the preventative measure for IBS faults USDK 248.1 {28-2243-0526}. | KRAYN-WKO-NDX-20100507 | 1
KRAYN-WKO-NDX-20100509-01 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.86111 | Forced |  |  | 0.46528 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-02 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-03 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-04 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-05 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-06 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-07 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.63194 | Forced |  |  | 0.23611 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-08 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.86111 | Forced |  |  | 0.46528 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100509-09 | US-HIGHLAND_22WEA80830_PunchList Items | 2010-05-09 | 2010-05-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.86111 | Forced |  |  | 0.46528 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100509 | 1
KRAYN-WKO-NDX-20100510-01 | IBS interbus stop | 2010-05-10 | 2010-05-10 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 13 | Forced |  |  | 6.3881 | Highland 1 | Production HRS 9873.13h. Investigate and troubleshoot Turbine for FE700-IBS interbus stop. Clean and repair pitch slipring as part of the preventative measure for IBS faults USDK 248.1 R.2 {29-1463-0314}. Found 1 broken Grease bottle in the Hub. Place Turbine back in Operation. | KRAYN-WKO-NDX-20100510 | 1
KRAYN-WKO-NDX-20100510-02 | Maintenance | 2010-05-10 | 2010-05-10 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 36 | Planned |  |  | 9.35 | Highland 1 | 10175.74 | KRAYN-WKO-NDX-20100510 | 1
KRAYN-WKO-NDX-20100510-03 | Manual Stop | 2010-05-10 | 2010-05-10 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 14 | Planned |  |  | 6.9167 | Highland 1 | Technicians performed the hub portion of the type 3 maints. Operation hours : 10396.42 | KRAYN-WKO-NDX-20100510 | 1
KRAYN-WKO-NDX-20100512-01 | US-HIGHLAND_05WEA80812_PunchList Items | 2010-05-12 | 2010-05-12 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 1.1382 | Forced |  |  | 0.66181 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100512 | 1
KRAYN-WKO-NDX-20100512-02 | US-HIGHLAND_05WEA80812_PunchList Items | 2010-05-12 | 2010-05-12 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 1.1382 | Forced |  |  | 0.66181 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100512 | 1
KRAYN-WKO-NDX-20100512-03 | US-HIGHLAND_05WEA80812_PunchList Items | 2010-05-12 | 2010-05-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.1382 | Forced |  |  | 0.66181 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100512 | 1
KRAYN-WKO-NDX-20100512-04 | US-HIGHLAND_05WEA80812_PunchList Items | 2010-05-12 | 2010-05-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.1382 | Forced |  |  | 0.66181 | Highland 1 | Bacement bolts/cleaning | KRAYN-WKO-NDX-20100512 | 1
KRAYN-WKO-NDX-20100513-01 | Manual Stop | 2010-05-13 | 2010-05-13 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 14.5 | Planned |  |  | 6.9981 | Highland 1 | Type 3 Maintenance. OP HRS = 10460.53 | KRAYN-WKO-NDX-20100513 | 1
KRAYN-WKO-NDX-20100513-02 | Manual Stop | 2010-05-13 | 2010-05-13 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 14.5 | Planned |  |  | 6.9981 | Highland 1 | Type 3 Maintenance. OP HRS = 10460.53 | KRAYN-WKO-NDX-20100513 | 1
KRAYN-WKO-NDX-20100514-01 | Manual Stop | 2010-05-14 | 2010-05-14 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.31667 | Highland 1 | Removed ice detection unit as to customers request. 10029.24 Op hrs | KRAYN-WKO-NDX-20100514 | 1
KRAYN-WKO-NDX-20100514-02 | Manual Stop | 2010-05-14 | 2010-05-14 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 5.3333 | Forced | KRAYN-NDX-PRT-0325 | 1 | 1.7258 | Highland 1 | operating hours 8755.20…..Replaced Oil filter for gearbox offline filter Per AWP. Filter was showing %75 percent cloged on NCII. | KRAYN-WKO-NDX-20100514 | 1
KRAYN-WKO-NDX-20100514-03 | LV Insulat Monitor 660v stop | 2010-05-14 | 2010-05-14 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 11.7333 | Highland 1 | The wind turbine is currently having a 660VAC insulation fault Due to the MET tower being wired into the turbine transformer. Directed by Everpower to switch off the MET tower until further notice. There is no up tower time on this wind turbine. Operation hrs:7212.79 | KRAYN-WKO-NDX-20100514 | 1
KRAYN-WKO-NDX-20100514-04 | Gear oil filter warning | 2010-05-14 | 2010-05-14 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.65 | Highland 1 | Changed out gear oil filter. 9905 Op hrs | KRAYN-WKO-NDX-20100514 | 1
KRAYN-WKO-NDX-20100514-05 | Manual Stop | 2010-05-14 | 2010-05-14 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.16667 | Highland 1 | Operation hrs: 9674.66 The turbine has FM 168 gearbox filter 75% clogged alarm. The Nordex service technicians changed the filter and reset the alarm. The technicians had to restart the wind turbine due to lightning on the park will return when clear. The Nordex service team returned to the turbine to perform the filter change out. up tower time:1 hr | KRAYN-WKO-NDX-20100514 | 1
KRAYN-WKO-NDX-20100516-01 | US-HIGHLAND_02WEA80809_PunchList Items | 2010-05-16 | 2010-05-16 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.65972 | Forced |  |  | 0.44444 | Highland 1 | Punchlist Items | KRAYN-WKO-NDX-20100516 | 1
KRAYN-WKO-NDX-20100516-02 | LV Grid error 660v alarm | 2010-05-16 | 2010-05-17 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 28.75 | Forced | KRAYN-NDX-PRT-0090,KRAYN-NDX-PRT-0043 | 10,5 | 71.4333 | Highland 1 | Turbine went down on Friday due to grid error. Went to turbine to reset safety chain and reset turine. When we got there found we tried to reset it found more problems.Did some troule shooting couldn’t find whats wrong turine sat down.This crew on the service report came in monday did some more trouble shooting. Found ten suppresor diodes bad along with a fuse on the control board. | KRAYN-WKO-NDX-20100516 | 1
KRAYN-WKO-NDX-20100518-01 | Manual Stop | 2010-05-18 | 2010-05-18 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 14 | Planned |  |  | 5.6628 | Highland 1 | Operation Hours 10050.84hrs brought supplies up tower and cleaned part of bottom of nacell cleaned walls in nacelle and cleaned grease traps 2 Renew technicians High torqued the outside base of tower 1st dec 2nd deck,3rd deck,yaw deck. 5.25 hours climb for Uty and Mark | KRAYN-WKO-NDX-20100518 | 1
KRAYN-WKO-NDX-20100518-02 | Manual Stop | 2010-05-18 | 2010-05-18 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 27.5 | Planned | KRAYN-NDX-PRT-0062 | 8 | 6.9364 | Highland 1 | Matt Mayer and George Quaha Hytorqed the foundation from 8:30-10:30. Mark, UT and John Performed maintenance in the bottom of the tower and then went to tower 1. Dan, Sean and Aj performed Maintenance 3 in the Nacelle and Hub. John returned to help in the Hub for 2 hours in the afternoon, and then went back to WT1. Production Hours 10346 | KRAYN-WKO-NDX-20100518 | 1
KRAYN-WKO-NDX-20100519-01 | Manual Stop | 2010-05-19 | 2010-05-19 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 6.25 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356 | 1,1 | 5.7131 | Highland 1 | Operating Hours 10068.66 hours. Worked with 2 Renew Technicans. Filled main bairing auto greeser and generator kluberpex auto greeser fillled. Changed off line and online filters, Hightorque'd Hub 10% per service Manual. | KRAYN-WKO-NDX-20100519 | 1
KRAYN-WKO-NDX-20100519-02 | Manual Stop | 2010-05-19 | 2010-05-19 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 22.5 | Planned |  |  | 7.2614 | Highland 1 | Performed a type 3 maintenance, no materials were used. 10363 hours | KRAYN-WKO-NDX-20100519 | 1
KRAYN-WKO-NDX-20100519-03 | Manual Stop | 2010-05-19 | 2010-05-19 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 2.6167 | Highland 1 | Nordex Technicians stopped the wind turbine to perform the generator portion of type three maint.. Operation hours: 10590.96 | KRAYN-WKO-NDX-20100519 | 1
KRAYN-WKO-NDX-20100519-04 | Yaw hydraulic brake not open | 2010-05-19 | 2010-05-19 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 20.25 | Forced | KRAYN-NDX-PRT-0702 | 1 | 6.6128 | Highland 1 | The turbine had FM420 disabled allowing it to run without high risk. We took apart the hydraulic system and readjusted throttle valve 710. It had the adjustment screw turned all the way out preventing enough hydraulic fluid to flow freely through it, it needs to be adjusted all the way in. We then installed the hydraulic station retrofit kit, renabled the fault, ran through some testing with the yaw converter, and placed the turbine back online. | KRAYN-WKO-NDX-20100519 | 1
KRAYN-WKO-NDX-20100520-01 | Manual Stop | 2010-05-20 | 2010-05-20 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 16 | Planned |  |  | 8.2278 | Highland 1 | Operating hours 10086 Hours Torqued nacelle bolts per manual and marked bolts, cleaned bottom of nacelle, filled gear oil, changed nacelle window window above access hatch. | KRAYN-WKO-NDX-20100520 | 1
KRAYN-WKO-NDX-20100520-02 | Manual Stop | 2010-05-20 | 2010-05-20 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0702 | 1 | 5.9833 | Highland 1 | Nordex technicians stopped wind turbine to instal the hydr. Retro.. Operation Hrs: 10612.35 Up tower time:4.5 hrs | KRAYN-WKO-NDX-20100520 | 1
KRAYN-WKO-NDX-20100520-03 | manual stop | 2010-05-20 | 2010-05-20 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0634 | 1 | 0.67333 | Highland 1 | Went to turbine 9 to change HUR. Checked box should be services. Production hours 8000 | KRAYN-WKO-NDX-20100520 | 1
KRAYN-WKO-NDX-20100520-04 | manual stop | 2010-05-20 | 2010-05-20 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0634 | 1 | 0.67333 | Highland 1 | Went to turbine 9 to change HUR. Checked box should be services. Production hours 8000 | KRAYN-WKO-NDX-20100520 | 1
KRAYN-WKO-NDX-20100520-05 | manual stop | 2010-05-20 | 2010-05-20 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 10.5 | Forced | KRAYN-NDX-PRT-0634 | 1 | 4.1 | Highland 1 | Went to turbine 7 to perform SEG Maintenance. Also replaced HUR board. Checked box should be "Scheduled Maintenance" Production hours 8642 | KRAYN-WKO-NDX-20100520 | 1
KRAYN-WKO-NDX-20100528-01 | Manual Stop | 2010-05-28 | 2010-05-28 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0105 | 1 | 1.5108 | Highland 1 | Completed the ALU RetroFit In Accordinance with Nordex Instruction. Hours 10270 | KRAYN-WKO-NDX-20100528 | 1
KRAYN-WKO-NDX-20100528-02 | Manual Stop | 2010-05-28 | 2010-05-28 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 1.5108 | Highland 1 | Drip pan retrofit, Completed By Dan Ihle per Nordex Maintenance Instruction. No SAP for Drip Pan. Hours 10270 | KRAYN-WKO-NDX-20100528 | 1
KRAYN-WKO-NDX-20100528-03 | Manual Stop | 2010-05-28 | 2010-05-28 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.5108 | Highland 1 | Hydraulic RetroFit was Performed on the WTG Per Nordex Instruction. Hours 10270 | KRAYN-WKO-NDX-20100528 | 1
KRAYN-WKO-NDX-20100528-04 | Manual Stop | 2010-05-28 | 2010-05-28 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 15 | Forced |  |  | 1.5108 | Highland 1 | Also George Quaha and Matt Mayer from Renew were at the tower from 8am to 10 am. Today we worked on the typeIII Maintenance In Accordinance With Nordex Instruction. Hours 10270 | KRAYN-WKO-NDX-20100528 | 1
KRAYN-WKO-NDX-20100528-05 | Manual Stop | 2010-05-28 | 2010-05-28 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 30 | Forced | KRAYN-NDX-PRT-0702,KRAYN-NDX-PRT-0105 | 1,1 | 1.5108 | Highland 1 | Also George Quaha and Matt Mayer from Renew were at the tower from 8am to 10 am. We performed a hydraulic retrofit, the drip pan retrofit, and the ALU relay retrofit. Hours 10270. Hydraulic retro SR # is 600013493. We do not have SR numbers for the other two retros yet. | KRAYN-WKO-NDX-20100528 | 1
KRAYN-WKO-NDX-20100601-01 | Manual Stop | 2010-06-01 | 2010-06-01 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 25 | Planned |  |  | 7.04 | Highland 1 | We went up with Matt Mayer to finish the Maintenance 3 Matt worked from 8am to 5 Pm on this turbine. We performed function tests , painted and cleaned. Production hours 10353 | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-02 | Type 3 Maint. | 2010-06-01 | 2010-06-01 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 18.4 | Planned |  |  | 8.1833 | Highland 1 | Type 3 Maintenance. OP HRS = 9180.32 (Task performed in tower today was torquing) | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-03 | Type 3 Maint. | 2010-06-01 | 2010-06-01 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 18.4 | Planned |  |  | 8.1833 | Highland 1 | Type 3 Maintenance. OP HRS = 9180.32 (Task performed in tower today was torquing) | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-04 | Yaw motor break not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0106 | 3 | 19.8667 | Highland 1 | Nordex Technicians performed the ALU Retpro in the top box. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-05 | yaw motor break not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 19.8667 | Highland 1 | Nordex Technicians performed drip-pan retro. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-06 | Yaw Motor Brk not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 14 | Planned | KRAYN-NDX-PRT-0480,KRAYN-NDX-PRT-0486 | 1,5 | 19.8667 | Highland 1 | Nordex Technicians went to the down turbine to troubleshot the FM 414 fault. They found that 2 of the 3 fuses of 120 F1 were blown. Due to no support down tower the technicians had to go to the shop to get new fuses. The techs replaced the fuses and they blew again due to the cab cooler leaked water on the yaw convertor which was replaced on Friday the week prior. Replaced the yaw convertor and fuses again and performed the Drip pan retro. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-07 | Yaw Motor Brk not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 14 | Planned | KRAYN-NDX-PRT-0480,KRAYN-NDX-PRT-0486 | 1,5 | 19.8667 | Highland 1 | Nordex Technicians went to the down turbine to troubleshot the FM 414 fault. They found that 2 of the 3 fuses of 120 F1 were blown. Due to no support down tower the technicians had to go to the shop to get new fuses. The techs replaced the fuses and they blew again due to the cab cooler leaked water on the yaw convertor which was replaced on Friday the week prior. Replaced the yaw convertor and fuses again and performed the Drip pan retro. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-08 | Yaw Motor Brk not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 14 | Planned | KRAYN-NDX-PRT-0480,KRAYN-NDX-PRT-0486 | 1,5 | 19.8667 | Highland 1 | Nordex Technicians went to the down turbine to troubleshot the FM 414 fault. They found that 2 of the 3 fuses of 120 F1 were blown. Due to no support down tower the technicians had to go to the shop to get new fuses. The techs replaced the fuses and they blew again due to the cab cooler leaked water on the yaw convertor which was replaced on Friday the week prior. Replaced the yaw convertor and fuses again and performed the Drip pan retro. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100601-09 | Yaw Motor Brk not open | 2010-06-01 | 2010-06-01 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 14 | Planned | KRAYN-NDX-PRT-0480,KRAYN-NDX-PRT-0486 | 1,5 | 19.8667 | Highland 1 | Nordex Technicians went to the down turbine to troubleshot the FM 414 fault. They found that 2 of the 3 fuses of 120 F1 were blown. Due to no support down tower the technicians had to go to the shop to get new fuses. The techs replaced the fuses and they blew again due to the cab cooler leaked water on the yaw convertor which was replaced on Friday the week prior. Replaced the yaw convertor and fuses again and performed the Drip pan retro. Operation hrs: 8960.48 Uptower time:9.5 hrs | KRAYN-WKO-NDX-20100601 | 1
KRAYN-WKO-NDX-20100602-01 | Type 3 Maint. | 2010-06-02 | 2010-06-02 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 36 | Planned |  |  | 10.5167 | Highland 1 | Type 3 Maintenance. OP HRS = 9196.08 | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-02 | Type 3 Maint. | 2010-06-02 | 2010-06-02 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 36 | Planned |  |  | 10.5167 | Highland 1 | Type 3 Maintenance. OP HRS = 9196.08 | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-03 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 3 | Planned | KRAYN-NDX-PRT-0106 | 1 | 8.5617 | Highland 1 | Performed The ALU retrofit as per Retrofit instruction K0805_016317_EN | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-04 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.5617 | Highland 1 | Performed the Drip pan retrofit | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-05 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 2 | Planned | KRAYN-NDX-PRT-0702 | 1 | 8.5617 | Highland 1 | Performed the Hydraulic Kit retrofit as per instruction K0809_012912_EN | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-06 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 32 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0277,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964 | ,,,, | 8.5617 | Highland 1 | We went up with Matt Mayer to finish the Maintenance 3 Matt worked from 8am to 7:00 Pm on this turbine. Production hours 8949 | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-07 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned | KRAYN-NDX-PRT-0106 | 1 | 8.7333 | Highland 1 | The operation hrs: 7685.82 Uptower time is 8.5 hrs Nordex technicians performed the ALU Retro. | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-08 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.7333 | Highland 1 | The operation hrs: 7685.82 Uptower time is 8.5 hrs Nordex technicians performed the Drip-Pan retro | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-09 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 12 | Planned |  |  | 8.7333 | Highland 1 | Nordex Technicians stopped the windturbine to troubleshot the FM 1157 Pitchangle2 Diff. Acc. Red Act Fault. Adjusted all three blade cam switches and run tested the turbine. Found that the cam switches were way out of adjustment. The operation hrs: 7685.82 Uptower time is 8.5 hrs | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100602-10 | Manual Stop | 2010-06-02 | 2010-06-02 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned | KRAYN-NDX-PRT-0702 | 1 | 8.7333 | Highland 1 | The operation hrs: 7685.82 Uptower time is 8.5 hrs Nordex technicians performed the Hydr. Retro.. | KRAYN-WKO-NDX-20100602 | 1
KRAYN-WKO-NDX-20100603-01 | Type 3 Maint. | 2010-06-03 | 2010-06-03 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 35.25 | Planned |  |  | 10.35 | Highland 1 | Type 3 Maintenance. OP HRS = 9210.26(No parts used) | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-02 | Type 3 Maint. | 2010-06-03 | 2010-06-03 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 35.25 | Planned |  |  | 10.35 | Highland 1 | Type 3 Maintenance. OP HRS = 9210.26(No parts used) | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-03 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 30 | Planned | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0351 | 1,4 | 8.8667 | Highland 1 | We went up with Matt Mayer to finish the Maintenance 3 Matt worked from 8am to 6:00 Pm on this turbine. Production hours 8964 | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-04 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0558 | 2 | 4.65 | Highland 1 | The windturbine was still faulting on a FM 1157 Pitchangle 2 Diff Acc Red Act fault. The Nordex technicians went back up to troubleshot this problem and found that the cam switch was faulty so removed and replaced the cam switch. After adjusting the new cam switch found it was faulty also. The techs had to go to the shop to get a new cam switch and installed and adjucted accordingly. | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-05 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0558 | 2 | 4.65 | Highland 1 | The windturbine was still faulting on a FM 1157 Pitchangle 2 Diff Acc Red Act fault. The Nordex technicians went back up to troubleshot this problem and found that the cam switch was faulty so removed and replaced the cam switch. After adjusting the new cam switch found it was faulty also. The techs had to go to the shop to get a new cam switch and installed and adjucted accordingly. | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-06 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0105 | 3 | 3.8833 | Highland 1 | The operating hours are:8854.53 and the uptower time :4hrs.. The Nordex technicians performed the ALU retro.. | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-07 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 3.8833 | Highland 1 | The operating hours are:8854.53 and the uptower time :4hrs.. The Nordex technicians performed the Drip-pan retro.. | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100603-08 | Manual Stop | 2010-06-03 | 2010-06-03 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.8833 | Highland 1 | The Nordex technicians performed a hydraulic retro because the turbine was faulting for a FM 420 and changed the throttle valve but the valve which was given was used and still was inop.. So the techs had to leave the fault disabled. The operating hours are:8854.53 and the uptower time :4hrs.. | KRAYN-WKO-NDX-20100603 | 1
KRAYN-WKO-NDX-20100604-01 | Type 3 Maint. | 2010-06-04 | 2010-06-04 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 28.2 | Planned |  |  | 8.1333 | Highland 1 | Type 3 Maintenance. OP HRS = 9223.81(No parts used) | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-02 | Type 3 Maint. | 2010-06-04 | 2010-06-04 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 28.2 | Planned |  |  | 8.1333 | Highland 1 | Type 3 Maintenance. OP HRS = 9223.81(No parts used) | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-03 | Manual Stop | 2010-06-04 | 2010-06-04 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 8.2994 | Highland 1 | We went up with Matt Meyer to finish hytorc and hydraulic station for Maintenance 3. Production hours 8979 | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-04 | Manual Stop | 2010-06-04 | 2010-06-04 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 20 | Planned | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 8.2994 | Highland 1 | We went up with John to perform the yaw motor retrofit. Production hours 8979 | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-05 | Manual Stop | 2010-06-04 | 2010-06-04 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 13.6667 | Forced |  |  | 6.8333 | Highland 1 | Nordex technicians stopped the turbine to troubleshoot the FM 1157 fault further. Previously the techs. Changed the pitch cam swithch and adjusted all three blades and the turbine was still faulting on blade 2. The next step was to change the pitch convertor and to change the firmware. The Nordex techs. then manualy ran the turbine to monitor the pitch values and seen there was problems with blade 2. Swapped the cables in the pitch box number one and pitch box number 2 to see if the problem would follow. The values did stabalized after the swapp, the Nordex techs will still continue to watch the turbine. The Pitch convertor was not defective serial number of the one in the turbine 090250206. | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-06 | Manual Stop | 2010-06-04 | 2010-06-04 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 13.6667 | Forced |  |  | 6.8333 | Highland 1 | Nordex technicians stopped the turbine to troubleshoot the FM 1157 fault further. Previously the techs. Changed the pitch cam swithch and adjusted all three blades and the turbine was still faulting on blade 2. The next step was to change the pitch convertor and to change the firmware. The Nordex techs. then manualy ran the turbine to monitor the pitch values and seen there was problems with blade 2. Swapped the cables in the pitch box number one and pitch box number 2 to see if the problem would follow. The values did stabalized after the swapp, the Nordex techs will still continue to watch the turbine. The Pitch convertor was not defective serial number of the one in the turbine 090250206. | KRAYN-WKO-NDX-20100604 | 1
KRAYN-WKO-NDX-20100604-07 | Manual Stop | 2010-06-04 | 2010-06-04 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 13.6667 | Forced | KRAYN-NDX-PRT-0480 | 1 | 6.8333 | Highland 1 | Nordex technicians stopped the turbine to troubleshoot the FM 1157 fault further. Previously the techs. Changed the pitch cam swithch and adjusted all three blades and the turbine was still faulting on blade 2. The next step was to change the pitch convertor and to change the firmware. The Nordex techs. then manualy ran the turbine to monitor the pitch values and seen there was problems with blade 2. Swapped the cables in the pitch box number one and pitch box number 2 to see if the problem would follow. The values did stabalized after the swapp, the Nordex techs will still continue to watch the turbine. The Pitch convertor was not defective serial number of the one in the turbine 090250206. |  | 1
KRAYN-WKO-NDX-20100605-01 | Yaw motor brake not closed | 2010-06-05 | 2010-06-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 6 | Forced |  |  | 1.7697 | Highland 1 | The turbine had recently had new Ramme yaw motors installed. The microswitch on the first yaw motor had been adjusted incorrectly. We readjusted it and placed the turbine back online. |  | 1
KRAYN-WKO-NDX-20100605-02 | Yaw motor brake not closed | 2010-06-05 | 2010-06-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 6 | Forced |  |  | 1.7697 | Highland 1 | The turbine had recently had new Ramme yaw motors installed. The microswitch on the first yaw motor had been adjusted incorrectly. We readjusted it and placed the turbine back online. |  | 1
KRAYN-WKO-NDX-20100607-01 | US-HIGHLAND_06WEA80813_PunchList Items | 2010-06-07 | 2010-06-07 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.44444 | Forced | KRAYN-NDX-PRT-0009 | 1 | 0.22222 | Highland 1 | Punchlist Items |  | 1
KRAYN-WKO-NDX-20100607-02 | ALU retrofit | 2010-06-07 | 2010-06-07 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 1.25 | Forced | KRAYN-NDX-PRT-0105 | 3 | 2.5567 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100607-03 | Hydraulic Orifice | 2010-06-07 | 2010-06-07 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0702 | 1 | 2.5567 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100607-04 | ALU retrofit | 2010-06-07 | 2010-06-07 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0105 | 3 | 2.0083 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100607-05 | Hydraulic Orifice | 2010-06-07 | 2010-06-07 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced | KRAYN-NDX-PRT-0702 | 1 | 2.0417 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100607-06 | ALU retrofit | 2010-06-07 | 2010-06-07 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0105 | 3 | 3.4161 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100607-07 | Hyrdraulic Orifice | 2010-06-07 | 2010-06-07 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.4161 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100607-08 | Manual Stop | 2010-06-07 | 2010-06-07 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 26 | Planned | KRAYN-NDX-PRT-0038 | 2 | 9.95 | Highland 1 | The Nordex technicians performed type 3 maint. Which includes: change of the V-ring seal of the main bearing, cleaning of the nacelle, yaw deck, lower decks and painting of the nacelle parts, top cabinet function test and the hydraulic station tests.Operation hrs:9274.51 |  | 1
KRAYN-WKO-NDX-20100607-09 | Manual stop | 2010-06-07 | 2010-06-07 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 13.5 | Planned |  |  | 4.4667 | Highland 1 | Type 3 maintenance and replace canopy cover plexi glass. |  | 1
KRAYN-WKO-NDX-20100607-10 | Manual Stop | 2010-06-07 | 2010-06-07 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 1.1667 | Highland 1 | Start Type 3 Maintenance |  | 1
KRAYN-WKO-NDX-20100608-01 | US-HIGHLAND_06WEA80813_PunchList Items | 2010-06-08 | 2010-06-08 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.034722 | Forced |  |  | 0.017361 | Highland 1 | Punchlist Items |  | 1
KRAYN-WKO-NDX-20100608-02 | US-HIGHLAND_07WEA80814_PunchList Items | 2010-06-08 | 2010-06-08 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.65972 | Forced |  |  | 0.34028 | Highland 1 | Punchlist Items |  | 1
KRAYN-WKO-NDX-20100608-03 | ALU Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 2.1833 | Planned | KRAYN-NDX-PRT-0106 | 3 | 9.1667 | Highland 1 | Operation hs:7785.19 Nordex Technicians performed ALU retro with Renew guys. 8.750 hrs up turbine |  | 1
KRAYN-WKO-NDX-20100608-04 | Drip Pan Retro | 2010-06-08 | 2010-06-08 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 9.1667 | Highland 1 | Operation hs:7785.19 Nordex Technicians performed Drip-Pan retro 8.750 hrs up turbine |  | 1
KRAYN-WKO-NDX-20100608-05 | Hydraulic Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 4.3667 | Planned | KRAYN-NDX-PRT-0702 | 1 | 9.1667 | Highland 1 | Operation hs:7785.19 Nordex Technicians performed Hydraulic Retro retro 8.750 hrs up turbine |  | 1
KRAYN-WKO-NDX-20100608-06 | Maint 3 | 2010-06-08 | 2010-06-08 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 17 | Planned |  |  | 9.1667 | Highland 1 | Operation hs:7785.19 Nordex Technicians performed type 3 maintenance which includes nacelle and yaw drive torques and Function tests. The gearbox and hydraulic portion of the maintenance portion was also performed. Also the technicians performed the yaw portion of type three maint which includes cleaning of the yaw break disc, Checking the pad thickness. The rotor brake portion was also performed. 8.750 hrs up turbine |  | 1
KRAYN-WKO-NDX-20100608-07 | ALU Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0105 | 3 | 9.6333 | Highland 1 | did they ALU retro on wind turbine 9 |  | 1
KRAYN-WKO-NDX-20100608-08 | Hydraulic Retro | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0702 | 1 | 9.6333 | Highland 1 | did the hydraulic retro on wind turbine 9 George Quaha worked along with AJ on this Retro with the same time. |  | 1
KRAYN-WKO-NDX-20100608-09 | Manual Stop | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 30 | Planned |  |  | 9.6333 | Highland 1 | Op-hrs 8455.60 Type 3 maintenance. |  | 1
KRAYN-WKO-NDX-20100608-10 | ALU Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0105 | 3 | 9.6333 | Highland 1 | did they ALU retro on wind turbine 9 |  | 1
KRAYN-WKO-NDX-20100608-11 | Hydraulic Retro | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0702 | 1 | 9.6333 | Highland 1 | did the hydraulic retro on wind turbine 9 George Quaha worked along with AJ on this Retro with the same time. |  | 1
KRAYN-WKO-NDX-20100608-12 | Manual Stop | 2010-06-08 | 2010-06-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 30 | Planned |  |  | 9.6333 | Highland 1 | Op-hrs 8455.60 Type 3 maintenance. |  | 1
KRAYN-WKO-NDX-20100608-13 | ALU retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0105 | 3 | 2.1894 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100608-14 | Hydraulic Orifice | 2010-06-08 | 2010-06-08 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0702 | 1 | 2.1894 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100608-15 | ALU retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0105 | 3 | 1.9425 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100608-16 | Hydraulic Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.83333 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.9425 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100608-17 | ALU retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0105 | 3 | 2.435 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the auotmatic lubrication unit retrofit by replacing 3 relays and moving them to another location in the top box. |  | 1
KRAYN-WKO-NDX-20100608-18 | Hydraulic Retrofit | 2010-06-08 | 2010-06-08 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced | KRAYN-NDX-PRT-0702 | 1 | 2.435 | Highland 1 | Marty Kleinsasser and Reuben Waldner from Renew were working with me. Together we performed the hydraulic station retrofit. |  | 1
KRAYN-WKO-NDX-20100609-01 | Type 3 Maint. | 2010-06-09 | 2010-06-09 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 1.3603 | Highland 1 | Went to refill empty accumulator with George Quaha . During Maintenance 3 the accumulator charging kit broke while being used. Dustan had it fixed so we went up to refill the accumulator. However, the new piece did not fit properly and we were still unable to use it. We will have to go up again as soon as we get it working. Operating hours 9313. |  | 1
KRAYN-WKO-NDX-20100609-02 | Type 3 Maint. | 2010-06-09 | 2010-06-09 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 25.5 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0327,KRAYN-NDX-PRT-0964 | 1,4,1,4,1,1 | 8.1333 | Highland 1 | Operation hrs:7800.02 Nordex technicians performed type 3 maintenance which includes tower torques, yaw brake torques, function tests, yaw motor brake checks,yaw disc cleaning, nacelle cleaning. Uptower time 7.5 hrs |  | 1
KRAYN-WKO-NDX-20100609-03 | Type 3 Maint. | 2010-06-09 | 2010-06-09 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 24 | Planned |  |  | 5.2575 | Highland 1 | Went to perform Maintenance 3 work with George Quaha. George had same hours as Aaron Edelson on this tower. Operating Hours 8470 |  | 1
KRAYN-WKO-NDX-20100609-04 | Type 3 Maint. | 2010-06-09 | 2010-06-09 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 24 | Planned |  |  | 5.2575 | Highland 1 | Went to perform Maintenance 3 work with George Quaha. George had same hours as Aaron Edelson on this tower. Operating Hours 8470 |  | 1
KRAYN-WKO-NDX-20100609-05 | No work order description provided by contractor | 2010-06-09 | 2010-06-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 3.2114 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100609-06 | No work order description provided by contractor | 2010-06-09 | 2010-06-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.2114 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100609-07 | Drip Pan Retro | 2010-06-09 | 2010-06-09 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 1.0603 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100609-08 | Hydraulic Retrofit | 2010-06-09 | 2010-06-09 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.0603 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100609-09 | Drip Pan Retro | 2010-06-09 | 2010-06-09 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 1.1444 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100609-10 | Hydraulic Orifice | 2010-06-09 | 2010-06-09 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 2.25 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.1444 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online remotely by Dustan Thill. |  | 1
KRAYN-WKO-NDX-20100610-01 | Manual Stop | 2010-06-10 | 2010-06-10 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 34 | Planned | KRAYN-NDX-PRT-0558 | 1 | 10.8167 | Highland 1 | Operation hrs:7816.25 Nordex technicians performed type 3 maintenance which includes Hub tasks, function tests, generator slipring cleaning. While doing the blade alignment the blades pitched back to 90 degrees and broke the cam switch. Nordex technicians removed the inoperational cam switch and replaced and adjusted the blades. |  | 1
KRAYN-WKO-NDX-20100610-02 | No work order description provided by contractor | 2010-06-10 | 2010-06-10 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.43944 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-03 | Drip Pan Retro | 2010-06-10 | 2010-06-10 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 1.3936 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retro. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-04 | Hydraulic Orifice | 2010-06-10 | 2010-06-10 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.3936 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-05 | Drip Pan Retro | 2010-06-10 | 2010-06-10 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.29583 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-06 | Drip Pan Retro | 2010-06-10 | 2010-06-10 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 2.3939 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retro fit. The turbine was put back online by Dan Ihle. |  | 1
KRAYN-WKO-NDX-20100610-07 | Hydraulic Orifice | 2010-06-10 | 2010-06-10 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced | KRAYN-NDX-PRT-0702 | 1 | 2.3939 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online by Dan Ihle. |  | 1
KRAYN-WKO-NDX-20100610-08 | Hydraulic Orifice | 2010-06-10 | 2010-06-10 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.1664 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-09 | Drip Pan Retro | 2010-06-10 | 2010-06-10 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 1.7003 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online remotely by Dan Ihle. |  | 1
KRAYN-WKO-NDX-20100610-10 | Hydraulic Orifice | 2010-06-10 | 2010-06-10 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.7003 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online remotely by Dan Ihle. |  | 1
KRAYN-WKO-NDX-20100610-11 | Drip Pan Retro | 2010-06-10 | 2010-06-10 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 1.9561 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the drip pan retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100610-12 | No work order description provided by contractor | 2010-06-10 | 2010-06-10 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 1.9561 | Highland 1 | Marty Kleinsasser and Reuben Waldner installed the hydraulic station retrofit. The turbine was put back online. |  | 1
KRAYN-WKO-NDX-20100611-01 | Manual stop | 2010-06-11 | 2010-06-11 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 17 | Planned |  |  | 8.7714 | Highland 1 | Went to finish Maintenance 3 with Matt Meyer and George Quaha. George and Matt have the same hours as John. Aj came after leaving WT 9 and did the gen alignment and then helped finish the maintenance. Operating hours |  | 1
KRAYN-WKO-NDX-20100611-02 | Manual stop | 2010-06-11 | 2010-06-11 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 3.5297 | Highland 1 | Went to perform generator alignment for maintenance. Brought up Bradley from Rothrock subcontractor to show around. At 10:30 everpower came uptower to inspect. Operating Hours 8504 |  | 1
KRAYN-WKO-NDX-20100611-03 | Manual stop | 2010-06-11 | 2010-06-11 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 17 | Planned |  |  | 8.7714 | Highland 1 | Went to finish Maintenance 3 with Matt Meyer and George Quaha. George and Matt have the same hours as John. Aj came after leaving WT 9 and did the gen alignment and then helped finish the maintenance. Operating hours |  | 1
KRAYN-WKO-NDX-20100611-04 | Manual stop | 2010-06-11 | 2010-06-11 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 3.5297 | Highland 1 | Went to perform generator alignment for maintenance. Brought up Bradley from Rothrock subcontractor to show around. At 10:30 everpower came uptower to inspect. Operating Hours 8504 |  | 1
KRAYN-WKO-NDX-20100613-01 | Manual Stop | 2010-06-13 | 2010-06-13 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 14 | Planned |  |  | 3.0417 | Highland 1 | Went to Turbine 23 to perform SEG maintenance. Operation hours 9091. |  | 1
KRAYN-WKO-NDX-20100614-01 | Manual stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 7.1167 | Highland 1 | Replace yaw motors back to the original Leroy type. Worked with Marty and Ruben from Renew. |  | 1
KRAYN-WKO-NDX-20100614-02 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364 | 1,1,1,1 | 8.5333 | Highland 1 | Type 3 Maintenance (Grease,Filters,Torque, Cleaning) |  | 1
KRAYN-WKO-NDX-20100614-03 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 6.1667 | Forced |  |  | 8.5333 | Highland 1 | Geore Quaha and I changed the lift cable in the turbine he had the same amount of hours to this service order. |  | 1
KRAYN-WKO-NDX-20100614-04 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 11 | Planned |  |  | 8.5333 | Highland 1 | Type 3 Maintenance (Torque, Cleaning) |  | 1
KRAYN-WKO-NDX-20100614-05 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 6.1667 | Forced |  |  | 8.5333 | Highland 1 | George Quaha and I changed the lift cable in the turbine he had the same amount of hours to this service order. |  | 1
KRAYN-WKO-NDX-20100614-06 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned | KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,1,4 | 7.75 | Highland 1 | Operation hrs:9322.38 Nordex Service Technicians performed type 3 maint. Which includes nacelle torques, yaw drive torques, filling auto lubrication of yaw, generator and main bearing, check of the rotor brake, hydraulic filter change out, gearbox filters changed out and some nacelle cleaning. |  | 1
KRAYN-WKO-NDX-20100614-07 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,1,1,4 | 7.75 | Highland 1 | Operation hrs:9322.38 Nordex Service Technicians performed type 3 maint. Which includes nacelle torques, yaw drive torques, filling auto lubrication of yaw, generator and main bearing, check of the rotor brake, hydraulic filter change out, gearbox filters changed out and some nacelle cleaning. |  | 1
KRAYN-WKO-NDX-20100614-08 | Manual Stop | 2010-06-14 | 2010-06-14 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,1,1,4 | 7.75 | Highland 1 | Operation hrs:9322.38 Nordex Service Technicians performed type 3 maint. Which includes nacelle torques, yaw drive torques, filling auto lubrication of yaw, generator and main bearing, check of the rotor brake, hydraulic filter change out, gearbox filters changed out and some nacelle cleaning. |  | 1
KRAYN-WKO-NDX-20100615-01 | accumulator pressure | 2010-06-15 |  | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 0 | Forced |  |  | 9.95 | Highland 1 | we went up tower to fill accumulators wit nitrogen as we previously did not have the tool to do so correctly. |  | 1
KRAYN-WKO-NDX-20100615-02 | Manual Stop | 2010-06-15 | 2010-06-15 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 22 | Planned | 0,0,0,0 | , , , | 10.25 | Highland 1 | Type 3 Maintenance (Hub,Tourquing, Cleaning).No Parts Used. |  | 1
KRAYN-WKO-NDX-20100615-03 | Manual Stop | 2010-06-15 | 2010-06-03 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.8833 | Highland 1 | The Nordex technicians performed a hydraulic retro.Operation hrs:9338.62 |  | 1
KRAYN-WKO-NDX-20100615-04 | Manual Stop | 2010-06-15 | 2010-06-03 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.8833 | Highland 1 | The Nordex technicians performed a hydraulic retro.Operation hrs:9338.62 |  | 1
KRAYN-WKO-NDX-20100615-05 | Manual Stop | 2010-06-15 | 2010-06-03 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0702 | 1 | 3.8833 | Highland 1 | The Nordex technicians performed a hydraulic retro.Operation hrs:9338.62 |  | 1
KRAYN-WKO-NDX-20100615-06 | Manual Stop | 2010-06-15 | 2010-06-15 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 13.25 | Planned |  |  | 9.5 | Highland 1 | Operation hrs:9338.62 Nordex Service Technicians performed type 3 maint. Which includes slipring cleaning, some nacelle cleaning, yaw motor brk checks, yaw brk disc cleaning, hydraulic checks, some function tests, torq of the centa coupling, top box checks |  | 1
KRAYN-WKO-NDX-20100615-07 | Manual Stop | 2010-06-15 | 2010-06-15 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 13.25 | Planned |  |  | 9.5 | Highland 1 | Operation hrs:9338.62 Nordex Service Technicians performed type 3 maint. Which includes slipring cleaning, some nacelle cleaning, yaw motor brk checks, yaw brk disc cleaning, hydraulic checks, some function tests, torq of the centa coupling, top box checks |  | 1
KRAYN-WKO-NDX-20100615-08 | Manual Stop | 2010-06-15 | 2010-06-15 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 13.25 | Planned |  |  | 9.5 | Highland 1 | Operation hrs:9338.62 Nordex Service Technicians performed type 3 maint. Which includes slipring cleaning, some nacelle cleaning, yaw motor brk checks, yaw brk disc cleaning, hydraulic checks, some function tests, torq of the centa coupling, top box checks |  | 1
KRAYN-WKO-NDX-20100616-01 | Manual stop | 2010-06-16 | 2010-06-15 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 6.75 | Forced |  |  | 5.7333 | Highland 1 | Clean and buff slew ring to prevent any noise. Re adjust yaw brake pressure from 22 bar to 14 bar. Worked with Marty and Ruben from Renew. |  | 1
KRAYN-WKO-NDX-20100616-02 | Manual stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 3.1 | Highland 1 | Clean and buff slew ring to prevent any noise. Re adjust yaw brake pressure from 22 bar to 14 bar. Worked with Marty and Ruben from Renew. |  | 1
KRAYN-WKO-NDX-20100616-03 | Manual stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 3.1 | Highland 1 | Clean and buff slew ring to prevent any noise. Re adjust yaw brake pressure from 22 bar to 14 bar. Worked with Marty and Ruben from Renew. |  | 1
KRAYN-WKO-NDX-20100616-04 | Manual stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 4.2667 | Highland 1 | Clean and buff slew ring to prevent any noise. Re adjust yaw brake pressure from 22 bar to 14 bar. Worked with Marty and Ruben from Renew. |  | 1
KRAYN-WKO-NDX-20100616-05 | Manual Stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 27 | Planned |  |  | 8.8667 | Highland 1 | Operation hrs:9353.25 Nordex Service Technicians performed type 3 maint. Which includes tower torques, function tests, nacelle cleaning, slip ring in hub cleaning, yaw torqs, yaw drive torqs up tower time:9 hrs |  | 1
KRAYN-WKO-NDX-20100616-06 | Manual Stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 27 | Planned |  |  | 8.8667 | Highland 1 | Operation hrs:9353.25 Nordex Service Technicians performed type 3 maint. Which includes tower torques, function tests, nacelle cleaning, slip ring in hub cleaning, yaw torqs, yaw drive torqs up tower time:9 hrs |  | 1
KRAYN-WKO-NDX-20100616-07 | Manual Stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 27 | Planned |  |  | 8.8667 | Highland 1 | Operation hrs:9353.25 Nordex Service Technicians performed type 3 maint. Which includes tower torques, function tests, nacelle cleaning, slip ring in hub cleaning, yaw torqs, yaw drive torqs up tower time:9 hrs |  | 1
KRAYN-WKO-NDX-20100616-08 | Manual Stop | 2010-06-16 | 2010-06-16 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 20 | Planned | 0,0,0,0 | , , , | 9.0833 | Highland 1 | Type 3 Maintenance (Tourquing, Cleaning). |  | 1
KRAYN-WKO-NDX-20100617-01 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.35 | Highland 1 | had to get the serial numbers from the newly installed yaw motors |  | 1
KRAYN-WKO-NDX-20100617-02 | Manual stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 2.1333 | Highland 1 | Remove ice sensor and recharge all accumulators. I had Marty and Ruben from Renew with me. |  | 1
KRAYN-WKO-NDX-20100617-03 | Manual stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.1333 | Highland 1 | Remove ice sensors |  | 1
KRAYN-WKO-NDX-20100617-04 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 2.0833 | Highland 1 | removed ice sensor assembly for turbine 24. Matt and Ruben from Renew were with me. |  | 1
KRAYN-WKO-NDX-20100617-05 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 2.0833 | Highland 1 | removed ice sensor assembly for turbine 24. Matt and Ruben from Renew were with me. |  | 1
KRAYN-WKO-NDX-20100617-06 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 3.3333 | Highland 1 | Operation hrs:9368.86 Nordex Service Technicians performed tried to install the ice sensor but the cables were to short. |  | 1
KRAYN-WKO-NDX-20100617-07 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 3.3333 | Highland 1 | Operation hrs:9368.86 Nordex Service Technicians performed tried to install the ice sensor but the cables were to short. |  | 1
KRAYN-WKO-NDX-20100617-08 | Manual Stop | 2010-06-17 | 2010-06-17 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 3.3333 | Highland 1 | Operation hrs:9368.86 Nordex Service Technicians performed tried to install the ice sensor but the cables were to short. |  | 1
KRAYN-WKO-NDX-20100618-01 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 1.7667 | Forced |  |  | 1.7667 | Highland 1 | Ruben Waldner and I worked the same hours we worked on pulling the old cables out of turbine 8 for the ice sensors and took pictures of how they were wired. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-02 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 7.7167 | Highland 1 | Generator alignmentn performed with renew. Adjusted ladder and put a new washer on the Zarges lift to prevent it from hitting the first flange. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-03 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 7.7167 | Highland 1 | Generator alignment performed with renew. Adjusted ladder and put a new washer on the Zarges lift to prevent it from hitting the first flange. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-04 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 5.75 | Highland 1 | Ruben Waldner and I worked the same hours we worked on pulling the new cables for the ice sensor and replaced the ice sensor and the ice sensor box. Inverted the ice sensor and had to go back out and manual reset the ice sensor | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-05 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 7.5 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians installed Ice sensor from wtg 8.. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-06 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 7.5 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians installed Ice sensor from wtg 8.. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-07 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 7.5 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians installed Ice sensor from wtg 8.. | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-08 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians performed type 3 maint. Which includes hub and rotor . | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-09 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians performed type 3 maint. Which includes hub and rotor . | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100618-10 | Manual Stop | 2010-06-18 | 2010-06-18 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 6.9167 | Highland 1 | Operation hrs:9389.52 Nordex Service Technicians performed type 3 maint. Which includes hub and rotor . | KRAYN-WKO-NDX-20100618 | 1
KRAYN-WKO-NDX-20100621-01 | Manual Stop | 2010-06-21 | 2010-06-21 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 4.25 | Forced |  |  | 3.6667 | Highland 1 | Cleaned yaw ring to prevent futher noise and adjusted yaw brake pressure from 22 bar to 14 bar. I had 2 Renew techs with me. | KRAYN-WKO-NDX-20100621 | 1
KRAYN-WKO-NDX-20100621-02 | Manual Stop | 2010-06-21 | 2010-06-21 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 2.35 | Highland 1 | Cleaned yaw ring to prevent futher noise and adjusted yaw brake pressure from 22 bar to 14 bar. I had 2 Renew techs with me. | KRAYN-WKO-NDX-20100621 | 1
KRAYN-WKO-NDX-20100621-03 | Manual Stop | 2010-06-21 | 2010-06-21 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 15 | Planned | KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,1,4 | 7.5833 | Highland 1 | Operation hrs:9279.07 Nordex technicians performed type 3 maint. Which includes tower, blade, yaw, rotor torqs, generator checks, gearbox checks, filled all auto lubers, cleaned all drip pans. | KRAYN-WKO-NDX-20100621 | 1
KRAYN-WKO-NDX-20100621-04 | Manual stop | 2010-06-21 | 2010-06-21 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 20 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0587 | 1,4,4 | 8.2833 | Highland 1 | Went to Turbine 25 with George Quaha to perform Maintenance 3. Operating hours 9048. | KRAYN-WKO-NDX-20100621 | 1
KRAYN-WKO-NDX-20100622-01 | manual stop | 2010-06-22 | 2010-06-22 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 1.3333 | Forced | KRAYN-NDX-PRT-0418 | 1 | 0.66667 | Highland 1 | top box a/c on right side appeared to drip water at some point, damaging phoenix contacct multi eather net port adapter. 8080.99 | KRAYN-WKO-NDX-20100622 | 1
KRAYN-WKO-NDX-20100622-02 | Manual Stop | 2010-06-22 | 2010-06-22 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 17.5 | Planned |  |  | 0.5 | Highland 1 | Operation hrs:9295.48 Nordex technicians shut the turbine down to perform type 3 maint. But there was lightning on the park started wind turbine back up and waited for clearence to go ahead with maintenance. Nordex technicians performed type three maint. which includes nacelle torqs, yaw drive torqs. , generator torqs, function tests. while performing the function tests the turbine was faulting for rotor brake errors actuated the pressure switch a couple times to free up and the brake began to operate correctly. the test port on the rotor brake is leaking we have none on stock they are on order. | KRAYN-WKO-NDX-20100622 | 1
KRAYN-WKO-NDX-20100623-01 | Manual Stop | 2010-06-23 | 2010-06-23 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 2.9833 | Highland 1 | Went up turbine and cleaned out hydraulic valve 225 and found solonoid valve 210 loose, removed both and cleaned and reinstalled. Re adjusted pressure. Marty from Renew was up tower with me. | KRAYN-WKO-NDX-20100623 | 1
KRAYN-WKO-NDX-20100623-02 | Manual Stop | 2010-06-23 | 2010-06-23 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | 0,0,0,0 | , , , | 4.0333 | Highland 1 | Type 3 Maintenance ( Tourquing of Tower Section, Nacelle, Hub. Changed Filters and Lubes). Ophrs-10858.47 {07:00-08:00 Safety Meeting 08:00-09:00 rer and drive to site) | KRAYN-WKO-NDX-20100623 | 1
KRAYN-WKO-NDX-20100623-03 | Manual Stop | 2010-06-23 | 2010-06-23 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 16.5 | Planned |  |  | 8.95 | Highland 1 | Operation hrs:9312.24 Nordex technicians performed type 3 maintenance which includes nacelle cleaning , hub cleaning , tower cleaning , hub checks, generator torqs, generator coolant checks, yaw disc checks. | KRAYN-WKO-NDX-20100623 | 1
KRAYN-WKO-NDX-20100623-04 | Manual Stop | 2010-06-23 | 2010-06-23 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 11 | Planned |  |  | 3.5667 | Highland 1 | Type 3 Maintenance ( Cleaning).No Parts Used. Ophrs= 10858.47 | KRAYN-WKO-NDX-20100623 | 1
KRAYN-WKO-NDX-20100623-05 | Manual Stop | 2010-06-23 | 2010-06-23 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | 0,0,0,0 | , , , | 4.0333 | Highland 1 | Type 3 Maintenance ( Tourquing of Tower Section, Nacelle, Hub. Changed Filters and Lubes). Ophrs-10858.47 {07:00-08:00 Safety Meeting 08:00-09:00 rer and drive to site) | KRAYN-WKO-NDX-20100623 | 1
KRAYN-WKO-NDX-20100624-01 | No Fault | 2010-06-24 | 2010-06-24 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 11.5 | Forced | KRAYN-NDX-PRT-0335 | 28 | 9.0167 | Highland 1 | Cleaned out the yaw calipers and replaced yaw brake pads as per work instruction K0801_011371_EN Revision 02. Cleaned yaw deck and affected areas. Took pictures of the pads and sent them to Dustan. | KRAYN-WKO-NDX-20100624 | 1
KRAYN-WKO-NDX-20100624-02 | Gear OilPress GearInlt L Stop | 2010-06-24 | 2010-06-24 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 24.5 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0617,KRAYN-NDX-PRT-0290,KRAYN-NDX-PRT-0325 | 1,1,80.2,1 | 21.4456 | Highland 1 | 6/23/10_ Went to troubleshoot the error. Found a broken "lovejoy" connection between the gear oil pump and the pump motor. Took the pump apart to bring down so we can find a replacement asap. Turbine is still down. Operation hours 10413. Manuel Montalvo was with Aj Edelson for the same hours. Marty Kleinsasser had the same hours as John Huff. 6/24/10_Went back up Turbine this morning to put on new "Lovejoy". Pump still did not function properly so we then replaced the oil pump as well. Pump is not functioning properly but oil is not spraying into the gearbox as it should. Someone from Rexroth should be called to inspect the lines in the gearbox. Operation hours 10413. Manuel Montalvo was with Aj Edelson for the same hours. We had a service order meeting at the sop from 7-8, packed and drove to the turbine from 8-9:30, worked up tower from 9:30-4:30, drove back to the shop from 4:30-5:30, and did paperwork/discussed the problem from 5:30-6:30. | KRAYN-WKO-NDX-20100624 | 1
KRAYN-WKO-NDX-20100624-03 | Manual Stop | 2010-06-24 | 2010-06-24 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0364 | 1 | 6.9 | Highland 1 | Type 3 Maintenance ( Tourquing of Tower Section, Nacelle, Hub. Changed Filters and Lubes). OPHRS= 7997.43 [07:00-07:30 paperwork 07:30-08:00 meeting 08:00-09:00 prep and drive to site.] | KRAYN-WKO-NDX-20100624 | 1
KRAYN-WKO-NDX-20100624-04 | Manual Stop | 2010-06-24 | 2010-06-24 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 19.5 | Planned | KRAYN-NDX-PRT-0290 | 5 gal. | 6.9667 | Highland 1 | Operation hrs: 9759.23 Nordex technicians performed type 3 maintenance which includes generator and nacelle torqs. , Function tests , tower cleaning. The up tower time is 7 hrs. | KRAYN-WKO-NDX-20100624 | 1
KRAYN-WKO-NDX-20100625-01 | None | 2010-06-25 | 2010-06-25 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 2 | Highland 1 | Went the Turbine 6 today to replace a bad Ballast on Deck 3. We were on Deck 3 for about 1.5 hours. Manuel Montalvo was with Aj Edelson for the same hours. We drove from 10-10:15, then from 10:15-12:30. There is no SAP Number for the Light bulbs or Ballast. Operating hours 9693 | KRAYN-WKO-NDX-20100625 | 1
KRAYN-WKO-NDX-20100625-02 | No Fault | 2010-06-25 | 2010-06-25 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0335 | 28 | 7.1 | Highland 1 | Cleaned out the yaw calipers and replaced yaw brake pads as per work instruction K0801_011371_EN Revision 02, and completed yaw Brake Noise report as per doc K0808_017150_EN Revision 00. Cleaned yaw deck and affected areas. Took pictures of the pads and sent them to Dustan. | KRAYN-WKO-NDX-20100625 | 1
KRAYN-WKO-NDX-20100625-03 | Manual Stop | 2010-06-25 | 2010-06-25 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 16.5 | Planned | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0351 | 1,4 | 7.15 | Highland 1 | Operation hrs: 9776.60 Nordex technicians performed type 3 maintenance which includes Hub checks and generator slip ring cleaning and hydr. Checks and nacelle cleaning. Up tower time 7 hrs.. | KRAYN-WKO-NDX-20100625 | 1
KRAYN-WKO-NDX-20100625-04 | Manual Stop | 2010-06-25 | 2010-06-25 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 7.0833 | Planned | KRAYN-NDX-PRT-0364 | 1 | 7.6833 | Highland 1 | Type 3 Maintenance (Changed Filters, Torqued Tower Sections, Torqued Nacelle,Filled ALU's) Ophrs=9486.45 | KRAYN-WKO-NDX-20100625 | 1
KRAYN-WKO-NDX-20100628-01 | yaw hyd brakes not open | 2010-06-28 | 2010-06-28 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 9.0667 | Forced | KRAYN-NDX-PRT-0280 | 1 | 0.63333 | Highland 1 | opp hrs 10877.87 / we went up tower due to hydraulic yaw brakes not closed. The fault was intermittent and a valve was changed to see if this was the issue. The fault remained so we checked signals from the yaw convertor to see if proper functioin was occuring. the fault was intermitent and was still present so relay was replaced and the issue has not been back since. | KRAYN-WKO-NDX-20100628 | 1
KRAYN-WKO-NDX-20100628-02 | Manual Stop | 2010-06-28 | 2010-06-28 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 3.6 | Planned |  |  | 3.2667 | Highland 1 | Type 3 Maintenance (Finished Hub-Greasing, Torquing,Inspection) Ophrs=10969.36 | KRAYN-WKO-NDX-20100628 | 1
KRAYN-WKO-NDX-20100628-03 | Manual Stop | 2010-06-28 | 2010-06-28 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 3.6 | Planned |  |  | 3.2667 | Highland 1 | Type 3 Maintenance (Finished Hub-Greasing, Torquing,Inspection) Ophrs=10969.36 | KRAYN-WKO-NDX-20100628 | 1
KRAYN-WKO-NDX-20100628-04 | Manual Stop | 2010-06-28 | 2010-06-28 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 4.65 | Planned | KRAYN-NDX-PRT-0364 | 1 | 4.3667 | Highland 1 | Type 3 Maintenance (Torqued tower sections, Torqued Nacelle, Changed Filters,Filled ALU's, Cleaned) | KRAYN-WKO-NDX-20100628 | 1
KRAYN-WKO-NDX-20100628-05 | No Fault | 2010-06-28 | 2010-06-28 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0335 | 28 | 7.2 | Highland 1 | Cleaned out the yaw calipers and replaced yaw brake pads as per work instruction K0801_011371_EN Revision 02, and completed yaw Brake Noise report as per doc K0808_017150_EN Revision 00. Cleaned yaw deck and affected areas. Took pictures of the pads and sent them to Dustan. I had 2 Renew techs up tower with me for the same amount of time. | KRAYN-WKO-NDX-20100628 | 1
KRAYN-WKO-NDX-20100629-01 | Manual Stop | 2010-06-29 | 2010-06-29 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 10.5 | Forced | KRAYN-NDX-PRT-0335 | 28 | 7.3667 | Highland 1 | Cleaned out the yaw calipers and replaced yaw brake pads as per work instruction K0801_011371_EN Revision 02, and completed yaw Brake Noise report as per doc K0808_017150_EN Revision 00. Cleaned yaw deck and affected areas. Took pictures of the pads and sent them to Dustan. I had 2 Renew techs up tower with me for the same amount of time. | KRAYN-WKO-NDX-20100629 | 1
KRAYN-WKO-NDX-20100629-02 | Manual Stop | 2010-06-29 | 2010-06-29 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 7.1 | Planned | 0,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364 | ,1,1 | 7.05 | Highland 1 | Type 3 Maintenance (Torqued tower sections, Torqued Nacelle, Changed Filters,Filled ALU's, Cleaned) ophrs=8278.48 | KRAYN-WKO-NDX-20100629 | 1
KRAYN-WKO-NDX-20100630-01 | Manual Stop | 2010-06-30 | 2010-06-30 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 4.4 | Planned | 0,KRAYN-NDX-PRT-0291,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0277,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0356 | ,2,1,1,1,4,1,4,1,4,1 | 4.4 | Highland 1 | Type 3 Maintenance (Torqued Tower Sections, Torqued Nacelle, Filled ALU's Cleaned) ophrs=10537.50 Had a couple of Renew guys working with me. | KRAYN-WKO-NDX-20100630 | 1
KRAYN-WKO-NDX-20100630-02 | Manual Stop | 2010-06-30 | 2010-06-30 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 4.4 | Planned | 0,KRAYN-NDX-PRT-0291,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0277,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0356 | ,2,1,1,1,4,1,4,1,4,1 | 4.4 | Highland 1 | Type 3 Maintenance (Torqued Tower Sections, Torqued Nacelle, Filled ALU's Cleaned) ophrs=10537.50 Had a couple of Renew guys working with me. | KRAYN-WKO-NDX-20100630 | 1
KRAYN-WKO-NDX-20100630-03 | Manual Stop | 2010-06-30 | 2010-06-30 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 3.2 | Planned | 0,0,0,0 | , , , | 7.05 | Highland 1 | Type 3 Maintenance (Torqued Hub, Greased Hub) ophrs=8295.23 | KRAYN-WKO-NDX-20100630 | 1
KRAYN-WKO-NDX-20100630-04 | Manual Stop | 2010-06-30 | 2010-06-30 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 23 | Planned | KRAYN-NDX-PRT-0351 | 4 | 8.7333 | Highland 1 | Operation hrs:9981.71 Nordex Technicians performed type three maintenance which includes Hub and generator checks and rotor brake checks and nacelle cleaning. Up tower time 8.5 | KRAYN-WKO-NDX-20100630 | 1
KRAYN-WKO-NDX-20100701-01 | Manual Stop | 2010-07-01 | 2010-07-01 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 4 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0350 | 1,1,1,3,1 | 5.05 | Highland 1 | Type 3 Maintenance (Torqued Tower Sections, Torqued Nacelle, Filled ALU's Cleaned) ophrs=10691.39 | KRAYN-WKO-NDX-20100701 | 1
KRAYN-WKO-NDX-20100701-02 | FM6 manual stop | 2010-07-01 | 2010-07-01 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 20 | Planned |  |  | 7.7333 | Highland 1 | op hrs. 7900.05 Performed a type 3 maint. | KRAYN-WKO-NDX-20100701 | 1
KRAYN-WKO-NDX-20100702-01 | Type 3 Maint. | 2010-07-02 | 2010-07-02 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2.9 | Forced | KRAYN-NDX-PRT-0682 | 1 | 1.2167 | Highland 1 | Changed Out Gen Grounding Brushes, Prepared tower for type 3 maintenance Ophrs= 11070.42 | KRAYN-WKO-NDX-20100702 | 1
KRAYN-WKO-NDX-20100702-02 | Type 3 Maint. | 2010-07-02 | 2010-07-02 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2.9 | Forced | KRAYN-NDX-PRT-0682 | 1 | 1.2167 | Highland 1 | Changed Out Gen Grounding Brushes, Prepared tower for type 3 maintenance Ophrs= 11070.42 | KRAYN-WKO-NDX-20100702 | 1
KRAYN-WKO-NDX-20100702-03 | Manual Stop | 2010-07-02 | 2010-07-02 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 3.5667 | Planned | KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0291 | 1,1,4,6,2 | 3.1333 | Highland 1 | Type 3 Maintenance (Torqued Hub,Greased Hub,Torqued Gen Feet) ophrs=10711.35 | KRAYN-WKO-NDX-20100702 | 1
KRAYN-WKO-NDX-20100702-04 | Manual Stop | 2010-07-02 | 2010-07-02 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 7.5 | Planned | KRAYN-NDX-PRT-0351 | 4 | 4.4833 | Highland 1 | Nordex technicians performed type 3 maintenance which includes generator slipring cleaning and torqs, high speed coupling torqs, rotor brake checks, top box checks. Turbine operation hrs are 8339.98 , Turbine up tower time 4.5 | KRAYN-WKO-NDX-20100702 | 1
KRAYN-WKO-NDX-20100702-05 | Manual Stop | 2010-07-02 | 2010-07-02 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 25.5 | Forced |  |  | 2.2 | Highland 1 | Align anemometer, clean nacelle and all decks. I had 1 Renew tech (Marty Kleinsasser) worked the same time as us. | KRAYN-WKO-NDX-20100702 | 1
KRAYN-WKO-NDX-20100706-01 | Manual Stop | 2010-07-06 | 2010-07-06 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 5.5 | Highland 1 | operation hrs: 8431.50 Nordex technicians performed type 3 maintenance which includes hub checks , top box checks , speed monitor function tests , yaw motor brake checks. Up tower time is 6 hrs. Derrick Perry and Luke Lewis assisted with maintenance | KRAYN-WKO-NDX-20100706 | 1
KRAYN-WKO-NDX-20100707-01 | Type 3 Maint. | 2010-07-07 | 2010-07-07 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 31.5 | Planned | KRAYN-NDX-PRT-0290 | 5 gals | 7.7833 | Highland 1 | operation hrs: 8431.50 Nordex technicians performed type 3 maintenance which includes yaw cam switch function tests, hydraulic tests, generator cooler needed some coolant and the gearbox needed oil, nacelle and tower cleaning. Up tower time is hrs. Derrick Perry and Luke Lewis assisted with maintenance | KRAYN-WKO-NDX-20100707 | 1
KRAYN-WKO-NDX-20100708-01 | Manual Stop | 2010-07-08 | 2010-07-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 9.5 | Forced | KRAYN-NDX-PRT-0292 | .5 liter | 6.9333 | Highland 1 | Nordex technicians performed type 3 maintenance which includes hydraulic checks, yaw system checks, function tests: emergency stops, vibration sensors, cam switch checks , rotor brake checks, nacelle and tower cleaning. William Anderson and Luke Lewis assisted with the maintenance and the operation hrs are 10852.22 Up tower time 5.5 | KRAYN-WKO-NDX-20100708 | 1
KRAYN-WKO-NDX-20100709-01 | Manual Stop | 2010-07-09 | 2010-07-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 8.5 | Forced | KRAYN-NDX-PRT-0290,KRAYN-NDX-PRT-0351 | 5 gallons,4 | 5.9833 | Highland 1 | Nordex technicians performed type 3 maintenance which includes hub checks, generator slipring cleaning , high speed coupling torqs. William Anderson assisted with the maintenance and the operation hrs are 10869.28 Up tower time 6hrs | KRAYN-WKO-NDX-20100709 | 1
KRAYN-WKO-NDX-20100712-01 | FM6 manual stop | 2010-07-12 | 2010-07-12 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 34 | Planned |  |  | 4.4667 | Highland 1 | 11277.41 op hrs.Perfromed type 3 maint. In hub. Everyone on this report was up tower for 4.5 hrs | KRAYN-WKO-NDX-20100712 | 1
KRAYN-WKO-NDX-20100712-02 | Manual stop | 2010-07-12 | 2010-07-12 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 3.3042 | Highland 1 | Went to WT 13 to finish the Maintenance 3. Dillan and William from Nordex and Tim and Adam from renew all had the same hours as me. Operating hours 10935 | KRAYN-WKO-NDX-20100712 | 1
KRAYN-WKO-NDX-20100713-01 | Manual stop | 2010-07-13 | 2010-07-13 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 8.5 | Planned | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0350 | 1,4 | 4.5667 | Highland 1 | Went to WT 11 to perform the Maintenance 3. Dillan and William from Nordex and Tim and Adam from renew all had the same hours as me. Operating hours 10753 | KRAYN-WKO-NDX-20100713 | 1
KRAYN-WKO-NDX-20100713-02 | FM6 manual stop | 2010-07-13 | 2010-07-13 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 38 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0291,KRAYN-NDX-PRT-0277,KRAYN-NDX-PRT-0046 | 4,1,4,2,8 L,1,4 | 6.8167 | Highland 1 | 11296.44 op hrs.Perfromed type 3 maint.in naccelle. Everyone on this report was up tower for 6.5 hrs | KRAYN-WKO-NDX-20100713 | 1
KRAYN-WKO-NDX-20100714-01 | Manual stop | 2010-07-14 | 2010-07-14 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 10.5 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0290 | 4,10 | 5.6667 | Highland 1 | Went to WT 11 to perform the Maintenance 3. Dillan and William from Nordex and Tim and Adam from renew all had the same hours as me. Operating hours 10772 | KRAYN-WKO-NDX-20100714 | 1
KRAYN-WKO-NDX-20100714-02 | Manual stop | 2010-07-14 | 2010-07-15 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 6 | Planned | KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0291,KRAYN-NDX-PRT-0277,KRAYN-NDX-PRT-0046 | 2,5 L,4,4 | 2.2833 | Highland 1 | Went to WT 11 to perform the Maintenance 3. Dillan and William from Nordex and Tim and Adam from renew all had the same hours as me. Operating hours 10790 | KRAYN-WKO-NDX-20100714 | 1
KRAYN-WKO-NDX-20100714-03 | FM6 manual stop | 2010-07-14 | 2010-07-14 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 27 | Planned |  |  | 6.0333 | Highland 1 | 11313.53 op hrs.Perfromed type 3 maint. In hub. Everyone on this report was up tower for 6 hrs | KRAYN-WKO-NDX-20100714 | 1
KRAYN-WKO-NDX-20100715-01 | FM6 manual stop | 2010-07-15 | 2010-07-15 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 34 | Planned | KRAYN-NDX-PRT-0681 | 12 | 5.7833 | Highland 1 | 11003.18 op hrs.Perfromed type 3 maint. Everyone on this report was up tower for 5.5 hrs | KRAYN-WKO-NDX-20100715 | 1
KRAYN-WKO-NDX-20100716-01 | Manual Stop | 2010-07-16 | 2010-07-16 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 2.3667 | Highland 1 | Nordex technicians stopped the wind turbine because the wind turbine was faulting for FM 262 which is a rotor brake pressure hold fault. Checked all relays in this circuit which are operational. Could be a possible accumulator problem. Up tower time : 2 hrs , operation hrs:10378.54 | KRAYN-WKO-NDX-20100716 | 1
KRAYN-WKO-NDX-20100716-02 | WTG Manual Stop | 2010-07-16 | 2010-07-16 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0682,KRAYN-NDX-PRT-0681 | 2,11 | 1.4667 | Highland 1 | Went to change the carbon brushes that did not get changed during maintenance. Also investigated vibration picked up by the SKF monitor. Found lots of pitting and rough surfaces on the Generator Slip ring. Operating hours 10329. | KRAYN-WKO-NDX-20100716 | 1
KRAYN-WKO-NDX-20100717-01 | Manual Stop | 2010-07-17 | 2010-07-17 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0973,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0356 | 4,1,4,1 | 3.9017 | Highland 1 | Performed Type III maintenance. Change filter, clean tower. Total hrs. 11006.05 | KRAYN-WKO-NDX-20100717 | 1
KRAYN-WKO-NDX-20100717-02 | Manual Stop | 2010-07-17 | 2010-07-18 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 8 | Forced |  |  | 0.083333 | Highland 1 | The Nordex technitions went to turbine because EverPower was unable to see the turbine from scada. Reset the LPC and put the turbine back in service. | KRAYN-WKO-NDX-20100717 | 1
KRAYN-WKO-NDX-20100719-01 | WTG Manual Stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 29 | Planned | KRAYN-NDX-PRT-0558 | 1 | 6.1 | Highland 1 | Nordex Technicians stopped the wind turbine to perform type 3 maint. Which includes function tests of the emergency stops, yaw cam switch, vibration sensors, rotor brake checks. Operation hrs:11051.27 | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-02 | WTG Manual Stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 40 | Planned | KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0351 | 4,1,1,1,0.5,1,4 | 5.3167 | Highland 1 | Went to the turbine to perform maintenance 3. Operating hours 11244 | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-03 | WTG Manual Stop | 2010-07-19 | 2010-07-20 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 21.25 | Highland 1 | Went to Turbine with Wind Access, Jarter, and Jorge from blade company for blade inspections. Operation hours 1057.11. | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-04 | WTG Manual Stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 12 | Forced |  |  | 8.5667 | Highland 1 | Went to Turbine with Wind Access, Jarter, and Jorge from blade company for blade inspections. Operation hours 1057.11. | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-05 | Manual stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 0.83333 | Highland 1 | Mike Campagno and Donnie spent the same amount of time in the turbine. Replaced generator slipring brushes. | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-06 | Manual Stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 0.78333 | Highland 1 | Mike Campagno spent the same amount of time in the turbine. Replaced generator slipring brushes. | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100719-07 | Manual Stop | 2010-07-19 | 2010-07-19 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 5.5 | Forced | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 1.3667 | Highland 1 | Mike Campagno spent the same amount of time in the turbine. Replaced Generator slipring brushes. | KRAYN-WKO-NDX-20100719 | 1
KRAYN-WKO-NDX-20100721-01 | MI class B Fault | 2010-07-21 | 2010-07-22 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0632 | 1 | 1.25 | Highland 1 | the curcuit was shut down for substation maintenance upon re-energizing the circuit the sur controller failed the part was replaced and the turbine was put back online. (opp. Hrs 12087.27) | KRAYN-WKO-NDX-20100721 | 1
KRAYN-WKO-NDX-20100722-01 | Yaw SensTrack 2(0&deg | 2010-07-22 | 2010-07-22 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 8 | Forced |  |  | 3.3667 | Highland 1 | the turbine had faulted multiple times for sensor track defect we went up tower to investigate and found hydraulics not working properly fixed the issue and put the turbine back into operation. (opp. Hrs. 12087.27) | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-02 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 1.0039 | Highland 1 | Replaced generator slipring brushes on WTG: 14WEA80821. John Huff spent the same amount of time in the tower. | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-03 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 0.77722 | Highland 1 | Replaced generator slipring brushes on WTG: 15WEA80822. John Huff spent the same amount of time in the tower. | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-04 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 28.25 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 6.8667 | Highland 1 | Nordex technicians performed type 3 which includes tower torqs, yaw brake , yaw bearing torqs as well, hub function tests and changed slip ring brushes. Operation hrs : 11319.08 | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-05 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 0.72972 | Highland 1 | Replaced generator slipring brushes on WTG: 18WEA80825. John Huff spent the same amount of time in the tower. | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-06 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 1.2997 | Highland 1 | generator slipring brushes on WTG: 19WEA80826. John Huff spent the same amount of time in the tower. | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100722-07 | WTG Manual Stop | 2010-07-22 | 2010-07-22 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 30 | Planned |  |  | 4.9667 | Highland 1 | Went to Turbine 10 to start Maintenance 3. We performed all function tests and Started the Hub work. Operating hours 11043 | KRAYN-WKO-NDX-20100722 | 1
KRAYN-WKO-NDX-20100723-01 | WTG Manual Stop | 2010-07-23 | 2010-07-23 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 52.5 | Planned |  |  | 5.3875 | Highland 1 | Maintenance on WTG: 17WEA80824. John Huff and Sean Illig spent the same amount of time in the turbine. | KRAYN-WKO-NDX-20100723 | 1
KRAYN-WKO-NDX-20100723-02 | WTG Manual Stop | 2010-07-23 | 2010-07-23 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 6.6167 | Highland 1 | Went to Turbine with Jarter, and Jorge to preform blade inspections. Operation hours 10101.43. | KRAYN-WKO-NDX-20100723 | 1
KRAYN-WKO-NDX-20100724-01 | WTG Manual Stop | 2010-07-24 | 2010-07-24 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 42 | Planned |  |  | 4.95 | Highland 1 | Went to Turbine 10 to start Maintenance 3. Eric Haller also has the same hours as the rest of us but I could not fit him above. We hand torqued and Hytorced the Nacelle and Hub. Operating hours 11100 | KRAYN-WKO-NDX-20100724 | 1
KRAYN-WKO-NDX-20100724-02 | WTG Manual Stop | 2010-07-24 | 2010-07-24 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 43.5 | Planned |  |  | 5.7156 | Highland 1 | Maintenance on WTG: 17WEA80824. John Huff and Dustan Thill spent the same amount of time in the turbine. | KRAYN-WKO-NDX-20100724 | 1
KRAYN-WKO-NDX-20100724-03 | WTG Manual Stop | 2010-07-24 | 2010-07-24 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.5 | Highland 1 | Went to Turbine with Jarter, and Jorge to preform blade inspections. Operation hours 10115.43. | KRAYN-WKO-NDX-20100724 | 1
KRAYN-WKO-NDX-20100726-01 | WTG Manual Stop | 2010-07-26 | 2010-07-26 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 1.45 | Highland 1 | Nordex technicians stopped wind turbine to change generator brushes and install the drip pan on cooler. | KRAYN-WKO-NDX-20100726 | 1
KRAYN-WKO-NDX-20100726-02 | WTG Manual Stop | 2010-07-26 | 2010-07-26 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 1.1667 | Forced |  |  | 0.58333 | Highland 1 | Nordex Technicians stopped wind turbine to change generator slipring brushes and found they were already replaced. | KRAYN-WKO-NDX-20100726 | 1
KRAYN-WKO-NDX-20100726-03 | WTG Manual Stop | 2010-07-26 | 2010-07-26 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 4 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 1.5333 | Highland 1 | Nordex technicians stopped the windturbine to change generator slipring brushes. | KRAYN-WKO-NDX-20100726 | 1
KRAYN-WKO-NDX-20100727-01 | WTG Manual Stop | 2010-07-27 | 2010-07-27 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 4.6867 | Highland 1 | Perform Type III Maint. WTG: 10WEA80817. Torque tower sections and clean tower. John Huff, Luke Lewis, and Adam Heaverin were all up tower for the same times. Total hrs:11147 | KRAYN-WKO-NDX-20100727 | 1
KRAYN-WKO-NDX-20100727-02 | WTG Manual Stop | 2010-07-27 | 2010-07-27 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 12,2 | 4.3333 | Highland 1 | Nordex technicians stopped the wind turbine to change the generator brushes and generator alignment. While changing the generator slipring brushes found that the slipring races were never cleaned during maintenance , cleaned and replaced brushes. | KRAYN-WKO-NDX-20100727 | 1
KRAYN-WKO-NDX-20100727-03 | WTG Manual Stop | 2010-07-27 | 2010-07-27 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 9 | Forced |  |  | 5.3167 | Highland 1 | Went to Turbine with Jarter, and Jorge to preform blade inspections. Operation hours 9903.37. | KRAYN-WKO-NDX-20100727 | 1
KRAYN-WKO-NDX-20100728-01 | WTG Manual Stop | 2010-07-28 | 2010-07-28 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0335 | 24 | 8.7333 | Highland 1 | Replaced Svendborg yaw caliper brake pads as per instruction K0801_011371_EN_Rev1. And Cleaned affected areas. Mike Compagno, Luke Lewis and Adam Heaverin were up turbine at the same amount of time. | KRAYN-WKO-NDX-20100728 | 1
KRAYN-WKO-NDX-20100728-02 | WTG Customer Stop | 2010-07-28 | 2010-07-28 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.1667 | Highland 1 | Q/A service work in turbine with John Bennett from EverPower. OP HRS> 11302.84 | KRAYN-WKO-NDX-20100728 | 1
KRAYN-WKO-NDX-20100728-03 | WTG Manual Stop | 2010-07-28 | 2010-07-28 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 9.5 | Forced |  |  | 6.95 | Highland 1 | Went to Turbine with Jarter, and Jorge to preform blade inspections. Operation hours 10321.56. | KRAYN-WKO-NDX-20100728 | 1
KRAYN-WKO-NDX-20100729-01 | WTG Manual Stop | 2010-07-29 | 2010-07-29 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 10.5 | Planned | KRAYN-NDX-PRT-0959 | 2 | 3.9783 | Highland 1 | Installed yaw motor fan retro kit. John Huff, Casey Murphy, and Aaron Edelson were in the tower for the same amount of hrs. | KRAYN-WKO-NDX-20100729 | 1
KRAYN-WKO-NDX-20100729-02 | WTG Manual Stop | 2010-07-29 | 2010-07-29 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 3.4 | Forced |  |  | 3.4 | Highland 1 | Assisted AvanCos subcontractor technicians in operation of WTG during Blade Inspections | KRAYN-WKO-NDX-20100729 | 1
KRAYN-WKO-NDX-20100731-01 | WTG Manual Stop | 2010-07-31 | 2010-07-31 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 8.5 | Planned |  |  | 4.6206 | Highland 1 | Worked with blade inspection team. Adam Heaverin was up tower for the same amount of time. | KRAYN-WKO-NDX-20100731 | 1
KRAYN-WKO-NDX-20100801-01 | Pitchangle 2 Diff.Set-Act | 2010-08-01 | 2010-08-01 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0725 | 1 | 17.25 | Highland 1 | Troubleshoot turbine & Changed out slipring. Mike compagno was with me for the same amount of time. | KRAYN-WKO-NDX-20100801 | 1
KRAYN-WKO-NDX-20100804-01 | No work order description provided by contractor | 2010-08-04 |  | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 10 | Forced |  |  | 5.5736 | Highland 1 | Blade Inspections. | KRAYN-WKO-NDX-20100804 | 1
KRAYN-WKO-NDX-20100806-01 | Pitchangle 1 Diff.Set-Act | 2010-08-06 | 2010-08-07 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 21 | Forced | KRAYN-NDX-PRT-0725 | 1 | 14.0833 | Highland 1 | Went to WT 22 to troubleshoot Blade problem. Found broken bolt, which had broken the slip ring, light fixture, battery box vent, reset button, Auto-lube dispenser, and threw grease all over the hub. Had to come down and go back to shop to get replacement parts and supplies to fix it. Sean Illig and Aj edelson had the same hours as Aj Edelson above. Eric Haller went to the turbine with John Bennet for another reason, and began helping us with this service order at 2 PM. From 2 PM until 9 PM Eric Haller had the same hours as Aj and Sean. Dustan and Mike came at 5pm to bring more parts and stayed until 9 pm. I can not fit Sean and Eric hours in the above space. Operating hours were 10798. | KRAYN-WKO-NDX-20100806 | 1
KRAYN-WKO-NDX-20100807-01 | WTG Manual Stop | 2010-08-07 | 2010-08-07 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 8 | Forced |  |  | 5 | Highland 1 | Went to WT 15 with Avancos guys to perform Blade inspections. Jorge Metzler and Juan J. Meizoso had the same hours and Aj. Operating hours 9174. | KRAYN-WKO-NDX-20100807 | 1
KRAYN-WKO-NDX-20100811-01 | WTG Manual Stop | 2010-08-11 | 2010-08-11 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 21 | Forced |  |  | 5.0783 | Highland 1 | Worked with blade inspection team. | KRAYN-WKO-NDX-20100811 | 1
KRAYN-WKO-NDX-20100811-02 | Pitch1 PwrSupRed24VDC Fault | 2010-08-11 | 2010-08-11 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 15 | Forced | KRAYN-NDX-PRT-0475 | 1 | 16.5167 | Highland 1 | Nordex technicians went to faulted turbine to troubleshoot the pitch fault. Checked all cables and connections from 19F2 in pitch one to module 76A1 module and found that the turbine was also giving a pitch auto luber fault and while checking all connection the technicians found that light one on 76A1 was blinking.Checked cabling from the auto luber back to 76A1 and it appears to be ok, so the technicians removed and replaced 76A1. | KRAYN-WKO-NDX-20100811 | 1
KRAYN-WKO-NDX-20100812-01 | WTG Manual Stop | 2010-08-12 | 2010-08-12 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 18 | Forced |  |  | 6.7333 | Highland 1 | Went to Turbine 5 with Garnik Haghverdi from Siemens industry to check the slip ring problem. Operating hours 11281 | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100812-02 | WTG Manual Stop | 2010-08-12 | 2010-08-12 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 8.5 | Forced |  |  | 4.9375 | Highland 1 | Worked with blade inspection team WTG: 13WEA80820. | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100812-03 | WTG Manual Stop | 2010-08-12 | 2010-08-12 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 0.33333 | Highland 1 | Nordex technicians performed a zarges lift maintenance according to maintenance procedures. Operation hrs.:9103.92 | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100812-04 | No work order description provided by contractor | 2010-08-12 | 2010-08-12 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 0.43333 | Highland 1 | Performed a Zarges lift maint. 264258.29 OP hrs Both Nordex employee's went uptower for 26 mins | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100812-05 | No work order description provided by contractor | 2010-08-12 | 2010-08-12 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 0.46667 | Highland 1 | Performed a Zarges lift maint. 10460.73 OP hrs Both Nordex employee's went uptower for 28 mins | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100812-06 | WTG Manual Stop | 2010-08-12 | 2010-08-12 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 8.5 | Planned |  |  | 0.45 | Highland 1 | Nordex technicians performed Zarges maintenance according to maintenance procedures.Operation hrs.:10632.86 | KRAYN-WKO-NDX-20100812 | 1
KRAYN-WKO-NDX-20100813-01 | No work order description provided by contractor | 2010-08-13 | 2010-08-13 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 0.31667 | Highland 1 | Performed a Zarges lift maint. 9305.4 OP hrs Both Nordex employee's went uptower for 19 mins | KRAYN-WKO-NDX-20100813 | 1
KRAYN-WKO-NDX-20100813-02 | No work order description provided by contractor | 2010-08-13 | 2010-08-13 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 0.45 | Highland 1 | Performed a Zarges lift maint. 10936.6 OP hrs Both Nordex employee's went uptower for 27 mins | KRAYN-WKO-NDX-20100813 | 1
KRAYN-WKO-NDX-20100816-01 | WTG Manual Stop | 2010-08-16 | 2010-08-16 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 10 | Forced |  |  | 5.4253 | Highland 1 | Worked with blade inspection team. Charles Martin was up tower for the same amount of time. | KRAYN-WKO-NDX-20100816 | 1
KRAYN-WKO-NDX-20100816-02 | WTG Manual Stop | 2010-08-16 | 2010-08-16 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 15.5 | Forced | KRAYN-NDX-PRT-0344,KRAYN-NDX-PRT-0553 | 1,1 | 5.3667 | Highland 1 | Nordex technicians manualy stopped the wind turbine to trouble shoot the rotor brake hold pressure fault. They changed out valves 720 and 730 and on the electro valve had to reconnect the plug wires due to oil being on the plug also found some paint in the lines. The techs cleaned all lines dealing with the rotor brake and also the turbine had a FM 368 fault and the techs manualy ran turbine up and fast logged the RPM signals. The techs also seen there was a grid failure before the RPM fault and think thats why the alarm was present.Operation hrs:11020.43 The FM 262 fault is still present will contact master techs to see how we can resolve this problem. | KRAYN-WKO-NDX-20100816 | 1
KRAYN-WKO-NDX-20100817-01 | Yaw SensTrack 1(90&deg | 2010-08-17 |  | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 58 | Forced | KRAYN-NDX-PRT-0781,KRAYN-NDX-PRT-0781 | 1,1 | 6.1 | Highland 1 | .Nordex Technicians along with Dickinson crane company removed and replaced yaw gearbox drives which includes with the proper seating of the drives and bolt placement and backlashing of the pinion gears. | KRAYN-WKO-NDX-20100817 | 1
KRAYN-WKO-NDX-20100818-01 | Yaw SensTrack 1(90&deg | 2010-08-18 | 2010-08-18 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 50 | Forced |  |  | 195.7833 | Highland 1 | .Nordex Technicians went back to turbine to finish the yaw drive replacement which includes hytorqing the bolts to machine frame, reinstalling of the yaw motors, checking that the back lash is good, programming of the yaw convertor. Operation hrs:11564.64 | KRAYN-WKO-NDX-20100818 | 1
KRAYN-WKO-NDX-20100823-01 | WTG Manual Stop | 2010-08-23 | 2010-08-23 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 43 | Forced | KRAYN-NDX-PRT-0335,KRAYN-NDX-PRT-0029 | 28,1 gal | 9.3 | Highland 1 | Nordex technicians stopped the wind turbine to perform a yaw brake installation which includes removing all bolts and cleaning brake calipers and installing new brake pads and a total re-torq of all brake calipers and total cleaning of the turbine. | KRAYN-WKO-NDX-20100823 | 1
KRAYN-WKO-NDX-20100824-01 | WTG Manual Stop | 2010-08-24 | 2010-08-24 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 7 | Forced |  |  | 4.2833 | Highland 1 | Nordex tech along with Seimens tech Performed a generator alignment and generator slip ring inspection for warranty work. Operation hrs: 12306.00 | KRAYN-WKO-NDX-20100824 | 1
KRAYN-WKO-NDX-20100825-01 | No work order description provided by contractor | 2010-08-25 | 2010-08-25 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 6.75 | Forced |  |  | 6.4167 | Highland 1 | tower cleaning 12873.80 op hrs | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-02 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.58333 | Forced |  |  | 0.58333 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox. Operation hrs: 11764.78 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-03 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 2.1167 | Highland 1 | Went to Turbine 12 with Garnik Haghverdi from Siemens industry to perform tests on the gen slip ring. Operating hours 12284 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-04 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.58333 | Forced |  |  | 0.56667 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox. Operation hrs: 11835.13 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-05 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.41667 | Forced |  |  | 0.53333 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox. Operation hrs: 11835.13 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-06 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 0.58333 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox. Operation hrs: 11835.13 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-07 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 1.3333 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox and found that the turbine had a leaking yaw brake caliper. Operation hrs: 11835.13 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-08 | WTG System ok | 2010-08-25 | 2010-08-25 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 2.0167 | Forced |  |  | 1.8167 | Highland 1 | sanded yaw brake disc to reduce noise levels, also took oil samples from gearbox brad foy from everpower was with me | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-09 | WTG System ok | 2010-08-25 | 2010-08-25 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 2.5167 | Forced |  |  | 2.5167 | Highland 1 | sanded yaw brake disc to reduce noise levels, also took oil samples from gearbox brad foy from everpower was with me | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-10 | WTG System ok | 2010-08-25 | 2010-08-25 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 1.6167 | Forced |  |  | 1.6167 | Highland 1 | sanded yaw brake disc to reduce noise levels, also took oil samples from gearbox brad foy from everpower was with me | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100825-11 | WTG Manual Stop | 2010-08-25 | 2010-08-25 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.83333 | Highland 1 | Nordex technician along with Everpower rep. John Bennette pulled oil sample on gearbox. Operation hrs: 11835.13 | KRAYN-WKO-NDX-20100825 | 1
KRAYN-WKO-NDX-20100826-01 | No work order description provided by contractor | 2010-08-26 | 2010-08-26 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 7.75 | Forced |  |  | 103.2667 | Highland 1 | Avanco techs did blade inspections and cleaned parts of the tower. Nordex assisted and completed punch list items which include, 29) Dust cover on valves dry rotted. 33) Chipped paint on gearbox. 34) nacelle window cracked. 41,42,43 Bearbox oil filter housing leaking. 53) chipped paint in hub under pitch gear blade 1. 57) paint peeling under pitch gear on balde 1. 12685.28 op hrs | KRAYN-WKO-NDX-20100826 | 1
KRAYN-WKO-NDX-20100826-02 | WTG Manual Stop | 2010-08-26 | 2010-08-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 24 | Forced | KRAYN-NDX-PRT-0745,KRAYN-NDX-PRT-0335,KRAYN-NDX-PRT-0029 | 1,28,1.5 gal | 8 | Highland 1 | Nordex technicians found a leak on a caliper the day before so did a complete yaw brake pad change out and cleaned the existing calipers and nacelle. Operation hrs:11746.38 | KRAYN-WKO-NDX-20100826 | 1
KRAYN-WKO-NDX-20100826-03 | WTG Manual Stop | 2010-08-26 | 2010-08-26 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 2.7833 | Highland 1 | Went to Turbine 20 with Garnik Haghverdi from Siemens industry to perform tests on the gen slip ring. Operating hours 10848 | KRAYN-WKO-NDX-20100826 | 1
KRAYN-WKO-NDX-20100826-04 | WTG Manual Stop | 2010-08-26 | 2010-08-26 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.2833 | Highland 1 | Went to Turbine 20 with Garnik Haghverdi from Siemens industry to perform tests on the gen slip ring. Operating hours 11268 | KRAYN-WKO-NDX-20100826 | 1
KRAYN-WKO-NDX-20100827-01 | No work order description provided by contractor | 2010-08-27 | 2010-08-27 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 7.1833 | Highland 1 | Avanco techs cleaned the tower. Nordex assisted, cleaned nacelle and worked on yaw parameters 12701.87 op hrs | KRAYN-WKO-NDX-20100827 | 1
KRAYN-WKO-NDX-20100827-02 | WTG Manual Stop | 2010-08-27 | 2010-08-27 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.36667 | Highland 1 | Went to Turbine 12 with Garnik Haghverdi from Siemens industry to perform tests on the gen slip ring. Operating hours 12330 | KRAYN-WKO-NDX-20100827 | 1
KRAYN-WKO-NDX-20100827-03 | WTG Manual Stop | 2010-08-27 | 2010-08-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 17.5 | Forced | KRAYN-NDX-PRT-0054 | .5 gal | 5.3833 | Highland 1 | Nordex technicians stopped the wind turbine to check the abnormal noise coming from the blades while down tower and to perform a punch list inspection. Repainted the gearbox and main bearing because the people who painted used the wrong color paint. The Zarges lift light is out and told the site lead of the light and they are on order and will replace while doing the Zarges maintenence. The blades pitch fine and inspected to see if there was any obstructions in the blade teeth everything seemed to be fine. operation hrs:11788.99 | KRAYN-WKO-NDX-20100827 | 1
KRAYN-WKO-NDX-20100828-01 | WTG System ok | 2010-08-28 | 2010-08-28 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 4.2333 | Forced |  |  | 4.2333 | Highland 1 | Escorted Avon Cos techs uptower to perform blade inspection / maintenance. I corrected some punchlist deficiencies during their work. | KRAYN-WKO-NDX-20100828 | 1
KRAYN-WKO-NDX-20100829-01 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 2.4167 | Forced |  |  | 0.45 | Highland 1 | Cleaned brake discs to prevent squealing. Dustan Thill and Aaron Edelson were in the tower for the same time. Operating hrs: 11930 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100829-02 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.5 | Highland 1 | Cleaned brake discs to prevent squealing. Dustan Thill and Aaron Edelson were in the tower for the same time. Operating hrs: 11860 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100829-03 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.33333 | Forced |  |  | 0.23333 | Highland 1 | Cleaned brake discs to prevent squealing. Dustan Thill and Aaron Edelson were in the tower for the same time. Operating hrs: 12400 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100829-04 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.83333 | Forced |  |  | 0.36667 | Highland 1 | Cleaned brake discs to prevent squealing. Dustan Thill was in the tower for the same time. Operating hrs: 12074 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100829-05 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 3.0667 | Forced |  |  | 0.5 | Highland 1 | Cleaned brake discs to prevent squealing. Dustan Thill was in the tower for the same time. Operating hrs: 11948 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100829-06 | WTG Manual Stop | 2010-08-29 | 2010-08-29 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.2333 | Highland 1 | Cleaned brake discs to prevent squealing. Operating hrs: 9709 | KRAYN-WKO-NDX-20100829 | 1
KRAYN-WKO-NDX-20100830-01 | No work order description provided by contractor | 2010-08-30 | 2010-08-30 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.35 | Highland 1 | oil sample 12446.50 hrs | KRAYN-WKO-NDX-20100830 | 1
KRAYN-WKO-NDX-20100830-02 | No work order description provided by contractor | 2010-08-30 | 2010-08-30 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.68333 | Highland 1 | oil sample 12193.86 hrs | KRAYN-WKO-NDX-20100830 | 1
KRAYN-WKO-NDX-20100830-03 | No work order description provided by contractor | 2010-08-30 | 2010-08-30 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.31667 | Highland 1 | oil sample 11348.62 hrs | KRAYN-WKO-NDX-20100830 | 1
KRAYN-WKO-NDX-20100830-04 | Yaw MotBrake not open | 2010-08-30 | 2010-08-30 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 9 | Forced |  |  | 4.1167 | Highland 1 | Yaw Motor Brake not open, adjusted the limit switches on the brakes of the motors. 11333.73 op hrs | KRAYN-WKO-NDX-20100830 | 1
KRAYN-WKO-NDX-20100830-05 | WTG Manual Stop | 2010-08-30 | 2010-08-30 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 37.5 | Forced |  |  | 7.4667 | Highland 1 | Went to WT 25 with Adam Wangler from Engineering to attampt a blade bolt extraction. Almost completed the extraction but ran into a problem with the tools. The extractor did not fit in the bolt hole. We had to bring it to a machine shop to have it fixed. We will have to go pick it up at 9am on the 31st and go up to finish the extraction. Operating hours 10680. | KRAYN-WKO-NDX-20100830 | 1
KRAYN-WKO-NDX-20100831-01 | No work order description provided by contractor | 2010-08-31 | 2010-08-31 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 10 | Forced |  |  | 4.6 | Highland 1 | Avanco cleaned tower, nordex assisted and did punch list item which included. 21) Dust cover on valves dry rotted and cracking. 25) Rain seal on blade loose. 30,31) oil leak 41) cigarette in ladder rung 11722.60 op hrs | KRAYN-WKO-NDX-20100831 | 1
KRAYN-WKO-NDX-20100903-01 | WTG Manual Stop | 2010-09-03 | 2010-09-03 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0335 | 5 | 4.0797 | Highland 1 | Oil on brake pads due to damaged o-rings. Replaced 5 Svendborg yaw brake pads as per instruction K0801_011371_EN_Rev1, and cleanded affected areas. Replaced damaged o-rings. Charles Martin and Sean Illig were in the tower for the same amount of time. Operation hrs: 10014 | KRAYN-WKO-NDX-20100903 | 1
KRAYN-WKO-NDX-20100906-01 | Hyd OilLevel L Stopp | 2010-09-06 | 2010-09-06 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0029,KRAYN-NDX-PRT-0555 | .750 gallon,1 | 13.5333 | Highland 1 | Went up tower to find out why this fault fm250 was on. Found the tank to be low on oil added a small amount of oil. Then went to run a test on the hyd station and found out the 70 Bar accumulator leaking from the top. 11846.85 op hrs | KRAYN-WKO-NDX-20100906 | 1
KRAYN-WKO-NDX-20100906-02 | SafetyChain Activated | 2010-09-06 | 2010-09-13 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.51667 | Highland 1 | Turbine went down on a safety chain fault. Techs went out to check Q10 breaker. Noticed some of the set points where adjusted. We then put the set points back to what the turbine next to it was set at. Turbine is now in operation and will be watched tonight. 1339.44 op hrs | KRAYN-WKO-NDX-20100906 | 1
KRAYN-WKO-NDX-20100907-01 | Yaw MotBrake not closed | 2010-09-07 | 2010-09-07 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.65 | Highland 1 | nordex techs went up turbine to investigate a yaw motor brake not closed. Found out the limit switch for the brake on the motor the left of the turbine if you are facing the hub needed a small adjustment. Then techs procceeded to yaw the turbine to make sure the switch was in sync with the other motor. After a manual yaw test the techs then put it out of the wind and let the auto yaw bring it back. 12517.68 op hrs | KRAYN-WKO-NDX-20100907 | 1
KRAYN-WKO-NDX-20100909-01 | LV MainSwitch OFF | 2010-09-09 | 2010-09-09 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.9 | Highland 1 | Nordex technicians traveled to faulted turbine to troubleshoot the FM 300 fault. There were also other faults on this turbine , so the techs used the fast log portion of NC 2 and found that the rotor sensors needed some adjustment. Technicians beleive there could be a Q 10 problem will return to troubleshoot further Operation hrs: 13019.33 | KRAYN-WKO-NDX-20100909 | 1
KRAYN-WKO-NDX-20100910-01 | No work order description provided by contractor | 2010-09-10 | 2010-09-10 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 33 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 6 | Highland 1 | Nordex techs Perfromed a type 2 maint. Which included a gen. alignment in which this turbine needs aligned.Replaced hydrualic filter and offline gear oil filter. Also performed a sonic and wind vane alignment. Put in the new slipring prototype. Did some cleaning of the turbine. New slipring serial number #0018. 11942.95 op hrs | KRAYN-WKO-NDX-20100910 | 1
KRAYN-WKO-NDX-20100910-02 | WTG Manual Stop | 2010-09-10 | 2010-09-10 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 1.9333 | Highland 1 | john bennett was up tower with me as we worked on abb yaw convertor. Set up Windows Data Logger for anaysis of yaw converter signals. 12064.02 opp. Hours | KRAYN-WKO-NDX-20100910 | 1
KRAYN-WKO-NDX-20100914-01 | WTG Manual Stop | 2010-09-14 | 2010-09-14 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.46667 | Highland 1 | Cleaned brake discs to prevent squealing. Op hrs. 11703.83h | KRAYN-WKO-NDX-20100914 | 1
KRAYN-WKO-NDX-20100914-02 | WTG Manual Stop | 2010-09-14 | 2010-09-14 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.58167 | Highland 1 | Cleaned brake discs to prevent squealing. Op hrs. 9923.88h | KRAYN-WKO-NDX-20100914 | 1
KRAYN-WKO-NDX-20100914-03 | WTG Manual Stop | 2010-09-14 | 2010-09-14 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.64639 | Highland 1 | Cleaned brake discs to prevent squealing. Op hrs.9657.68h | KRAYN-WKO-NDX-20100914 | 1
KRAYN-WKO-NDX-20100914-04 | WTG Manual Stop | 2010-09-14 | 2010-09-14 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.59833 | Highland 1 | Cleaned brake discs to prevent squealing. Op hrs. 9391.73h | KRAYN-WKO-NDX-20100914 | 1
KRAYN-WKO-NDX-20100918-01 | WTG Manual Stop | 2010-09-18 | 2010-09-18 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 1.5219 | Highland 1 | Performed Type II Maintenance on WTG: 03, to include cleaning, filling hydraulic station accumulators, and filling generator coolant. Op hrs. 13484.93 | KRAYN-WKO-NDX-20100918 | 1
KRAYN-WKO-NDX-20100920-01 | SafetyChain Activated | 2010-09-20 | 2010-09-20 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 3.7333 | Highland 1 | Turbine went down on safety chain, which was caused by a rpm sensor monitor fault (fm55). Nordex tech went up tower to trouble shoot, we checked the cables and sensor. Found no cuts or tears in the cabling. Next step we changed the sensors around and found ou the problem did not follow it stayed with in the 142A8 module. The next step we did was we swap the cabling at the module with the other gen rpm sensor on module 142A9. Problem did not travel with the cable or sensor. Last thing we tried was a relanding of the wires and recommissioned the Monitor sensor 142A8. Turbine reset and was ran up to 650 rpms first then stop to see if the movement of the tower would trip it, it did not. Then ran up to 800rpms did the same test and did not fault. Turbine was then started and was running when techs left. 9950.66 op hrs | KRAYN-WKO-NDX-20100920 | 1
KRAYN-WKO-NDX-20100921-01 | WTG Manual Stop | 2010-09-21 | 2010-09-21 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 15 | Planned | KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0062 | 4,2 | 6.5464 | Highland 1 | Completed Type II Maintenance. Cleaned hub and slip ring, and cleaned and replaced filters for generator. Replaced 2 Skylight windows. Opened and visually inspected gearbox gears. Charles Martin (11979) was presnet for the same amount of time as Michael Campagno(11908). Op hrs: 10583.48h | KRAYN-WKO-NDX-20100921 | 1
KRAYN-WKO-NDX-20100921-02 | WTG Manual Stop | 2010-09-21 | 2010-09-21 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.29222 | Highland 1 | Remove zip ties from drip loop cables.Charles Martin was in the tower for the same times. Op hrs: 10209.05 hrs. | KRAYN-WKO-NDX-20100921 | 1
KRAYN-WKO-NDX-20100921-03 | SafetyChain Activated | 2010-09-21 | 2010-09-21 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0569 | 1 | 3.1239 | Highland 1 | Removed, replaced and reprogramed Pepperl and Fuchs monitor. Charles Martin (11979) was in the tower for the same amount of time. Op hrs: 9991.90h | KRAYN-WKO-NDX-20100921 | 1
KRAYN-WKO-NDX-20100922-01 | Gen brushWear Warn | 2010-09-22 | 2010-09-22 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.6833 | Highland 1 | Turbine 5 has been giving a Gen BrushWear Warn. Nordex techs went uptower to investigate a micro switch on the slipring,found one of the grounding micro switch not reading right. When switch is closed "1.9345 k ohms". On that reading we decided the switch is not working properly. Tech then took out the bad micro switch and put in the new one. Warning has been cleared and turbine will be monitored. 12192.05 op hrs SAP# 27086 Micro switch for Gen slip ring | KRAYN-WKO-NDX-20100922 | 1
KRAYN-WKO-NDX-20100923-01 | WTG Manual Stop | 2010-09-23 | 2010-09-23 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 27.75 | Planned | KRAYN-NDX-PRT-0871,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0074 | 1,1,1 | 6.8333 | Highland 1 | Nordex technicians stopped the wind turbine to perform type 2 maintenance which includes blade greasing, slip ring in hub cleaning and lubricating, hub clean up, changed gearbox off line filter and hydraulic filters, gearbox inspection with foam report, rotor brake checks, yaw brake system checks, convertor and generator cooler checks, top box and bottom box checks and some nacelle cleaning. Also directed by Everpower to change the square ice sensor to the oval ice sensor. operation hrs:13327.20 | KRAYN-WKO-NDX-20100923 | 1
KRAYN-WKO-NDX-20100923-02 | WTG Manual Stop | 2010-09-23 | 2010-09-23 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 27.75 | Planned | KRAYN-NDX-PRT-0871,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0074 | 1,1,1 | 6.8333 | Highland 1 | Nordex technicians stopped the wind turbine to perform type 2 maintenance which includes blade greasing, slip ring in hub cleaning and lubricating, hub clean up, changed gearbox off line filter and hydraulic filters, gearbox inspection with foam report, rotor brake checks, yaw brake system checks, convertor and generator cooler checks, top box and bottom box checks and some nacelle cleaning. Also directed by Everpower to change the square ice sensor to the oval ice sensor. operation hrs:13327.20 | KRAYN-WKO-NDX-20100923 | 1
KRAYN-WKO-NDX-20100924-01 | WTG Manual Stop | 2010-09-24 | 2010-09-24 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 10.5 | Planned |  |  | 1.2667 | Highland 1 | Nordex technicians stopped the wind turbine to perform type 2 maintenance. All the equipment and parts needed to perform the maintenance was lifted up tower to perform the maintenance.In the process of lifting we were called and told that wind turbine 22 faulted so the technicians went to the down turbine to trouble shoot. | KRAYN-WKO-NDX-20100924 | 1
KRAYN-WKO-NDX-20100924-02 | WTG Manual Stop | 2010-09-24 | 2010-09-24 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 10.5 | Planned |  |  | 1.2667 | Highland 1 | Nordex technicians stopped the wind turbine to perform type 2 maintenance. All the equipment and parts needed to perform the maintenance was lifted up tower to perform the maintenance.In the process of lifting we were called and told that wind turbine 22 faulted so the technicians went to the down turbine to trouble shoot. | KRAYN-WKO-NDX-20100924 | 1
KRAYN-WKO-NDX-20100924-03 | WTG Manual Stop | 2010-09-24 | 2010-09-24 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 12 | Planned |  |  | 3.75 | Highland 1 | Nordex technicians stopped the wind turbine to continue type II maintanence. Completion included generator allginment and cleaning. Production hours at stop time = 13343 hrs. | KRAYN-WKO-NDX-20100924 | 1
KRAYN-WKO-NDX-20100927-01 | WTG Manual Stop | 2010-09-27 | 2010-09-27 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.6667 | Highland 1 | Performed a Zarges maint. On the lift system with wind turbine solution tech. 13111.28 op hrs | KRAYN-WKO-NDX-20100927 | 1
KRAYN-WKO-NDX-20100927-02 | WTG Manual Stop | 2010-09-27 | 2010-09-27 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.6667 | Highland 1 | Performed a Zarges maint. On the lift system with wind turbine solution tech. 13111.28 op hrs | KRAYN-WKO-NDX-20100927 | 1
KRAYN-WKO-NDX-20100927-03 | WTG Manual Stop | 2010-09-27 | 2010-09-27 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 21.25 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 4.3667 | Highland 1 | Nordex tech performed a type 2 maint. Which included, changing of the filters, cleaned grease traps, cleaned the slip ring, cleaned of the nacelle, check of the yaw oil level and check of the hyd. Level oil. 13111.28 op hrs | KRAYN-WKO-NDX-20100927 | 1
KRAYN-WKO-NDX-20100927-04 | WTG Manual Stop | 2010-09-27 | 2010-09-27 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 21.25 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 4.3667 | Highland 1 | Nordex tech performed a type 2 maint. Which included, changing of the filters, cleaned grease traps, cleaned the slip ring, cleaned of the nacelle, check of the yaw oil level and check of the hyd. Level oil. 13111.28 op hrs | KRAYN-WKO-NDX-20100927 | 1
KRAYN-WKO-NDX-20100927-05 | Gear OilTemp Sump H Warn | 2010-09-27 | 2010-09-27 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 2.3333 | Highland 1 | Nordex tech went up this turbine with charles stauffer to troubleshoot a Gear OilTemp Sump Warning H Warn (FM 831). For this fault we just checked to make sure all the lines were open for a good flow of gear oil. We also have relanded 2 of the 5 wires and noticed a drop of 10 degrees in temp. Also nordex tech worked with Charlie on the yaw triggers of the ABB convertor. | KRAYN-WKO-NDX-20100927 | 1
KRAYN-WKO-NDX-20100928-01 | WTG Manual Stop | 2010-09-28 | 2010-09-28 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.78333 | Highland 1 | Went up tower to change yaw convertor parameters with nordex engineer Charles Stauffer, also changed Yaw brake dragging pressure to 30 bar. | KRAYN-WKO-NDX-20100928 | 1
KRAYN-WKO-NDX-20100928-02 | WTG Manual Stop | 2010-09-28 | 2010-09-28 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 9 | Forced |  |  | 3.4 | Highland 1 | Went up tower to replace bad light bulb in nacelle, sanded yaw brake disc stopped all yawing noise from occuring, changed yaw brake dragging pressure to 30 bar, checked abb convertor with Charlie Staufer Nordex engineer and took many trigger files off tHe convertor for data analyzing of Ramme yaw motors. | KRAYN-WKO-NDX-20100928 | 1
KRAYN-WKO-NDX-20100928-03 | WTG Manual Stop | 2010-09-28 | 2010-09-28 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 16 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0058 | 1,1,1 | 6 | Highland 1 | Nordex tech performed a type 2 maint. Which included changing of the generatof filters, cleaned grease traps, changing oil and hydraulic fluid filters, filling generator coolant. 2 WTS techs were present. 11938 op. hours. | KRAYN-WKO-NDX-20100928 | 1
KRAYN-WKO-NDX-20100929-01 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 13 | Planned |  |  | 8.5667 | Highland 1 | Nordex technicians performed type 2 maintenance which includes sonic and wind vane alignment , hub greasing and slipring cleaning, performed a generator alignment which is under investigation, nacelle cleaning and hub cleaning. Operation hrs:13170.72 Wind solution techs helped with the maintenance. | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-02 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 13 | Planned |  |  | 8.5667 | Highland 1 | Nordex technicians performed type 2 maintenance which includes sonic and wind vane alignment , hub greasing and slipring cleaning, performed a generator alignment which is under investigation, nacelle cleaning and hub cleaning. Operation hrs:13170.72 Wind solution techs helped with the maintenance. | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-03 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.6167 | Highland 1 | Charlie Stauffer was up turbine with me for the same amount of hours. Replaced slipring in hub with new type. | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-04 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 1.8 | Highland 1 | Nordex techs took all tools needed to do complete type 2 maint. Got called out of tower to go help tower one with alignment. 11962.35 op hrs | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-05 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 1.8 | Highland 1 | Nordex techs took all tools needed to do complete type 2 maint. Got called out of tower to go help tower one with alignment. 11962.35 op hrs | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-06 | Pitch3 Not Ready | 2010-09-29 | 2010-09-29 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 15.5 | Forced | KRAYN-NDX-PRT-0686 | 1 | 6.55 | Highland 1 | Turbine went down on a pitch 3 not ready. Nordex techs been having problems with this turbine been trying to fix by going through a process of elimination. Today we went into the hub and saw that on nc2 it was sayin that pitch 3 was not ready. We looked more into this and noticed that pitch 3 was saying it has already reached it position when it was faulted. all the other Blades plus 3 were all at 90 degrees so we then proceeded to change out the pitchmaster. As of tonight the turbine was running will be watched by on call crew . 11009.46 op hrs | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-07 | Pitch3 Not Ready | 2010-09-29 | 2010-09-29 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 15.5 | Forced | KRAYN-NDX-PRT-0686 | 1 | 6.55 | Highland 1 | Turbine went down on a pitch 3 not ready. Nordex techs been having problems with this turbine been trying to fix by going through a process of elimination. Today we went into the hub and saw that on nc2 it was sayin that pitch 3 was not ready. We looked more into this and noticed that pitch 3 was saying it has already reached it position when it was faulted. all the other Blades plus 3 were all at 90 degrees so we then proceeded to change out the pitchmaster. As of tonight the turbine was running will be watched by on call crew . 11009.46 op hrs | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100929-08 | WTG Manual Stop | 2010-09-29 | 2010-09-29 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0480 | 1 | 1.5833 | Highland 1 | Climbed up turbine with Charles Stauffer to replace yaw converter and install parameter files on yaw converter. | KRAYN-WKO-NDX-20100929 | 1
KRAYN-WKO-NDX-20100930-01 | No work order description provided by contractor | 2010-09-30 |  | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 8.5667 | Highland 1 | Nordex and Wind solution technicians never stopped the wind turbine because we only had to change a man lift cable. The cable was bought local so there for there is no sap cable. The operation hrs are 13194.25 | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-02 | No work order description provided by contractor | 2010-09-30 |  | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 8.5667 | Highland 1 | Nordex and Wind solution technicians never stopped the wind turbine because we only had to change a man lift cable. The cable was bought local so there for there is no sap cable. The operation hrs are 13194.25 | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-03 | WTG Manual Stop | 2010-09-30 | 2010-09-30 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.93333 | Highland 1 | Charlie Stauffer was at this turbine for the same amount of hours. Performed Generator slipring inspection. | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-04 | WTG Manual Stop | 2010-09-30 | 2010-09-30 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.7 | Highland 1 | Charlie Stauffer was at this turbine for the same amount of hours. Generator slipring Inspection. | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-05 | WTG Manual Stop | 2010-09-30 | 2010-09-30 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 2.8 | Highland 1 | Nordex tech and WTS techs peformed a type 2 maint.today. Which included a gen alignment check, which was aligned.Also did some cleaning of the naccelle and installing just the box part of the ice detector. Due to weather only nacelle work was done 11962.35 op hrs | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-06 | WTG Manual Stop | 2010-09-30 | 2010-09-30 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 0.88333 | Highland 1 | Charlie Stauffer was at the turbine for the same amount of hours. Generator slipring inspections. | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-07 | WTG Manual Stop | 2010-09-30 | 2010-09-29 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 1.3333 | Highland 1 | Charlie Stauffer was at the turbine for the same amount of hours. Inspected Generator sliprings. | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20100930-08 | WTG Manual Stop | 2010-09-30 | 2010-09-30 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 2.8 | Highland 1 | Nordex tech and WTS techs peformed a type 2 maint.today. Which included a gen alignment check, which was aligned.Also did some cleaning of the naccelle and installing just the box part of the ice detector. Due to weather only nacelle work was done 11962.35 op hrs | KRAYN-WKO-NDX-20100930 | 1
KRAYN-WKO-NDX-20101001-01 | WTG Manual Stop | 2010-10-01 | 2010-10-01 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.98333 | Highland 1 | went up tower to inspect the generator slipring, inspect the ice detection sensor, with nordex engineering Charles Stauffer. While at the tower the service lift cable broke fixed the problem. | KRAYN-WKO-NDX-20101001 | 1
KRAYN-WKO-NDX-20101001-02 | WTG Manual Stop | 2010-10-01 | 2010-10-01 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.95 | Highland 1 | Went up tower to inspect generator slip rings with nordex engineering Charles Stauffer, also while up tower worked on ABB convertor for yaw system to collect data from Ramme yaw motors, and logged into ice detection unit to check parameters and settings to have a record of changes that will be implemented this winter. | KRAYN-WKO-NDX-20101001 | 1
KRAYN-WKO-NDX-20101001-03 | WTG Manual Stop | 2010-10-01 | 2010-10-01 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.95 | Highland 1 | Went up tower to inspect generator slip rings with nordex engineering Charles Stauffer, also while up tower worked on ABB convertor for yaw system to collect data from Ramme yaw motors, and logged into ice detection unit to check parameters and settings to have a record of changes that will be implemented this winter. | KRAYN-WKO-NDX-20101001 | 1
KRAYN-WKO-NDX-20101001-04 | WTG Manual Stop | 2010-10-01 | 2010-10-01 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 14.5 | Planned | KRAYN-NDX-PRT-0871 | 1 | 5.8167 | Highland 1 | Nordex Techs/WTS tech performed a type 2 maint. Which included, greasing of the blades, cleaning of the slip ring and alignment of sonic/wind vane. Finnished the cleaning as well. Finnished some punch list items. Rain seal peeling up (44).Lid ram leaking (47). Rain seal peeling (49). Lightning brushes riding on grease seal (51). Oil leak (56). Oil leak (54). oil leak/dirty (57). Rain seal peeling up (60). Paint damage/corrosion (62). Paint damge/corrosion (63). Also installed the sensor part of the ice sensor .11983.14 op hrs | KRAYN-WKO-NDX-20101001 | 1
KRAYN-WKO-NDX-20101001-05 | WTG Manual Stop | 2010-10-01 | 2010-10-01 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 14.5 | Planned | KRAYN-NDX-PRT-0871 | 1 | 5.8167 | Highland 1 | Nordex Techs/WTS tech performed a type 2 maint. Which included, greasing of the blades, cleaning of the slip ring and alignment of sonic/wind vane. Finnished the cleaning as well. Finnished some punch list items. Rain seal peeling up (44).Lid ram leaking (47). Rain seal peeling (49). Lightning brushes riding on grease seal (51). Oil leak (56). Oil leak (54). oil leak/dirty (57). Rain seal peeling up (60). Paint damage/corrosion (62). Paint damge/corrosion (63). Also installed the sensor part of the ice sensor .11983.14 op hrs | KRAYN-WKO-NDX-20101001 | 1
KRAYN-WKO-NDX-20101004-01 | US_Highland_Fan Wheel Retro | 2010-10-04 | 2010-10-04 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.076389 | Forced | KRAYN-NDX-PRT-0959 | 2 | 0.084722 | Highland 1 | Nordex technicians removed the old yaw motor fins and installed the new ones and adjusted micro switches for the motor brakes. | KRAYN-WKO-NDX-20101004 | 1
KRAYN-WKO-NDX-20101004-02 | WTG Manual Stop | 2010-10-04 | 2010-10-05 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 39 | Planned | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0959 | 1,1,1,1 | 31.5833 | Highland 1 | Nordex technicians stopped the wind turbine to change the Ramme motors back to the old style and to perform the retro. Also had to change the parameter files in the yaw convertor. Had to leave the wind turbine down because there were some troubles with the turbine yawing. Operation hrs:11848.47 | KRAYN-WKO-NDX-20101004 | 1
KRAYN-WKO-NDX-20101004-03 | WTG Manual Stop | 2010-10-04 | 2010-10-05 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 39 | Planned | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0959 | 1,1,1,1 | 31.5833 | Highland 1 | Nordex technicians stopped the wind turbine to change the Ramme motors back to the old style and to perform the retro. Also had to change the parameter files in the yaw convertor. Had to leave the wind turbine down because there were some troubles with the turbine yawing. Operation hrs:11848.47 | KRAYN-WKO-NDX-20101004 | 1
KRAYN-WKO-NDX-20101004-04 | WTG Manual Stop | 2010-10-04 | 2010-10-04 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017 | 1,1 | 5.6167 | Highland 1 | Nordex techs along with a WTS tech perfromed type 2 maintenance. This included change of filters,hydraulic pressure check,change of generator filters,clean of generator slip ring, generator alignment check ( -1.6 mm out of adjustment), filled up grease containers and check of phase brushes on generator side ( 42mm was the shortest). 10275.45 op hrs | KRAYN-WKO-NDX-20101004 | 1
KRAYN-WKO-NDX-20101004-05 | WTG Manual Stop | 2010-10-04 | 2010-10-04 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017 | 1,1 | 5.6167 | Highland 1 | Nordex techs along with a WTS tech perfromed type 2 maintenance. This included change of filters,hydraulic pressure check,change of generator filters,clean of generator slip ring, generator alignment check ( -1.6 mm out of adjustment), filled up grease containers and check of phase brushes on generator side ( 42mm was the shortest). 10275.45 op hrs | KRAYN-WKO-NDX-20101004 | 1
KRAYN-WKO-NDX-20101005-01 | WTG Manual Stop | 2010-10-05 | 2010-10-05 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 29.25 | Planned | KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0074 | 2,2,1,1,1 | 7.4667 | Highland 1 | Performed a type 2 maint. Today included. A generator alignment check was within in tolerance. Did the coolant check of both the gen and bottom cab. Performed a sonic alignment and wind vane alignment. Did hub work which included, grease of the blades, clean of the slipring, check of the pitch fluid and clean of the hub. Clean of the naccelle and yaw deck. Also used one tube of Ceplattyn (18674) 11846.17 op hrs | KRAYN-WKO-NDX-20101005 | 1
KRAYN-WKO-NDX-20101005-02 | WTG Manual Stop | 2010-10-05 | 2010-10-05 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 29.25 | Planned | KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0576,KRAYN-NDX-PRT-0074 | 2,2,1,1,1 | 7.4667 | Highland 1 | Performed a type 2 maint. Today included. A generator alignment check was within in tolerance. Did the coolant check of both the gen and bottom cab. Performed a sonic alignment and wind vane alignment. Did hub work which included, grease of the blades, clean of the slipring, check of the pitch fluid and clean of the hub. Clean of the naccelle and yaw deck. Also used one tube of Ceplattyn (18674) 11846.17 op hrs | KRAYN-WKO-NDX-20101005 | 1
KRAYN-WKO-NDX-20101006-01 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0293 | 1 | 0.5 | Highland 1 | Nordex technicians stopped the wind turbine to change out the UPS. The turbine was running with a UPS battery alarm the day prior tried to reset the ups but the alarm did not go away, so the nordex technicians removed and replaced the UPS. Operation hrs:12097.32 | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-02 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0293 | 1 | 0.5 | Highland 1 | Nordex technicians stopped the wind turbine to change out the UPS. The turbine was running with a UPS battery alarm the day prior tried to reset the ups but the alarm did not go away, so the nordex technicians removed and replaced the UPS. Operation hrs:12097.32 | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-03 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0237 | 5 gal,1 | 2.4 | Highland 1 | Nordex technicians stopped the wind turbine to perform Zarges maintenance which includes function tests and cleaning, chassis checks and reinstalled the brackets for the man lift door and in the process of megging manlift cables found the supply breaker cracked removed and replaced, also while the turbine was shut down we added gearbox oil and gearbox checklist. Operation hrs:11848.47 | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-04 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0237 | 5 gal,1 | 2.4 | Highland 1 | Nordex technicians stopped the wind turbine to perform Zarges maintenance which includes function tests and cleaning, chassis checks and reinstalled the brackets for the man lift door and in the process of megging manlift cables found the supply breaker cracked removed and replaced, also while the turbine was shut down we added gearbox oil and gearbox checklist. Operation hrs:11848.47 | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-05 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13 | Planned | KRAYN-NDX-PRT-0017 | 1 | 6.6 | Highland 1 | Nordex techs performed type 2 maint. Which included sonic alignment and wind vane,Grease of blade bearings,clean of the slip ring and clean of the nacelle. Replaced a hydraulic pressure filter as well 10317.11 op hrs | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-06 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13 | Planned | KRAYN-NDX-PRT-0017 | 1 | 6.6 | Highland 1 | Nordex techs performed type 2 maint. Which included sonic alignment and wind vane,Grease of blade bearings,clean of the slip ring and clean of the nacelle. Replaced a hydraulic pressure filter as well 10317.11 op hrs | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-07 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13 | Planned | KRAYN-NDX-PRT-0017 | 1 | 6.6 | Highland 1 | Nordex techs performed type 2 maint. Which included sonic alignment and wind vane,Grease of blade bearings,clean of the slip ring and clean of the nacelle. Replaced a hydraulic pressure filter as well 10317.11 op hrs | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101006-08 | WTG Manual Stop | 2010-10-06 | 2010-10-06 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13 | Planned | KRAYN-NDX-PRT-0017 | 1 | 6.6 | Highland 1 | Nordex techs performed type 2 maint. Which included sonic alignment and wind vane,Grease of blade bearings,clean of the slip ring and clean of the nacelle. Replaced a hydraulic pressure filter as well 10317.11 op hrs | KRAYN-WKO-NDX-20101006 | 1
KRAYN-WKO-NDX-20101007-01 | Gear OilTemp Sump H Warn | 2010-10-07 | 2010-10-07 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 19 | Planned | KRAYN-NDX-PRT-0327 | 1 | 7.5333 | Highland 1 | Nordex technicians stopped the wind turbine to trouble shoot the gearbox oil high temp problem. Changed the manifold block on the oil filter and checked to see if the oil was being pumped out from the coolers and checked if the pt 100's were operational. Operation hrs:13361.27 | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-02 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 5.8667 | Highland 1 | Nordex techs along with wts tech performed a type 2 maint. Today techs did hydraulic checks and filter changes.Clean of the generator slipring,check of the brushes and change of the filters. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-03 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 5.8667 | Highland 1 | Nordex techs along with wts tech performed a type 2 maint. Today techs did hydraulic checks and filter changes.Clean of the generator slipring,check of the brushes and change of the filters. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-04 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 5.8667 | Highland 1 | Performed a Zarges maint. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-05 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 5.8667 | Highland 1 | Performed a Zarges maint. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-06 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 5.8667 | Highland 1 | Nordex techs along with wts tech performed a type 2 maint. Today techs did hydraulic checks and filter changes.Clean of the generator slipring,check of the brushes and change of the filters. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-07 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 5.8667 | Highland 1 | Nordex techs along with wts tech performed a type 2 maint. Today techs did hydraulic checks and filter changes.Clean of the generator slipring,check of the brushes and change of the filters. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-08 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 5.8667 | Highland 1 | Performed a Zarges maint. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-09 | WTG Manual Stop | 2010-10-07 | 2010-10-07 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 5.8667 | Highland 1 | Performed a Zarges maint. | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-10 | SafetyChain Activated | 2010-10-07 | 2010-10-07 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 10.9167 | Highland 1 | The wind turbine faulted during the night on a safety chain fault and nordex service technicians came in to troubleshoot the generator/rotor sensors and speed monitoring system and found some minor discrepancies and corrected them, in the process of starting the turbine it faulted with a interbus stop. Being that the turbine had not faulted for this problem did a complete hub shutdown and started the wind turbine. Operation hrs: 10518.08 | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101007-11 | SafetyChain Activated | 2010-10-07 | 2010-10-07 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 10.9167 | Highland 1 | The wind turbine faulted during the night on a safety chain fault and nordex service technicians came in to troubleshoot the generator/rotor sensors and speed monitoring system and found some minor discrepancies and corrected them, in the process of starting the turbine it faulted with a interbus stop. Being that the turbine had not faulted for this problem did a complete hub shutdown and started the wind turbine. Operation hrs: 10518.08 | KRAYN-WKO-NDX-20101007 | 1
KRAYN-WKO-NDX-20101008-01 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.65 | Highland 1 | Charles Henderson was with me the for the same amount of hours. Cleaned slipring in hub. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-02 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.3333 | Highland 1 | Charles Henderson was with me the for the same amount of hours. Cleaned slipring in hub. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-03 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.65 | Highland 1 | Nordex tech along with WTS tech performed a type 2 maint. Today techs did hub work which included cleaning of the slip ring, pitch fluid check and grease of the blades. Then performed a sonic alignment and wind vane alignment. Completed a Gen alignment check, measurements were good. Finished the day with cleaning the hub, nacelle, tower and bottom box. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-04 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.65 | Highland 1 | Nordex tech along with WTS tech performed a type 2 maint. Today techs did hub work which included cleaning of the slip ring, pitch fluid check and grease of the blades. Then performed a sonic alignment and wind vane alignment. Completed a Gen alignment check, measurements were good. Finished the day with cleaning the hub, nacelle, tower and bottom box. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-05 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.65 | Highland 1 | Nordex tech along with WTS tech performed a type 2 maint. Today techs did hub work which included cleaning of the slip ring, pitch fluid check and grease of the blades. Then performed a sonic alignment and wind vane alignment. Completed a Gen alignment check, measurements were good. Finished the day with cleaning the hub, nacelle, tower and bottom box. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-06 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.1833 | Highland 1 | Charles Henderson was with me the for the same amount of hours. Cleaned slipring in hub. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-07 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 17 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0074 | 1,2,4,1 | 5.9 | Highland 1 | Operation hrs:12246.76 Nordex technicians performed type 2 maintenance which includes Gearbox inspection with foam report, Generator slip ring cleaning with filter change and measured the phase brushes and ground brushes, yaw motor inspection and adjusted motor number 2's micro switch, hydraulic station accumulator checks with filter replacement, Gearbox offline filter replacement and cleaned mainbearing drip pan. Installed new skylites with cauking, cleaned up gear oil leak and found that the inspection plate was leaking retightened and will investigate further. Added Grease to the mainbearing , generator, yaw auto lubrication units, added coolant to convertor and generator cooling pumps. Adam Mckenzie with wind turbine solutions helped with the maintenance. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-08 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 17 | Planned | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0074 | 1,2,4,1 | 5.9 | Highland 1 | Operation hrs:12246.76 Nordex technicians performed type 2 maintenance which includes Gearbox inspection with foam report, Generator slip ring cleaning with filter change and measured the phase brushes and ground brushes, yaw motor inspection and adjusted motor number 2's micro switch, hydraulic station accumulator checks with filter replacement, Gearbox offline filter replacement and cleaned mainbearing drip pan. Installed new skylites with cauking, cleaned up gear oil leak and found that the inspection plate was leaking retightened and will investigate further. Added Grease to the mainbearing , generator, yaw auto lubrication units, added coolant to convertor and generator cooling pumps. Adam Mckenzie with wind turbine solutions helped with the maintenance. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-09 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.81667 | Highland 1 | Charles Henderson (12102) was with me the for the same amount of hours. Cleaned slipring in hub. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101008-10 | WTG Manual Stop | 2010-10-08 | 2010-10-08 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.65 | Highland 1 | Nordex tech along with WTS tech performed a type 2 maint. Today techs did hub work which included cleaning of the slip ring, pitch fluid check and grease of the blades. Then performed a sonic alignment and wind vane alignment. Completed a Gen alignment check, measurements were good. Finished the day with cleaning the hub, nacelle, tower and bottom box. | KRAYN-WKO-NDX-20101008 | 1
KRAYN-WKO-NDX-20101009-01 | SafetyChain Activated | 2010-10-09 | 2010-10-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 4.4333 | Highland 1 | turbine faulted tripping the main breakers, we inspected the trip settings of the breakers checked the grid for spikes or dips checked the adjustment of the inductive sensors on the high speed side and low side. All was ok reset the main breakers cleared the saftey chain faults and started the turbine back up. | KRAYN-WKO-NDX-20101009 | 1
KRAYN-WKO-NDX-20101011-01 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 1 | Highland 1 | stopped turbine for yaw disc sanding robert zaccaria from WTS assisted | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-02 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.53333 | Highland 1 | stopped turbine for yaw disc sanding robert zaccaria from WTS assisted. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-03 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 1.8167 | Highland 1 | Nordex tech work today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-04 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 1.8167 | Highland 1 | Nordex tech work today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-05 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.6892 | Highland 1 | Nordex techs went out today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-06 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.6892 | Highland 1 | Nordex techs went out today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-07 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 0.91667 | Highland 1 | Nordex techs went out today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-08 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 0.91667 | Highland 1 | Nordex techs went out today to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-09 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 1.5167 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-10 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 1.5167 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101011-11 | WTG Manual Stop | 2010-10-11 | 2010-10-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 4.55 | Forced |  |  | 0.53333 | Highland 1 | stopped turbine for yaw disc sanding robert zaccaria from WTS assisted. | KRAYN-WKO-NDX-20101011 | 1
KRAYN-WKO-NDX-20101012-01 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.35 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-02 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.35 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-03 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.35 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-04 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.35 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-05 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 1.3333 | Forced |  |  | 0.56667 | Highland 1 | stopped turbine for yaw disc sanding robert zaccaria from WTS assisted | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-06 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 0.93333 | Highland 1 | stopped turbine for yaw disc sanding robert zaccaria from WTS assisted | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-07 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 1.05 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101012-08 | WTG Manual Stop | 2010-10-12 | 2010-10-12 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 1.05 | Highland 1 | Nordex tech along with WTS tech went up to grind the yaw disc to eliminate the yaw noise. | KRAYN-WKO-NDX-20101012 | 1
KRAYN-WKO-NDX-20101013-01 | WTG Manual Stop | 2010-10-13 | 2010-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 15 | Planned |  |  | 4.9833 | Highland 1 | Checked generator allignment; brought it within horizontal tolerance; began work to allign vertically, couldn't complete due to lack of neccessary tools. Cleaned yaw deck. Master tech Charles Henderson present, as was WTS employee Todd Smith. Hours in operation = 8394.5 | KRAYN-WKO-NDX-20101013 | 1
KRAYN-WKO-NDX-20101013-02 | WTG Manual Stop | 2010-10-13 | 2010-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 15 | Planned |  |  | 4.9833 | Highland 1 | Checked generator allignment; brought it within horizontal tolerance; began work to allign vertically, couldn't complete due to lack of neccessary tools. Cleaned yaw deck. Master tech Charles Henderson present, as was WTS employee Todd Smith. Hours in operation = 8394.5 | KRAYN-WKO-NDX-20101013 | 1
KRAYN-WKO-NDX-20101013-03 | WTG Manual Stop | 2010-10-13 | 2010-10-13 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 2.1833 | Highland 1 | went up tower to install new version of parameters and software into abb convertor drive with rob zaccaria of wts, also ran an auto id run to maximize the performance of the system | KRAYN-WKO-NDX-20101013 | 1
KRAYN-WKO-NDX-20101013-04 | WTG Manual Stop | 2010-10-13 | 2010-10-13 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 2.1833 | Highland 1 | went up tower to install new version of parameters and software into abb convertor drive with rob zaccaria of wts, also ran an auto id run to maximize the performance of the system | KRAYN-WKO-NDX-20101013 | 1
KRAYN-WKO-NDX-20101014-01 | WTG Manual Stop | 2010-10-14 | 2010-10-14 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 2.25 | Highland 1 | Went up tower to clean hub slipring turbine had alarm 744 present. Correct cleaner was used and fault cleared. Rob Zaccarria from WTS was with me | KRAYN-WKO-NDX-20101014 | 1
KRAYN-WKO-NDX-20101014-02 | WTG Manual Stop | 2010-10-14 | 2010-10-14 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 23 | Forced | KRAYN-NDX-PRT-0335 | 28 | 9.4667 | Highland 1 | Nordex technicians stopped the wind turbine to change the yaw brakes and clean and inspect yaw brake disc. Operation hrs: 13014.48 | KRAYN-WKO-NDX-20101014 | 1
KRAYN-WKO-NDX-20101015-01 | WTG Manual Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.1167 | Highland 1 | cleaned hub slipring with robert zaccaria from wts alarm 744 was present on the turbine. Fault cleared | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-02 | IBS Interbus Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG13 | Warranty Repair | Nordex USA OandM | 5.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.7167 | Highland 1 | Nordex technicians along with wind turbine solution tech Todd Smith stopped the wind turbine to troubleshoot the FM 700 alarm and to replace the slipring in the hub with the proto-type slipring. Operation hrs:13149.35 | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-03 | GenRot RpmMonitor Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1.9 | Planned | KRAYN-NDX-PRT-0033 | 2 | 2.5667 | Highland 1 | Adjusted arm holding inductive sensors on the main rotor. Changed inductive sensors. | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-04 | WTG Manual Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2.2333 | Planned |  |  | 1.6333 | Highland 1 | Cleaned hub slip ring in WTG 18. Used 3M General Purpose Contact Cleaner for cleaning and DeoxIT lubricant. Brad Foy of EverPower attended. 8717 hrs in operation. | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-05 | WTG Manual Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 1.9 | Highland 1 | Cleaned hub slip ring in WTG 20. Used 3M General Purpose Contact Cleaner for cleaning and DeoxIT lubricant. Brad Foy of EverPower attended. 9637 hrs in operation. | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-06 | WTG Manual Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 1.3333 | Forced |  |  | 1.1667 | Highland 1 | went up tower to clean hub slipring as alarm 744 was present prior | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101015-07 | IBS Interbus Stop | 2010-10-15 | 2010-10-15 | KRAYN-WTG13 | Warranty Repair | Nordex USA OandM | 5.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.7167 | Highland 1 | Nordex technicians along with wind turbine solution tech Todd Smith stopped the wind turbine to troubleshoot the FM 700 alarm and to replace the slipring in the hub with the proto-type slipring. Operation hrs:13149.35 | KRAYN-WKO-NDX-20101015 | 1
KRAYN-WKO-NDX-20101018-01 | WTG Manual Stop | 2010-10-18 | 2010-10-18 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0959 | 1,1,2 | 7.2 | Highland 1 | Nordex technician along with WTS techs. Changed out the yaw drive motors from Ramme to Leroy Sommer and installed the yaw fan retro, also had to reprogram the yaw convertor with new parameter files. | KRAYN-WKO-NDX-20101018 | 1
KRAYN-WKO-NDX-20101018-02 | WTG Manual Stop | 2010-10-18 | 2010-10-18 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 3.65 | Highland 1 | I went up tower due to a noise (something bouncing around in the hub), while up tower I found a broke blade bolt on the leading edge of the blade on blade2. the greasing wheel bracket was bent and the hub had 21 broken grease catch bottles along with lots of paint damage. I inspected the blade teeth and all other componets in the hub for damage, the turbine was clear to put back into opperation. I was up tower with matt smith from WTS. | KRAYN-WKO-NDX-20101018 | 1
KRAYN-WKO-NDX-20101018-03 | WTG Manual Stop | 2010-10-18 | 2010-10-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 21.5 | Planned |  |  | 9.4667 | Highland 1 | Nordex techs performed a type 2 maint. Today included a gen. alignment (completed). Hub work, Grease of the blades,replaced 8 of the blade bottles for grease fittings,clean of the slipring and clean of the Hub. Also tech did a alignment of the wind vane and ultrasonic. | KRAYN-WKO-NDX-20101018 | 1
KRAYN-WKO-NDX-20101018-04 | WTG Manual Stop | 2010-10-18 | 2010-10-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 21.5 | Planned |  |  | 9.4667 | Highland 1 | Nordex techs performed a type 2 maint. Today included a gen. alignment (completed). Hub work, Grease of the blades,replaced 8 of the blade bottles for grease fittings,clean of the slipring and clean of the Hub. Also tech did a alignment of the wind vane and ultrasonic. | KRAYN-WKO-NDX-20101018 | 1
KRAYN-WKO-NDX-20101019-01 | Pitch2 Not Ready | 2010-10-19 | 2010-10-19 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0686 | 1 | 11.75 | Highland 1 | Nordex tech went up tower to troubleshoot the FM1145. Service techs first tried to reprogram the pitch convertor but the problem did not go away. Techs then replaced the pitch convertor in blade 2. Turbine was now able to pitch and was ready to come back online. | KRAYN-WKO-NDX-20101019 | 1
KRAYN-WKO-NDX-20101019-02 | Pitch2 Not Ready | 2010-10-19 | 2010-10-19 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 10 | Forced | KRAYN-NDX-PRT-0686 | 1 | 11.75 | Highland 1 | Nordex tech went up tower to troubleshoot the FM1145. Service techs first tried to reprogram the pitch convertor but the problem did not go away. Techs then replaced the pitch convertor in blade 2. Turbine was now able to pitch and was ready to come back online. | KRAYN-WKO-NDX-20101019 | 1
KRAYN-WKO-NDX-20101019-03 | WTG Manual Stop | 2010-10-19 | 2010-10-19 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.2833 | Highland 1 | Turbine has been having fm744 warnings. Techs went up and cleaned the slipring. | KRAYN-WKO-NDX-20101019 | 1
KRAYN-WKO-NDX-20101019-04 | WTG Manual Stop | 2010-10-19 | 2010-10-19 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4.75 | Forced | KRAYN-NDX-PRT-0959 | 2 | 2.9667 | Highland 1 | Nordex techs along with WTS techs stopped the wind turbine to perform the yaw hat retro which includes removing the old fins and installing the new one and adjusting the micro switches and brake pads. | KRAYN-WKO-NDX-20101019 | 1
KRAYN-WKO-NDX-20101019-05 | WTG Manual Stop | 2010-10-19 | 2010-10-19 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 7.25 | Forced | KRAYN-NDX-PRT-0959 | 2 | 8.8167 | Highland 1 | Nordex techs along with WTS techs stopped the wind turbine to perform the yaw hat retro which includes removing the old fins and installing the new one and adjusting the micro switches and brake pads. | KRAYN-WKO-NDX-20101019 | 1
KRAYN-WKO-NDX-20101020-01 | LV InsulatMonitor 660V Stop | 2010-10-20 | 2011-10-20 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.0333 | Highland 1 |  | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101020-02 | WTG Manual Stop | 2010-10-20 | 2010-10-20 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 5.5 | Forced | KRAYN-NDX-PRT-0533 | 1 | 2.2333 | Highland 1 | Nordex technicians stopped the wind turbine to investigate the yaw problem and to set the RPM parameter value on the yaw convertor to 500, also changed valve number 225. The technicians started the wind turbine to listen to the yaw while under load and found that the turbine was pausing while yawing. | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101020-03 | WTG Manual Stop | 2010-10-20 | 2010-10-20 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0725 | 1 | 4.7 | Highland 1 | Nordex tech along with WTS tech Rob Z. stopped the wind turbine to trouble shoot the interbus fault and found that the slipring was faulty. So the technicians proceeded with the slipring in the hub removal and turned the voltage to the hub back on and still had a interbus problem with the new proto-type and after troubleshooting foundthat the rs232 serial port was damaged but were able to fix the problem and put the wind turbine to run mode. | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101020-04 | WTG Manual Stop | 2010-10-20 | 2010-10-20 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0725 | 1 | 4.7 | Highland 1 | Nordex tech along with WTS tech Rob Z. stopped the wind turbine to trouble shoot the interbus fault and found that the slipring was faulty. So the technicians proceeded with the slipring in the hub removal and turned the voltage to the hub back on and still had a interbus problem with the new proto-type and after troubleshooting foundthat the rs232 serial port was damaged but were able to fix the problem and put the wind turbine to run mode. | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101020-05 | WTG Manual Stop | 2010-10-20 | 2010-10-20 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 18 | Planned |  |  | 7 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. Techs has have completed, sonic alignment,wind vane alignment,generator check. Generator alignment,Grease of blades, clean of the slip ring and a hydraulic maint( accumulator check,pressure check). | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101020-06 | WTG Manual Stop | 2010-10-20 | 2010-10-20 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 18 | Planned |  |  | 7 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. Techs has have completed, sonic alignment,wind vane alignment,generator check. Generator alignment,Grease of blades, clean of the slip ring and a hydraulic maint( accumulator check,pressure check). | KRAYN-WKO-NDX-20101020 | 1
KRAYN-WKO-NDX-20101021-01 | US-HIGHLAND_24WEA80816_PunchList Items | 2010-10-21 | 2010-10-21 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.1875 | Forced |  |  | 0.25208 | Highland 1 | Quantity | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101021-02 | WTG Manual Stop | 2010-10-21 | 2010-10-20 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 13.5 | Forced |  |  | 3.6333 | Highland 1 | Nordex technicians along with WTS techs stopped the wind turbine to troubleshoot the yaw problem further which includes greasing the yaw bearing and thrust bearings of the yaw drive also did a backlash check to see if the turbine was in specs. Will contact nordex engineer dept. with the info that we have found. | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101021-03 | WTG Manual Stop | 2010-10-21 | 2010-10-21 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.78333 | Highland 1 | Nordex technicians along with a WTS tech stopped the wind turbine to see what the back lash is and to compare the difference with turbine 16. | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101021-04 | WTG Manual Stop | 2010-10-21 | 2010-10-21 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 4 | Planned | KRAYN-NDX-PRT-0004 | 2 | 6.05 | Highland 1 | Nordex techs did the last few things left on the punch list which included, Paint damage/corrosion (13,14). Lightning protection brushes adjusted wrong (20). We just added new brushes and pins into the holder. | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101021-05 | WTG Manual Stop | 2010-10-21 | 2010-10-21 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 13 | Planned |  |  | 6.05 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. Techs have cleaned the naccelle,did function test of the breakers,stress test of the lighting and check of the elasto bearing | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101021-06 | WTG Manual Stop | 2010-10-21 | 2010-10-21 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 13 | Planned |  |  | 6.05 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. Techs have cleaned the naccelle,did function test of the breakers,stress test of the lighting and check of the elasto bearing | KRAYN-WKO-NDX-20101021 | 1
KRAYN-WKO-NDX-20101022-01 | US-HIGHLAND-23WEA80815_Type 2 Maint. | 2010-10-22 | 2010-10-22 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.5625 | Forced | KRAYN-NDX-PRT-0725,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351 | 1,1,1,4 | 0.17639 | Highland 1 | Quantity | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101022-02 | WTG Manual Stop | 2010-10-22 | 2010-10-22 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 12.25 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 10.4333 | Highland 1 | Nordex tech along with WTS tech stopped the wind turbine to change out the Ramme motors with Lerroy motors and to perform the yaw motor retro and adjusted yaw motor brakesalso programmed yaw convertor. While tring to perform this task motor number 2 was stuck in the yaw drive and the seal leaked some oil but no damage was present. Technicians will monitor the drive for any leaks in the future. | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101022-03 | SafetyChain Activated | 2010-10-22 | 2010-10-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.86667 | Highland 1 | Nordex tech along with WTS tech went out the the turbine to reset the safety chain fault | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101022-04 | WTG Manual Stop | 2010-10-22 | 2010-10-22 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 13.5 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351 | 1,1,4 | 4.2333 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. The gen.slipring was cleaned, gen.filters were changed, alu bottles were filled up, hydraulic filter was changed, accumulators were checked and charged,oil protocol was done, stress test of lights, functional test of breakers and offline by pass filter changed | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101022-05 | WTG Manual Stop | 2010-10-22 | 2010-10-22 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 13.5 | Planned | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351 | 1,1,4 | 4.2333 | Highland 1 | Nordex techs along with WTS tech performed a type 2 maint. Today on the maint. The gen.slipring was cleaned, gen.filters were changed, alu bottles were filled up, hydraulic filter was changed, accumulators were checked and charged,oil protocol was done, stress test of lights, functional test of breakers and offline by pass filter changed | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101022-06 | SafetyChain Activated | 2010-10-22 | 2010-10-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.86667 | Highland 1 | Nordex tech along with WTS tech went out the the turbine to reset the safety chain fault | KRAYN-WKO-NDX-20101022 | 1
KRAYN-WKO-NDX-20101023-01 | Yaw MotBrake not closed | 2010-10-23 | 2010-10-23 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 4.0333 | Highland 1 | Nordex technicians had to adjust the yaw motor brake on motor number 1 because the micro swith was sticking because the brake was out of adjustment. Technicians verified all spots of gapping by feeler gage and by jumping the relay to activate the brakes. | KRAYN-WKO-NDX-20101023 | 1
KRAYN-WKO-NDX-20101023-02 | WTG Manual Stop | 2010-10-23 | 2010-10-23 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 22.65 | Forced | KRAYN-NDX-PRT-0782,KRAYN-NDX-PRT-0782 | 1,1 | 5.8333 | Highland 1 | Technicians changed 2 yaw motors on WTG 4 (replaced Ramme motor with Leroy Somers); applied retrofit fins to new yaw motors. 2 technicians from WTS also present. | KRAYN-WKO-NDX-20101023 | 1
KRAYN-WKO-NDX-20101025-01 | swap yaw motors | 2010-10-25 | 2010-10-25 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 1.6562 | Forced |  |  | 0.55208 | Highland 1 | uptower time | KRAYN-WKO-NDX-20101025 | 1
KRAYN-WKO-NDX-20101026-01 | 001 Highland 24WEA80816 FM253 NC2_1.0 | 2010-10-26 | 2010-10-27 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.0034722 | Highland 1 | Wind turbine was faulted thru the night and on-call techs were told to leave down till morning because of weather. | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-02 | US-HIGHLAND-25WEA80829_Type 2 Maint. | 2010-10-26 | 2010-10-26 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.16875 | Forced | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0017 | 1,4,1 | 0.20903 | Highland 1 | Performed type 2 maintenance which includes generator slipring cleaning, hydraulic checks, gearbox offline filter change,gearbox ch | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-03 | US-HIGHLAND-25WEA80829_Type 2 Maint. | 2010-10-26 | 2010-10-26 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.1688 | Forced | KRAYN-NDX-PRT-0725,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0017 | 1,1,4,1 | 0.47917 | Highland 1 | Performed type 2 maintenance which includes generator slipring cleaning, hydraulic checks, gearbox offline filter change,gearbox ch | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-04 | Yaw convertor firmware update | 2010-10-26 | 2010-10-26 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.22917 | Forced |  |  | 0.083333 | Highland 1 | tool prep and travel | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-05 | WTG Manual Stop | 2010-10-26 | 2010-10-26 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 4 | Forced |  |  | 1.9667 | Highland 1 | turbine need a firmware update of the abb convertor | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-06 | WTG Manual Stop | 2010-10-26 | 2010-10-26 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 7.3333 | Planned |  |  | 2.9167 | Highland 1 | Nordex technicians replaced yaw motor brake fin with new retrofit. Unsure what previous SAP # was, but the SAP # on retrofit box = 33600. in operations hours = 10214. | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101026-07 | US-HIGHLAND-25WEA80829_Type 2 Maint. | 2010-10-26 | 2010-10-26 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 1.3563 | Forced | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0725 | 1,4,1,1 | 0.56389 | Highland 1 | Performed type 2 maintenance which includes generator slipring cleaning, hydraulic checks, gearbox offline filter change,gearbox ch | KRAYN-WKO-NDX-20101026 | 1
KRAYN-WKO-NDX-20101027-01 | 001 Highland 23WEA80815 FM1177 NC2_1.0 | 2010-10-27 | 2010-10-28 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.14028 | Forced |  |  | 0.17153 | Highland 1 | Pitch power failure | KRAYN-WKO-NDX-20101027 | 1
KRAYN-WKO-NDX-20101027-02 | 001 Highland 23WEA80815 FM415 NC2_1.0 | 2010-10-27 | 2010-10-27 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.4375 | Forced |  |  | 0.44375 | Highland 1 | Nordex techs along with WTS tech went up this faulted turbine to adjust the micro switch due to the FM414. Techs started by checkin | KRAYN-WKO-NDX-20101027 | 1
KRAYN-WKO-NDX-20101028-01 | StarLift hoist | 2010-10-28 | 2010-10-28 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.75972 | Forced |  |  | 0.17153 | Highland 1 | Morning of the 28th, Illig and Martin prepared to replace chain hoist bag (along with preparing to troubleshoot pitch power fault f | KRAYN-WKO-NDX-20101028 | 1
KRAYN-WKO-NDX-20101028-02 | FM 416 Yaw Invertor Fault WEA 80823 | 2010-10-28 | 2010-10-28 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.12986 | Highland 1 | Nordex technicians seen that the turbine was faulted and responded. | KRAYN-WKO-NDX-20101028 | 1
KRAYN-WKO-NDX-20101028-03 | WEA 19-80826 FM 1208 MI Class B | 2010-10-28 | 2010-10-28 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.18403 | Highland 1 | Wind turbine faulted during off duty hours and techs responded first thing in the morning. | KRAYN-WKO-NDX-20101028 | 1
KRAYN-WKO-NDX-20101029-01 | IBS Busquality Warning | 2010-10-29 | 2010-10-29 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned |  |  | 4.9333 | Highland 1 | Nordex technicians cleaned and lubricated the contacts of the hub slip ring. Also cleaned hub. Nordex technician Charles Henderson also present. Henderson also reconfigured the ABB converter and increased yaw brake pressure per Engineer Charles Stauffer. Prior to leaving, the turbine showed an FM 419 Yaw motor brake fault likely due to the change of ABB configuration. Techs had to return uptower to attend to that fault. No further faults noted, no further incidents. | KRAYN-WKO-NDX-20101029 | 1
KRAYN-WKO-NDX-20101105-01 | US-HIGHLAND-19WEA80826_Type 2 Maint. | 2010-11-05 | 2010-11-05 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.69861 | Forced |  |  | 0.35 | Highland 1 | change,bypass oil filter change, visual checks of the nacelle and electrical check of breakers | KRAYN-WKO-NDX-20101105 | 1
KRAYN-WKO-NDX-20101109-01 | Highland 16WEA80823 Yaw converter Data | 2010-11-09 | 2010-11-09 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.23194 | Forced |  |  | 0.091667 | Highland 1 | pulled and saved trigger files, e-mailed them to Stauffer, changed trigger files to Stauffer's specs | KRAYN-WKO-NDX-20101109 | 1
KRAYN-WKO-NDX-20101111-01 | US-HIGHLAND_18WEA80825_PunchList Items | 2010-11-11 | 2010-11-11 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20101111 | 1
KRAYN-WKO-NDX-20101111-02 | US-HIGHLAND_18WEA80825_PunchList Items | 2010-11-11 | 2010-11-11 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20101111 | 1
KRAYN-WKO-NDX-20101111-03 | Pitch2 DC.link Overcurrent | 2010-11-11 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 18 | Forced |  |  | 2.5833 | Highland 1 | Troubleshot Turbine for FE-1108 Pitch2 DC.link Overcurrent. No resolution will continue next opportunity. | KRAYN-WKO-NDX-20101111 | 1
KRAYN-WKO-NDX-20101112-01 | Highland 10WEA80817 Supression Diodes | 2010-11-12 | 2010-11-12 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.18542 | Forced |  |  | 0.17153 | Highland 1 | worked down tower durring this time | KRAYN-WKO-NDX-20101112 | 1
KRAYN-WKO-NDX-20101112-02 | Highland 10WEA80817 Supression Diodes | 2010-11-12 | 2010-11-12 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.18542 | Forced |  |  | 0.17153 | Highland 1 | shut down time of the turbine | KRAYN-WKO-NDX-20101112 | 1
KRAYN-WKO-NDX-20101112-03 | Highland 02WEA80809 Delayed Discrepancy | 2010-11-12 | 2010-11-12 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.19375 | Forced |  |  | 0.175 | Highland 1 | drove to the turbine | KRAYN-WKO-NDX-20101112 | 1
KRAYN-WKO-NDX-20101115-01 | WTG 25 wind speed unequal power | 2010-11-15 | 2010-11-15 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.13194 | Forced |  |  | 0.125 | Highland 1 | drive to turbine | KRAYN-WKO-NDX-20101115 | 1
KRAYN-WKO-NDX-20101115-02 | Highland 10WEA80817 wind measurement dev | 2010-11-15 | 2010-11-15 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.08125 | Forced |  |  | 0.060417 | Highland 1 | Check of the wind vane alignment and sonic.Also checked connections of the wind vane and sonic | KRAYN-WKO-NDX-20101115 | 1
KRAYN-WKO-NDX-20101116-01 | 001 Highland 05WEA80812 FM55 NC2_1.0 | 2010-11-16 | 2010-11-18 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 1.3833 | Forced |  |  | 0.23472 | Highland 1 | Beginning on the 16th, the MFR was discovered to be faulty. Component was changed. During machine restart procedure, it showed pi | KRAYN-WKO-NDX-20101116 | 1
KRAYN-WKO-NDX-20101117-01 | Highland WEA_24_80816_FM 1174_11-18-10 | 2010-11-17 | 2010-11-18 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.54167 | Forced |  |  | -0.022222 | Highland 1 | Windturbine faulted with a pitch problem the day prior and the wind was to high to lock out the hub. So the technicians reported to | KRAYN-WKO-NDX-20101117 | 1
KRAYN-WKO-NDX-20101117-02 | Highland 15WEA yaw motor brake not open | 2010-11-17 | 2010-11-17 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.086806 | Highland 1 | Nordex techs along with everpower tech went up the tower to troubleshoot a yaw brake fault. Techs then found out the micro switch o | KRAYN-WKO-NDX-20101117 | 1
KRAYN-WKO-NDX-20101117-03 | 001 Highland 16WEA80823 FM1208 | 2010-11-17 | 2010-11-17 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.3875 | Forced |  |  | 0.21389 | Highland 1 | this was parts prep and the drive time to the turbine | KRAYN-WKO-NDX-20101117 | 1
KRAYN-WKO-NDX-20101117-04 | Highland 16WEA80823 improve rpm signals | 2010-11-17 | 2010-11-17 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | -0.84861 | Highland 1 | parts prep and drive time to the turbine | KRAYN-WKO-NDX-20101117 | 1
KRAYN-WKO-NDX-20101118-01 | Highland WEA_10_80817 FM 1172_11-18-10 | 2010-11-18 | 2010-11-18 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.13958 | Highland 1 | Windturbine faulted for a pitch power volt problem. Nordex technicians reported to the turbine to troubleshoot. | KRAYN-WKO-NDX-20101118 | 1
KRAYN-WKO-NDX-20101119-01 | 001 Highland 10WEA80817 FM1177 NC2_1.0 | 2010-11-19 | 2010-11-19 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.43472 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.14306 | Highland 1 | interbus fault, slipring prototype added | KRAYN-WKO-NDX-20101119 | 1
KRAYN-WKO-NDX-20101122-01 | Turbine 18 FE 1141Fault | 2010-11-22 | 2010-11-22 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.80417 | Forced |  |  | 0.38681 | Highland 1 | travel to site | KRAYN-WKO-NDX-20101122 | 1
KRAYN-WKO-NDX-20101123-01 | US-HIGHLAND-20WEA80827_Type 2 Maint. | 2010-11-23 | 2010-11-23 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.83403 | Forced |  |  | 0.26181 | Highland 1 | travel to site | KRAYN-WKO-NDX-20101123 | 1
KRAYN-WKO-NDX-20101123-02 | Safety chain on WTG1 | 2010-11-23 | 2010-11-23 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.056944 | Highland 1 | Safety Chain due to RPMs | KRAYN-WKO-NDX-20101123 | 1
KRAYN-WKO-NDX-20101123-03 | Safety chain on WTG1 | 2010-11-23 | 2010-11-23 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.056944 | Highland 1 | Safety Chain due to RPMs | KRAYN-WKO-NDX-20101123 | 1
KRAYN-WKO-NDX-20101124-01 | US-HIGHLAND-17WEA80824_Type 2 Maint. | 2010-11-24 | 2010-11-24 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.54861 | Forced |  |  | 0.29514 | Highland 1 | traveling from troubleshooting on WTG 11 to WTG 17 for type II maint. | KRAYN-WKO-NDX-20101124 | 1
KRAYN-WKO-NDX-20101124-02 | Turbine 11 FM 50 Fault | 2010-11-24 | 2010-11-24 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.095139 | Highland 1 | Turbine had a safety chain fault. Nordex techs went up this tower to clean off the gen. rpm sensors. The safety chain fault was do | KRAYN-WKO-NDX-20101124 | 1
KRAYN-WKO-NDX-20101126-01 | Highland 16WEA80823 FM55 | 2010-11-26 | 2010-11-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1.2708 | Forced |  |  | 0.44097 | Highland 1 | travel from geistown to highland | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-02 | Highland 16WEA80823 FM55 | 2010-11-26 | 2010-11-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1.2708 | Forced |  |  | 0.44097 | Highland 1 | travel from geistown to highland | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-03 | Highland 16WEA80823 FM55 | 2010-11-26 | 2010-11-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.1042 | Forced |  |  | 0.87153 | Highland 1 | travel from geistown to highland | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-04 | Highland 16WEA80823 FM55 | 2010-11-26 | 2010-11-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.1042 | Forced |  |  | 0.87153 | Highland 1 | travel from geistown to highland | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-05 | 1 HIGHLAND 11WEA80818 RM2 | 2010-11-26 | 2010-11-26 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.5625 | Forced |  |  | 0.56736 | Highland 1 | The wind turbine never started but the original stop time is 05:53 and work stop time is 19:30. | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-06 | 1 HIGHLAND 11WEA80818 RM2 | 2010-11-26 | 2010-11-29 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1.5208 | Forced | KRAYN-NDX-PRT-0650 | 1 | 0.56736 | Highland 1 | The wind turbine faulted over the weekend and the nordex technicians troubleshot thru the weekend till the next week. | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101126-07 | 1 HIGHLAND 11WEA80818 RM2 | 2010-11-26 | 2010-11-26 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1.6917 | Forced |  |  | 0.57431 | Highland 1 | The wind turbine never started but the original stop time is 05:53 and work stop time is 19:30. | KRAYN-WKO-NDX-20101126 | 1
KRAYN-WKO-NDX-20101130-01 | Highland 24WEA80816 11-30-2010 safety | 2010-11-30 | 2010-11-30 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.029167 | Forced |  |  | 0.017361 | Highland 1 | safety chain fault d/t MI ext. hardware error | KRAYN-WKO-NDX-20101130 | 1
KRAYN-WKO-NDX-20101130-02 | Highland 10WEA80817 11-30-2010 | 2010-11-30 | 2010-11-30 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.069444 | Forced |  |  | 0.065972 | Highland 1 | safety chain dt GenRPM H stop | KRAYN-WKO-NDX-20101130 | 1
KRAYN-WKO-NDX-20101130-03 | US-HIGHLAND-14WEA80821_Type 2 Maint. | 2010-11-30 | 2010-11-30 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.57361 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0962,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0058 | 1,2,2,2 | 0.069444 | Highland 1 | travel from Geistown to Highland | KRAYN-WKO-NDX-20101130 | 1
KRAYN-WKO-NDX-20101130-04 | Highland 06WEA80813 11-30-2010 safety | 2010-11-30 | 2010-11-30 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.052778 | Forced |  |  | 0 | Highland 1 | downtime for the machine | KRAYN-WKO-NDX-20101130 | 1
KRAYN-WKO-NDX-20101202-01 | US-HIGHLAND-13WEA80820_Type 2 Maint. | 2010-12-02 | 2010-12-02 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.23611 | Forced | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0351 | 1,1,1,4 | 0.38542 | Highland 1 | Performed Type 2 maint. with a WTS tech | KRAYN-WKO-NDX-20101202 | 1
KRAYN-WKO-NDX-20101203-01 | US-HIGHLAND-11WEA80818_Type 2 Maint. | 2010-12-03 | 2010-12-03 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.13194 | Forced | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074 | 1,1 | 0.067361 | Highland 1 | Performed a type 2 maint. with WTS Tech | KRAYN-WKO-NDX-20101203 | 1
KRAYN-WKO-NDX-20101203-02 | US-HIGHLAND-11WEA80818_Type 2 Maint. | 2010-12-03 | 2010-12-03 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.29028 | Forced | KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0004 | 1,1,4,2 | 0.20278 | Highland 1 | Performed a type 2 maint. with WTS Tech | KRAYN-WKO-NDX-20101203 | 1
KRAYN-WKO-NDX-20101203-03 | US-HIGHLAND-12WEA80819_Type 2 Maint. | 2010-12-03 | 2010-12-03 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.31042 | Forced | KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0292 | 2,1,1,2,3,4,1,2 | 0.28958 | Highland 1 | machine was stopped for type II maintanence. | KRAYN-WKO-NDX-20101203 | 1
KRAYN-WKO-NDX-20101207-01 | Highland_25WEA80829_2010-12-7_FM 831 | 2010-12-07 | 2010-12-07 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.14236 | Forced | KRAYN-NDX-PRT-0327 | 1 | 0.11806 | Highland 1 | Nordex technician, accompanied by WTS contractor went uptower to changed mechanical thermostat under gearbox filter. | KRAYN-WKO-NDX-20101207 | 1
KRAYN-WKO-NDX-20101207-02 | Highland_25WEA80829_2010-12-7_FM 831 | 2010-12-07 | 2010-12-07 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.14236 | Forced | KRAYN-NDX-PRT-0327 | 1 | 0.11806 | Highland 1 | Nordex technician, accompanied by WTS contractor went uptower to changed mechanical thermostat under gearbox filter. | KRAYN-WKO-NDX-20101207 | 1
KRAYN-WKO-NDX-20101208-01 | Highland_16WEA80823_2010-12-8_FM 416 | 2010-12-08 | 2010-12-08 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.53125 | Highland 1 | FM416 | KRAYN-WKO-NDX-20101208 | 1
KRAYN-WKO-NDX-20101213-01 | Highland_23WEA80815_FM1213 | 2010-12-13 | 2010-12-13 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.0875 | Forced |  |  | 0.022917 | Highland 1 | FM1213 | KRAYN-WKO-NDX-20101213 | 1
KRAYN-WKO-NDX-20101213-02 | Highland_23WEA80815_FM1213 | 2010-12-13 | 2010-12-13 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.0875 | Forced |  |  | 0.022917 | Highland 1 | FM1213 | KRAYN-WKO-NDX-20101213 | 1
KRAYN-WKO-NDX-20101213-03 | Highland_16WEA80823_2010-12-20_FM55 | 2010-12-13 | 2010-12-13 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.055556 | Forced |  |  | 0.0069444 | Highland 1 | FM55 | KRAYN-WKO-NDX-20101213 | 1
KRAYN-WKO-NDX-20101213-04 | Highland_18WEA80825_FM1153_12-13-10 RJW | 2010-12-13 | 2010-12-15 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.5 | Forced | KRAYN-NDX-PRT-0558 | 1 | 0.275 | Highland 1 | The wind turbine faulted on 12-13-10 and on 12-15-10 Nordex techs troubleshot the pitch issue. | KRAYN-WKO-NDX-20101213 | 1
KRAYN-WKO-NDX-20101213-05 | Highland 13WEA80820 FM 1153 | 2010-12-13 | 2010-12-13 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.30556 | Forced |  |  | 0.20833 | Highland 1 | FM 1172 | KRAYN-WKO-NDX-20101213 | 1
KRAYN-WKO-NDX-20101215-01 | FM700 | 2010-12-15 | 2010-12-15 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.05625 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.74653 | Highland 1 | Changed out bad slip ring | KRAYN-WKO-NDX-20101215 | 1
KRAYN-WKO-NDX-20101215-02 | FM700 | 2010-12-15 | 2010-12-15 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.05625 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.74653 | Highland 1 | Changed out bad slip ring | KRAYN-WKO-NDX-20101215 | 1
KRAYN-WKO-NDX-20101216-01 | HIGHLAND_22WEA80830_FM124_Oil Filter | 2010-12-16 | 2010-12-16 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.097222 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.040972 | Highland 1 | Nordex technicians stopped the wind turbine to change the gearbox oil filter because of the FM 124 warning. | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-02 | HIGHLAND_20WEA80827_FM831_Oil Temp | 2010-12-16 | 2010-12-16 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.10417 | Forced | KRAYN-NDX-PRT-0579 | 1 | 0.036806 | Highland 1 | Nordex technicians stopped the wind turbine to change valve on the gearbox because of the oil temp warning of the gear oil. | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-03 | HIGHLAND_21WEA80828_FM831_Oil Temp | 2010-12-16 | 2010-12-16 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.15972 | Forced | KRAYN-NDX-PRT-0579 | 1 | 0.09375 | Highland 1 | Nordex technicians traveled to the wind turbine to change gearbox thermal by-pass valve because of the high temp warning of the gea | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-04 | Highland_01WEA80808_FM744 | 2010-12-16 | 2010-12-16 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.14236 | Highland 1 | Stopped Turbine to adjust an ice sensor and to clean the slip ring. | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-05 | Highland_01WEA80808_FM744 | 2010-12-16 | 2010-12-16 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.14236 | Highland 1 | Stopped Turbine to adjust an ice sensor and to clean the slip ring. | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-06 | Highland_02WEA80809_FM420 | 2010-12-16 | 2010-12-16 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.072917 | Forced | KRAYN-NDX-PRT-0107 | 1 | 0.072917 | Highland 1 | Displaying yaw hydraulic brake fault. | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-07 | FM744 | 2010-12-16 | 2010-12-16 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.11458 | Forced |  |  | 0.097917 | Highland 1 | Cleaned the new prototype slipring | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101216-08 | FM744 | 2010-12-16 | 2010-12-16 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.11458 | Forced |  |  | 0.097917 | Highland 1 | Cleaned the new prototype slipring | KRAYN-WKO-NDX-20101216 | 1
KRAYN-WKO-NDX-20101217-01 | Highland_18WEA80825_2010-12-20_FM172 | 2010-12-17 | 2010-12-17 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.020833 | Highland 1 | Machine had been displaying an FM172 for several days. Breaker reset. no further incidents of this nature. | KRAYN-WKO-NDX-20101217 | 1
KRAYN-WKO-NDX-20101217-02 | Highland_04WEA80811_FM168 | 2010-12-17 | 2010-12-17 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.11111 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.13194 | Highland 1 | machine had been showing FM 168 for several days. Technicians changed gear box oil filter. During task, machine H stopped for Rot | KRAYN-WKO-NDX-20101217 | 1
KRAYN-WKO-NDX-20101220-01 | US-HIGHLAND-10WEA80817_Type 2 Maint. | 2010-12-20 | 2010-12-20 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.54861 | Forced | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0062 | 1,1,2,2,2,14,2,2,1 | 0.3125 | Highland 1 | Day 1 of type II | KRAYN-WKO-NDX-20101220 | 1
KRAYN-WKO-NDX-20101220-02 | US-HIGHLAND-10WEA80817_Type 2 Maint. | 2010-12-20 | 2010-12-20 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.67361 | Forced | KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0074,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0062 | 1,1,2,2,2,14,2,2,1 | 0.45833 | Highland 1 | Day 1 of type II | KRAYN-WKO-NDX-20101220 | 1
KRAYN-WKO-NDX-20101221-01 | US-HIGHLAND-15WEA80822_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0 | Highland 1 | replace zarges roller on lift | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-02 | US-HIGHLAND-16WEA80823_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0 | Highland 1 | Replace zarges lift roller | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-03 | US-HIGHLAND-17WEA80824_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.0625 | Highland 1 | chage roller on zarges lift | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-04 | Highland_10WEA80817_FM 501, 503 | 2010-12-21 | 2010-12-21 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0030 | 1 | 0.22917 | Highland 1 | Changed wind vane. | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-05 | Highland_10WEA80817_FM 501, 503 | 2010-12-21 | 2010-12-21 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0030 | 1 | 0.22917 | Highland 1 | Changed wind vane. | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-06 | US_Highland_10WEA80817_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-07 | US_Highland_11WEA80818_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0 | Highland 1 | Replace trolley zarges lift | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-08 | US_Highland_12WEA80819_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0.03125 | Highland 1 | Zardes lift roller | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-09 | US-HIGHLAND-13WEA80820_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0 | Highland 1 | Replace zarges roller on lift | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101221-10 | US_Highland_14WEA80821_Zarges Rollers | 2010-12-21 | 2010-12-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0 | Highland 1 | replace zarges roller | KRAYN-WKO-NDX-20101221 | 1
KRAYN-WKO-NDX-20101222-01 | FM744 | 2010-12-22 | 2010-12-22 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.11111 | Forced |  |  | 0.045833 | Highland 1 | Cleaned and lube the slip ring due to a FM 744 | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101222-02 | FM744 | 2010-12-22 | 2010-12-22 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.11111 | Forced |  |  | 0.045833 | Highland 1 | Cleaned and lube the slip ring due to a FM 744 | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101222-03 | Yaw motor retrofit | 2010-12-22 | 2010-12-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.45833 | Forced | KRAYN-NDX-PRT-0782 | 2 | 0.29167 | Highland 1 | downtime, including applying the retrofits. | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101222-04 | US_Highland_Fan Wheel Retro | 2010-12-22 | 2010-12-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.625 | Forced | KRAYN-NDX-PRT-0959 | 1 | 0.083333 | Highland 1 | machine downtime for retrofit | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101222-05 | Yaw motor retrofit | 2010-12-22 | 2010-12-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.45833 | Forced | KRAYN-NDX-PRT-0782 | 2 | 0.29167 | Highland 1 | downtime, including applying the retrofits. | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101222-06 | US_Highland_Fan Wheel Retro | 2010-12-22 | 2010-12-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.625 | Forced | KRAYN-NDX-PRT-0959 | 1 | 0.083333 | Highland 1 | machine downtime for retrofit | KRAYN-WKO-NDX-20101222 | 1
KRAYN-WKO-NDX-20101230-01 | Highland 17WEA80824 FM348 | 2010-12-30 | 2010-12-30 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.15625 | Forced | KRAYN-NDX-PRT-0187 | 1 | 0.03125 | Highland 1 | stopped for troubleshooting. | KRAYN-WKO-NDX-20101230 | 1
KRAYN-WKO-NDX-20110103-01 | LVS UPS Battery Change | 2011-01-03 | 2011-01-03 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.0625 | Highland 1 | Did a battery reset on the UPS | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-02 | LV UPS battery change | 2011-01-03 | 2011-01-03 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.0625 | Forced | KRAYN-NDX-PRT-0298 | 2 | 0.022917 | Highland 1 | LV UPS Battery change fault. Replaced two bad batteries with two we had in stock. | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-03 | LV UPS battery change | 2011-01-03 | 2011-01-03 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.0625 | Forced | KRAYN-NDX-PRT-0298 | 2 | 0.022917 | Highland 1 | LV UPS Battery change fault. Replaced two bad batteries with two we had in stock. | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-04 | LV UPS battery change | 2011-01-03 | 2011-01-03 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.0625 | Forced | KRAYN-NDX-PRT-0298 | 2 | 0.022917 | Highland 1 | LV UPS Battery change fault. Replaced two bad batteries with two we had in stock. | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-05 | Highland 03WEA80810 FM124 | 2011-01-03 | 2011-01-03 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.1875 | Forced | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0364 | 1,1 | 0.072917 | Highland 1 | changed main gear filter. filled yaw ALU. | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-06 | Highland 04WEA80811 FM 744 Clean hub S R | 2011-01-03 | 2011-01-03 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.14583 | Highland 1 | Stopped for this reason, along with the Zarges cable guide retrofit (different SR). | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110103-07 | US_Highland_04WEA80811_ Zarges Rollers | 2011-01-03 | 2011-01-03 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.27083 | Forced |  |  | 0.11458 | Highland 1 | Along with slip ring cleaning (different SR). | KRAYN-WKO-NDX-20110103 | 1
KRAYN-WKO-NDX-20110104-01 | 001 Highland 24WEA80816 FM419 NC2_1.0 | 2011-01-04 | 2011-01-05 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.052778 | Forced |  |  | -0.17847 | Highland 1 | Nordex techs took triggers and then starting troubleshooting till SEG got back to them with what the issue could be. After trouble | KRAYN-WKO-NDX-20110104 | 1
KRAYN-WKO-NDX-20110104-02 | #N/A | 2011-01-04 | 2012-01-04 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 1.3833 | Highland 1 | Drove to WTG8. Manually stopped turbine. Opened bottom box (Nordex Side) dissconected 230V heating supply, wire W120, terminal X1, 230V interbus supply, wire W121, terminal X,. Interbus bus connection to remote bus interface IN at module 23.0 wire W122 and Fiberoptic's. Removed deck plate to access basement. Pulled wires W120, W121 & W122 out of bottom box, through the basement and back up under Measurement Interface (Messbox). Ziptied Wires to (Messbox) and loaded it in the truck. Restarted WTG8. | KRAYN-WKO-NDX-20110104 | 1
KRAYN-WKO-NDX-20110105-01 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-05 | 2011-01-05 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.29167 | Forced |  |  | 0.16667 | Highland 1 | Haller and Martin went uptower to perform a slip ring inspection. Examined slip rings, brushes; measured runout using dial microme | KRAYN-WKO-NDX-20110105 | 1
KRAYN-WKO-NDX-20110105-02 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-05 | 2011-01-05 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.71875 | Forced |  |  | 0.19792 | Highland 1 | Replace earthing ring and troubleshoot broken sensor by contractor | KRAYN-WKO-NDX-20110105 | 1
KRAYN-WKO-NDX-20110105-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-05 | 2011-01-05 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.41667 | Forced |  |  | 0.15625 | Highland 1 | Replace earthing ring and troubleshoot broken sensor by contractor | KRAYN-WKO-NDX-20110105 | 1
KRAYN-WKO-NDX-20110106-01 | US_High1_02WEA80809_FM168 | 2011-01-06 | 2011-01-06 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.10417 | Highland 1 | machine down for slip ring inspection; cable guide change; and gear oil filter change. | KRAYN-WKO-NDX-20110106 | 1
KRAYN-WKO-NDX-20110106-02 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-06 | 2011-01-06 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.10417 | Highland 1 | turbine down for slip ring inspection, gear oil filter change, zarges cable guide retrofit | KRAYN-WKO-NDX-20110106 | 1
KRAYN-WKO-NDX-20110106-03 | US_Highland_02WEA80809_ Zarges Rollers | 2011-01-06 | 2011-01-06 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110106 | 1
KRAYN-WKO-NDX-20110107-01 | US_Highland 12WEA80819_HUR Board | 2011-01-07 | 2011-01-07 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.052778 | Forced |  |  | 0.22569 | Highland 1 | HUR board will not commission due bad HUR board | KRAYN-WKO-NDX-20110107 | 1
KRAYN-WKO-NDX-20110107-02 | US_Highland 12WEA80819_HUR Board | 2011-01-07 | 2011-01-07 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.088889 | Forced |  |  | 0.41319 | Highland 1 | HUR board will not commission due bad HUR board | KRAYN-WKO-NDX-20110107 | 1
KRAYN-WKO-NDX-20110107-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-07 | 2011-01-07 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.10417 | Highland 1 | performed inspection of generator slip ring. | KRAYN-WKO-NDX-20110107 | 1
KRAYN-WKO-NDX-20110107-04 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-07 | 2011-01-07 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.26389 | Forced |  |  | 0 | Highland 1 | turbine stopped for this time. | KRAYN-WKO-NDX-20110107 | 1
KRAYN-WKO-NDX-20110109-01 | #N/A | 2011-01-09 | 2012-01-09 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 5.15 | Highland 1 | In side each blade root locate and document each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. Damaged blade seals were documented and photographed. | KRAYN-WKO-NDX-20110109 | 1
KRAYN-WKO-NDX-20110110-01 | US_Highland_24WEA80816_FM 172 | 2011-01-10 | 2011-01-10 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.070833 | Forced |  |  | 0.09375 | Highland 1 | WTG 24 had a FM172 do to the by pass pump breaker beaing tripped | KRAYN-WKO-NDX-20110110 | 1
KRAYN-WKO-NDX-20110110-02 | US_Highland_13WEA80820_FM 420 | 2011-01-10 | 2011-01-10 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.065972 | Forced | KRAYN-NDX-PRT-0280 | 1 | 0.024306 | Highland 1 | drove from Geistown to Highland | KRAYN-WKO-NDX-20110110 | 1
KRAYN-WKO-NDX-20110111-01 | US_Highland_24WEA80816_Zarges Rollers | 2011-01-11 | 2011-01-11 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Drove from WTG 25 to 24 | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-02 | US-HIGHLAND_25WEA80829_PunchList Items | 2011-01-11 | 2011-01-11 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-03 | US_Highland_25WEA80829_Zarges Rollers | 2011-01-11 | 2011-01-11 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-04 | US-HIGHLAND_20WEA80827_PunchList Items | 2011-01-11 | 2011-01-11 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-05 | US_Highland_20WEA80827_Zarges Rollers | 2011-01-11 | 2011-01-11 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-06 | US-HIGHLAND_21WEA80828_PunchList Items | 2011-01-11 | 2011-01-11 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0 | Forced |  |  | 0.041667 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110111-07 | US_Highland_21WEA80828_Zarges Rollers | 2011-01-11 | 2011-01-11 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110111 | 1
KRAYN-WKO-NDX-20110112-01 | 001 Highland 02WEA80809 FM1208 NC2_1.0 | 2011-01-12 | 2011-01-12 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.09375 | Highland 1 | drove from Geistown to Highland; inclimate weather. | KRAYN-WKO-NDX-20110112 | 1
KRAYN-WKO-NDX-20110113-01 | 001 Highland 22WEA80830 FM1208 NC2_1.0 | 2011-01-13 | 2011-01-13 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.12361 | Highland 1 | Turbine 22 went down on a MI Class B fault. Nordex techs went to the turbine to find that the hur lost its programming. Techs then | KRAYN-WKO-NDX-20110113 | 1
KRAYN-WKO-NDX-20110114-01 | MI Class B fault | 2011-01-14 | 2011-01-14 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.175 | Forced |  |  | 0.13472 | Highland 1 | Nordex tech responded to a FM 1208. The techs then proceeded to check the encoder on the MI rpm sensor. Then recommissioned the HUR | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110114-02 | US_Highland_22WEA80830_Zarges Rollers | 2011-01-14 | 2011-01-14 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.020833 | Highland 1 | Performed a Zarges retro | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110114-03 | Highland_16WEA80823_2011-01-14_oil add | 2011-01-14 | 2011-01-14 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.083333 | Highland 1 | Drive from Geistown to Highland. | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110114-04 | Highland_05WEA80812_2011-01-14_FM744 | 2011-01-14 | 2011-01-14 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.1875 | Forced |  |  | 0.083333 | Highland 1 | drove from Geistown to Highland | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110114-05 | Highland_05WEA80812_1-14-2011_gear_sens | 2011-01-14 | 2011-01-14 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.27083 | Forced | KRAYN-NDX-PRT-0560 | 1 | 0.083333 | Highland 1 | drove from Geistown to Highland | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110114-06 | US_Highland_05WEA80812_ Zarges Rollers | 2011-01-14 | 2011-01-14 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110114 | 1
KRAYN-WKO-NDX-20110117-01 | oil filter change, ups battery change | 2011-01-17 | 2011-01-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.1875 | Forced | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0298 | 1,4 | 0.020833 | Highland 1 | preped materials and travled to site for work to be completed | KRAYN-WKO-NDX-20110117 | 1
KRAYN-WKO-NDX-20110117-02 | oil filter change, ups battery change | 2011-01-17 | 2011-01-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.1875 | Forced | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0298 | 1,4 | 0.020833 | Highland 1 | preped materials and travled to site for work to be completed | KRAYN-WKO-NDX-20110117 | 1
KRAYN-WKO-NDX-20110118-01 | US-HIGHLAND_02WEA80809_PunchList Items | 2011-01-18 | 2011-01-18 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.14583 | Highland 1 | turbine stopped for punchlist hub painting and zarges cable protection retro. | KRAYN-WKO-NDX-20110118 | 1
KRAYN-WKO-NDX-20110118-02 | US-HIGHLAND-02WEA80809_ZargesLoopProtect | 2011-01-18 | 2011-01-18 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.30556 | Forced |  |  | 0.14514 | Highland 1 | Performed a new zarges cable protection retro fit | KRAYN-WKO-NDX-20110118 | 1
KRAYN-WKO-NDX-20110119-01 | FM50 / SafetyChain Activated | 2011-01-19 | 2012-01-20 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 10 | Forced |  |  | 14.0667 | Highland 1 | On call, checked NC2 for faults and focused our attention on the safety chain fault. Troubleshoot the top box for 230v, 24v and tripped fuses. Found no 24v with emegency stop at X21 pin 01. In the bottom box troubleshoot 24v safety chain line. Called Kelly Miller for additional help. At 23:45 called it a night due to weather and fatigue. Returned to turbine next morning with Sean illig continued to troubleshoot 24v line. Found Q10 needed to be reset, reset Q10, safety chain and reset turbine.Tried to take a trigger file but found HUR file card needed to be reformated. | KRAYN-WKO-NDX-20110119 | 1
KRAYN-WKO-NDX-20110122-01 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.6271 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 1.4306 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110122-02 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.8771 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 1.6771 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110122-03 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 10.5854 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 1.9271 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110122-04 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 11.9604 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 2.3854 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110122-05 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 11.9604 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 2.3854 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110122-06 | US_5_Gearbox damage. Metal shavings and | 2011-01-22 | 2011-01-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 14.0229 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1,1,1 | 1.9271 | Highland 1 | germany and us confrence calls preparing set up of works performed | KRAYN-WKO-NDX-20110122 | 1
KRAYN-WKO-NDX-20110124-01 | turbine faulted for pitch one blade stuc | 2011-01-24 | 2011-01-24 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.69444 | Forced |  |  | 0.10625 | Highland 1 | prepared a pitch convertor for turbine and traveled to WTG | KRAYN-WKO-NDX-20110124 | 1
KRAYN-WKO-NDX-20110124-02 | 001 Highland 04WEA80811 FM1208 NC2_1.0 | 2011-01-24 | 2011-01-24 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.020833 | Highland 1 | Troubleshooting conducted; all contactors appeared to be working appropriately. Turbine restarted. No further incidents. | KRAYN-WKO-NDX-20110124 | 1
KRAYN-WKO-NDX-20110125-02 | US_Highland_07WEA80814_Zarges Rollers | 2011-01-25 | 2011-01-25 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.16042 | Highland 1 | Perfromed a retro on the zarges rollers for the lift. Then did punchlist items this is why the turbine was down for awhile | KRAYN-WKO-NDX-20110125 | 1
KRAYN-WKO-NDX-20110125-09 | US-HIGHLAND_07WEA80814_PunchList Items | 2011-01-25 | 2011-01-25 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.36111 | Forced |  |  | 0.20139 | Highland 1 | drove from Geistown to Highland | KRAYN-WKO-NDX-20110125 | 1
KRAYN-WKO-NDX-20110126-01 | US_5_24WEA80816_2011-01-26_FM55 | 2011-01-26 | 2011-01-26 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 1.7083 | Forced |  |  | 0.79167 | Highland 1 | Initiated troubleshooting by addressing the potential for an MI problem, due to the LV Main Switch fault. Attempted restart & disc | KRAYN-WKO-NDX-20110126 | 1
KRAYN-WKO-NDX-20110127-01 | Highland_16WEA80823_2011-01-27_FM165 | 2011-01-27 | 2011-01-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.20833 | Forced |  |  | 0.125 | Highland 1 | stopped turbine to correct FM 165 | KRAYN-WKO-NDX-20110127 | 1
KRAYN-WKO-NDX-20110128-01 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-28 | 2011-01-28 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.22917 | Forced |  |  | 0.11458 | Highland 1 | Nordex technicians initiated generator slip ring inspection | KRAYN-WKO-NDX-20110128 | 1
KRAYN-WKO-NDX-20110128-02 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-28 | 2011-01-28 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.38194 | Forced |  |  | 0.19792 | Highland 1 | Nordex technicians initiated generator slip ring inspection | KRAYN-WKO-NDX-20110128 | 1
KRAYN-WKO-NDX-20110128-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-28 | 2011-01-28 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.25694 | Forced |  |  | 0.10764 | Highland 1 | Performing the gen slip ring inspection for Nordex Engineers for warranty | KRAYN-WKO-NDX-20110128 | 1
KRAYN-WKO-NDX-20110128-04 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-28 | 2011-01-28 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.1875 | Forced |  |  | 0.072917 | Highland 1 | Part I of generator slip ring warranty inspection for Nordex Engineers | KRAYN-WKO-NDX-20110128 | 1
KRAYN-WKO-NDX-20110128-05 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-28 | 2011-01-28 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.4375 | Forced |  |  | 0.11111 | Highland 1 | Part I of generator slip ring warranty inspection for Nordex Engineers | KRAYN-WKO-NDX-20110128 | 1
KRAYN-WKO-NDX-20110131-01 | US_5_25WEA80829_ice sensor | 2011-01-31 | 2011-01-31 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.10903 | Forced | KRAYN-NDX-PRT-0871 | 1 | 0.088889 | Highland 1 | Changed out the ice sensor from square to oval. Then programmed it | KRAYN-WKO-NDX-20110131 | 1
KRAYN-WKO-NDX-20110131-02 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-31 | 2011-01-31 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.18056 | Forced |  |  | 0.0625 | Highland 1 | Conducted slip ring inspection for Nordex engineering for purpose of generator warranty | KRAYN-WKO-NDX-20110131 | 1
KRAYN-WKO-NDX-20110131-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-01-31 | 2011-01-31 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.15278 | Forced |  |  | 0.097222 | Highland 1 | Conducted the gen slip ring warranty inspection for nordex engineers. | KRAYN-WKO-NDX-20110131 | 1
KRAYN-WKO-NDX-20110202-01 | Highland_16WEA80823_2011-02-02_FM55 | 2011-02-02 | 2011-02-02 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.38542 | Forced |  |  | 0.10764 | Highland 1 | FM55 | KRAYN-WKO-NDX-20110202 | 1
KRAYN-WKO-NDX-20110202-02 | Highland_18WEA80825_2011-02-02_FM104 | 2011-02-02 | 2011-02-02 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.020833 | Highland 1 | FM104 | KRAYN-WKO-NDX-20110202 | 1
KRAYN-WKO-NDX-20110203-01 | Highland_22WEA80830_2011-2-3_hubslipring | 2011-02-03 | 2011-02-03 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.91667 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.3125 | Highland 1 | replace old slip ring | KRAYN-WKO-NDX-20110203 | 1
KRAYN-WKO-NDX-20110203-02 | 001 Highland 17WEA80824 FM55 | 2011-02-03 | 2011-02-03 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.017361 | Highland 1 | Gen RPM H stop was troubleshot downtower. Techs considered possible malfunctions and, given the circumstances, opted to restart do | KRAYN-WKO-NDX-20110203 | 1
KRAYN-WKO-NDX-20110203-03 | Highland_18WEA80825_2011-02-02_FM1146 | 2011-02-03 | 2011-02-03 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.14306 | Forced |  |  | 0.050694 | Highland 1 | Pitch limit switch stuck | KRAYN-WKO-NDX-20110203 | 1
KRAYN-WKO-NDX-20110203-04 | US_5_01WEA80808_FM104 | 2011-02-03 | 2011-02-03 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.020833 | Highland 1 | Examined fast logs, considered potential problems. Decided to restart the turbine. No further problems of this nature, will conti | KRAYN-WKO-NDX-20110203 | 1
KRAYN-WKO-NDX-20110204-01 | US-HIGHLAND-WEA80830 | 2011-02-04 | 2011-02-04 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 2.1667 | Forced |  |  | 0.5625 | Highland 1 | During travel time, material was acquired and prepared. | KRAYN-WKO-NDX-20110204 | 1
KRAYN-WKO-NDX-20110207-01 | US_Highland_09WEA80832_Zarges Rollers | 2011-02-07 | 2011-02-07 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110207 | 1
KRAYN-WKO-NDX-20110207-02 | Highland_06WEA80813_2011-02-07_yaw hyd | 2011-02-07 | 2011-02-07 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.72917 | Forced | KRAYN-NDX-PRT-0280 | 1 | 0.26042 | Highland 1 | Nordex technicians replaced contactor 124K1, removed valve 181A4, observed solenoid / spindle operation to be functional. Observed | KRAYN-WKO-NDX-20110207 | 1
KRAYN-WKO-NDX-20110207-03 | US_Highland_06WEA80813_Zarges Rollers | 2011-02-07 | 2011-02-07 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110207 | 1
KRAYN-WKO-NDX-20110208-01 | Highland_06WEA80813_2-8-2011_yaw_hyd | 2011-02-08 | 2011-02-08 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.15556 | Forced |  |  | 0.056944 | Highland 1 | Day 2 of attempt to correct the yaw hydraulic brake fault. Technicians replaced the bleader valve, the solenoid valve, and checked | KRAYN-WKO-NDX-20110208 | 1
KRAYN-WKO-NDX-20110210-01 | US_Highland_23WEA80815_Zarges Rollers | 2011-02-10 | 2011-02-10 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110210 | 1
KRAYN-WKO-NDX-20110210-02 | US-HIGHLAND-18WEA80825_Zarges Rollers | 2011-02-10 | 2011-02-10 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110210 | 1
KRAYN-WKO-NDX-20110210-03 | US_Highland_19WEA80826_Zarges Rollers | 2011-02-10 | 2011-02-10 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110210 | 1
KRAYN-WKO-NDX-20110210-04 | US_5_01WEA80808_2011-02-14_Lift cbl rep | 2011-02-10 | 2011-02-10 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.41389 | Forced |  |  | 0.0625 | Highland 1 | preped drove to the turbine, stopped by everpowers for an availability meeting | KRAYN-WKO-NDX-20110210 | 1
KRAYN-WKO-NDX-20110210-05 | US_5_01WEA80808_2011-02-14_Lift cbl rep | 2011-02-10 | 2011-02-10 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.41389 | Forced |  |  | 0.0625 | Highland 1 | preped drove to the turbine, stopped by everpowers for an availability meeting | KRAYN-WKO-NDX-20110210 | 1
KRAYN-WKO-NDX-20110211-01 | US-HIGHLAND-WEA80811_2011-02-14_Replace | 2011-02-11 | 2011-02-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.29167 | Forced |  |  | 0.083333 | Highland 1 | Replaced Zarges lift cable | KRAYN-WKO-NDX-20110211 | 1
KRAYN-WKO-NDX-20110214-01 | Highland_02WEA80809_2011-02-14_FM105 | 2011-02-14 | 2011-02-14 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.33333 | Forced | KRAYN-NDX-PRT-0883 | 2 | 0.10764 | Highland 1 | Parts assembly and preparation for an FM 105 | KRAYN-WKO-NDX-20110214 | 1
KRAYN-WKO-NDX-20110215-01 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-15 | 2011-02-15 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.22917 | Forced |  |  | 0.072917 | Highland 1 | Nordex technicians completed first part of a Gen slip ring inspection. Will return to complete due to a change in required informa | KRAYN-WKO-NDX-20110215 | 1
KRAYN-WKO-NDX-20110215-02 | 001 Highland 24WEA80816 FM1208 NC2_1.0 | 2011-02-15 | 2011-02-15 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 0.16181 | Highland 1 | Nordex techs changed out the Q10 breaker as to SEG's request. | KRAYN-WKO-NDX-20110215 | 1
KRAYN-WKO-NDX-20110215-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-15 | 2011-02-15 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.17361 | Forced |  |  | 0.086806 | Highland 1 | nordex technicians performed a gen. slip ring inspection | KRAYN-WKO-NDX-20110215 | 1
KRAYN-WKO-NDX-20110216-01 | US_5_Gearbox damage. Metal shavings and | 2011-02-16 | 2011-02-16 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.44028 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325 | 1,1 | 0.22014 | Highland 1 | Nordex techs went up tower 22 to change out the gear box filter and gear box by-pass filter. Techs then noticed metal shavings in t | KRAYN-WKO-NDX-20110216 | 1
KRAYN-WKO-NDX-20110216-02 | US_5_Gearbox damage. Metal shavings and | 2011-02-16 | 2011-03-02 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.91667 | Forced |  |  | 0.28472 | Highland 1 | Nordex technicians ascended tower, pulled hoses uptower, drained gearbox, refilled gearbox with flushing solution (allowing it to s | KRAYN-WKO-NDX-20110216 | 1
KRAYN-WKO-NDX-20110216-03 | US_5_Gearbox damage. Metal shavings and | 2011-02-16 | 2011-03-02 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0616,KRAYN-NDX-PRT-0325 | 1,1 | 0.80556 | Highland 1 | Nordex technicians ascended tower, pulled hoses uptower, drained gearbox, refilled gearbox with flushing solution (allowing it to s | KRAYN-WKO-NDX-20110216 | 1
KRAYN-WKO-NDX-20110218-01 | Highland_14WEA80821_2011-02-18_FM 414 | 2011-02-18 | 2011-02-18 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.36389 | Forced |  |  | 0.16667 | Highland 1 | WTG 14 had a FM 414 yaw motor brake not open. Nordex techs went up tower to adjust the micrologics switch on the yaw motor | KRAYN-WKO-NDX-20110218 | 1
KRAYN-WKO-NDX-20110220-01 | Highland_14WEA80821_FM1172 | 2011-02-20 | 2011-02-20 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.3125 | Forced | KRAYN-NDX-PRT-0725 | 0 | 0.11181 | Highland 1 | WTG 14 has a slipring that has gone bad in it. Nordex techs went up tower to replace slipring. | KRAYN-WKO-NDX-20110220 | 1
KRAYN-WKO-NDX-20110221-01 | Highland_23WEA80815_2011-02-21_FM168 | 2011-02-21 | 2011-02-21 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.15278 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.034722 | Highland 1 | Changed the main gearbox oil filter. | KRAYN-WKO-NDX-20110221 | 1
KRAYN-WKO-NDX-20110221-02 | Highland_11WEA80818_2011-02-21_FM168 | 2011-02-21 | 2011-02-21 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.15278 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.041667 | Highland 1 | replace gear oil filter | KRAYN-WKO-NDX-20110221 | 1
KRAYN-WKO-NDX-20110221-03 | Highland_14WEA80821_2011-02-21_FM168 | 2011-02-21 | 2011-02-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.097222 | Forced |  |  | 0.041667 | Highland 1 | replace gear oil filter | KRAYN-WKO-NDX-20110221 | 1
KRAYN-WKO-NDX-20110222-01 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-22 | 2011-02-22 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.45833 | Forced |  |  | 0.097222 | Highland 1 | Nordex Technicians performed the gen slip ring warranty inspection and also confirmed the generator allignment. | KRAYN-WKO-NDX-20110222 | 1
KRAYN-WKO-NDX-20110223-01 | ZHigh1_06WEA80813_2011-02-24_FM168 | 2011-02-23 | 2011-02-23 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.081944 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.034028 | Highland 1 | Changed out the filter for the gear box oil | KRAYN-WKO-NDX-20110223 | 1
KRAYN-WKO-NDX-20110223-02 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-23 | 2011-02-25 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.034028 | Highland 1 | Inspected the Gen slipring for engineers | KRAYN-WKO-NDX-20110223 | 1
KRAYN-WKO-NDX-20110224-01 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-24 | 2011-02-24 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.6875 | Forced |  |  | 0.17708 | Highland 1 | slip ring inspection | KRAYN-WKO-NDX-20110224 | 1
KRAYN-WKO-NDX-20110224-02 | Highland_07WEA80814_FM 168 | 2011-02-24 | 2011-02-24 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.15972 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.047222 | Highland 1 | Replaced the Gear box filter due to a FM 168 | KRAYN-WKO-NDX-20110224 | 1
KRAYN-WKO-NDX-20110224-03 | Exten. Wear Gen.Gr Slip Ring Assemb | 2011-02-24 | 2011-02-24 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.31944 | Forced |  |  | 0.048611 | Highland 1 | Nordex technicians inspected generator slip ring for warranty. | KRAYN-WKO-NDX-20110224 | 1
KRAYN-WKO-NDX-20110227-01 | Highland_17WEA80824_2011-2-27_FM50 | 2011-02-27 | 2011-02-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.33333 | Highland 1 | FM 50 | KRAYN-WKO-NDX-20110227 | 1
KRAYN-WKO-NDX-20110303-01 | Highland_01WEA80808_2011-3-3_slipring | 2011-03-03 | 2011-03-03 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.28472 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.14236 | Highland 1 | Nordex Technicians attended turbine 1 to troubleshoot a pitch power fault. Attempted uptower reset. Unsuccessful. Brought up a n | KRAYN-WKO-NDX-20110303 | 1
KRAYN-WKO-NDX-20110303-02 | Highland_03WEA80810_2011-03-03_FM 419 | 2011-03-03 | 2011-03-03 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.34444 | Forced |  |  | 0.12917 | Highland 1 | FM 419 was the fault the Nordex techs went up tower to investigate. Which was just a solenoid stuck. it was accuated from the yaw c | KRAYN-WKO-NDX-20110303 | 1
KRAYN-WKO-NDX-20110303-03 | Highland_05WEA80812_2011-3-3_icesensor | 2011-03-03 | 2011-03-03 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.125 | Forced | KRAYN-NDX-PRT-0871 | 1 | 0.041667 | Highland 1 | Nordex Technicians attended turbine to change the ice detector per EverPower request. | KRAYN-WKO-NDX-20110303 | 1
KRAYN-WKO-NDX-20110310-01 | Adjust Ice sensor | 2011-03-10 | 2011-03-11 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.048611 | Forced |  |  | -0.40972 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110310 | 1
KRAYN-WKO-NDX-20110310-02 | 001 Highland 01WEA80808 FM55 | 2011-03-10 | 2011-03-10 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.22917 | Forced |  |  | 0.09375 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110310 | 1
KRAYN-WKO-NDX-20110311-01 | 001 Highland 17WEA80824 FM50 NC2_1.0 | 2011-03-11 | 2011-03-11 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.052083 | Forced |  |  | 0.23958 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110311 | 1
KRAYN-WKO-NDX-20110311-02 | Check Anemometer | 2011-03-11 | 2011-03-11 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.041667 | Highland 1 | Did remote reset on turbine. Sensor was froze from the ice | KRAYN-WKO-NDX-20110311 | 1
KRAYN-WKO-NDX-20110314-01 | FM 124 | 2011-03-14 | 2011-03-14 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.45833 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.1125 | Highland 1 | FM 124 Nordex techs replaced the main gear box filter | KRAYN-WKO-NDX-20110314 | 1
KRAYN-WKO-NDX-20110316-01 | FM 1213 | 2011-03-16 | 2011-03-16 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.1875 | Forced |  |  | 0.0625 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110316 | 1
KRAYN-WKO-NDX-20110320-01 | 001 Highland 24WEA80816 FM1172 | 2011-03-20 | 2011-03-20 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.30556 | Forced |  |  | 0.03125 | Highland 1 | today we picked the turbine to investagate the fault, it appeared from the ground that the turbine had a broke blade bolt from the | KRAYN-WKO-NDX-20110320 | 1
KRAYN-WKO-NDX-20110320-02 | FM 741 IBS peripherals Fault | 2011-03-20 | 2011-03-20 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.083333 | Forced | KRAYN-NDX-PRT-0043 | 1 | 0.083333 | Highland 1 | FM 741 IBS peripherals Fault | KRAYN-WKO-NDX-20110320 | 1
KRAYN-WKO-NDX-20110320-03 | FM 741 IBS peripherals Fault | 2011-03-20 | 2011-03-20 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.045139 | Forced | KRAYN-NDX-PRT-0043 | 1 | 0.019444 | Highland 1 | FM 741 IBS peripherals Fault | KRAYN-WKO-NDX-20110320 | 1
KRAYN-WKO-NDX-20110321-01 | blown fuse | 2011-03-21 | 2011-03-21 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.10417 | Forced | KRAYN-NDX-PRT-0043 | 1 | 0.16042 | Highland 1 | faulted time of the tower due to electric storm | KRAYN-WKO-NDX-20110321 | 1
KRAYN-WKO-NDX-20110321-02 | bus moduele fuse blown | 2011-03-21 | 2011-03-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.14236 | Forced | KRAYN-NDX-PRT-0043 | 1 | 0.26181 | Highland 1 | start and stop times | KRAYN-WKO-NDX-20110321 | 1
KRAYN-WKO-NDX-20110322-01 | FM1172 | 2011-03-22 | 2011-03-22 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.54167 | Forced | KRAYN-NDX-PRT-0693,KRAYN-NDX-PRT-0725 | 1,1 | 0.22222 | Highland 1 | FM 1172 Pitch power fault. Nordex techs went up to change out a slipring | KRAYN-WKO-NDX-20110322 | 1
KRAYN-WKO-NDX-20110411-01 | alu trouble shoot | 2011-04-11 | 2011-04-11 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.46875 | Highland 1 | ALU Refill | KRAYN-WKO-NDX-20110411 | 1
KRAYN-WKO-NDX-20110413-01 | Pitch Motor Brake Replacement | 2011-04-13 | 2011-04-13 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 1.0417 | Forced |  |  | 0.52083 | Highland 1 | WTG12_80819_Troubleshoot pitch | KRAYN-WKO-NDX-20110413 | 1
KRAYN-WKO-NDX-20110413-02 | Pitch Motor Brake Replacement | 2011-04-13 | 2011-04-13 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 2.1458 | Forced |  |  | 1.0833 | Highland 1 | WTG12_80819_Troubleshoot pitch | KRAYN-WKO-NDX-20110413 | 1
KRAYN-WKO-NDX-20110414-01 | Maintenanceplan 80829 | 2011-04-14 | 2011-04-14 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1.2778 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 4,13 | 0.56597 | Highland 1 | Function Test | KRAYN-WKO-NDX-20110414 | 1
KRAYN-WKO-NDX-20110414-02 | Maintenanceplan 80829 | 2011-04-14 | 2011-04-14 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1.7049 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 8,4,13 | 0.95486 | Highland 1 | Function Test | KRAYN-WKO-NDX-20110414 | 1
KRAYN-WKO-NDX-20110414-03 | Maintenanceplan 80829 | 2011-04-14 | 2011-04-14 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1.3854 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,4,4,6,3,2,17 | 0.66319 | Highland 1 | Function Test | KRAYN-WKO-NDX-20110414 | 1
KRAYN-WKO-NDX-20110414-04 | Maintenanceplan 80829 | 2011-04-14 | 2011-04-14 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 0.375 | Planned |  |  | 0.17361 | Highland 1 | Function Test | KRAYN-WKO-NDX-20110414 | 1
KRAYN-WKO-NDX-20110414-05 | Maintenanceplan 80829 | 2011-04-14 | 2011-04-14 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1.0625 | Planned |  |  | 0.37847 | Highland 1 | Function Test | KRAYN-WKO-NDX-20110414 | 1
KRAYN-WKO-NDX-20110418-01 | Maintenanceplan 80812 | 2011-04-18 | 2011-04-18 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 8.3243 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0363,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351 | 1,2,1,1,1,8,3,1,4 | 1.6396 | Highland 1 | Maintenance type III | KRAYN-WKO-NDX-20110418 | 1
KRAYN-WKO-NDX-20110418-02 | Maintenanceplan 80812 | 2011-04-18 | 2011-04-18 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 8.3451 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0363,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0351 | 1,2,1,1,1,8,3,1,4 | 1.8965 | Highland 1 | Maintenance type III | KRAYN-WKO-NDX-20110418 | 1
KRAYN-WKO-NDX-20110425-01 | US_Highland_22WEA80830_Maintenanceplan | 2011-04-25 | 2011-04-25 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3.4333 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,4,1,1,1 | 0.37153 | Highland 1 | Maintenance 3. | KRAYN-WKO-NDX-20110425 | 1
KRAYN-WKO-NDX-20110425-02 | US_Highland_22WEA80830_Maintenanceplan | 2011-04-25 | 2011-04-25 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 3.4333 | Forced | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0587 | 1,1,4,1,1,1 | 0.37153 | Highland 1 | Maintenance 3. | KRAYN-WKO-NDX-20110425 | 1
KRAYN-WKO-NDX-20110425-03 | Maintenanceplan 80831 | 2011-04-25 | 2011-04-25 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 5.1347 | Planned |  |  | 1.7458 | Highland 1 | Replace Slip Ring Brushes and Cleaned Cabinet. | KRAYN-WKO-NDX-20110425 | 1
KRAYN-WKO-NDX-20110425-04 | Maintenanceplan 80831 | 2011-04-25 | 2011-05-12 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.20833 | Planned |  |  | 0.0625 | Highland 1 | Replace Slip Ring Brushes and Cleaned Cabinet. | KRAYN-WKO-NDX-20110425 | 1
KRAYN-WKO-NDX-20110428-01 | Maintenanceplan 80810 | 2011-04-28 | 2011-04-28 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.2236 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,4,4,6,3,2,17 | 0.79583 | Highland 1 | Type 3 maintenance. | KRAYN-WKO-NDX-20110428 | 1
KRAYN-WKO-NDX-20110428-02 | Maintenanceplan 80810 | 2011-04-28 | 2011-04-28 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.5778 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,1,1,1,4,4,4,6,3,2,17 | 0.9 | Highland 1 | Type 3 maintenance. | KRAYN-WKO-NDX-20110428 | 1
KRAYN-WKO-NDX-20110428-03 | Maintenanceplan 80810 | 2011-04-28 | 2011-04-28 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.7236 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,1,1,1,4,4,4,6,3,2,17 | 0.97292 | Highland 1 | Type 3 maintenance. | KRAYN-WKO-NDX-20110428 | 1
KRAYN-WKO-NDX-20110501-01 | US_Highland_80820_Fan Wheel Retro | 2011-05-01 | 2011-05-01 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.47917 | Forced | KRAYN-NDX-PRT-0959 | 2 | 0.20139 | Highland 1 | Nordex technicians applied yaw motor brake retrofit. Had difficulty with a microswitch during process. | KRAYN-WKO-NDX-20110501 | 1
KRAYN-WKO-NDX-20110504-01 | US_Highland_12WEA80819_Slip ring replace | 2011-05-04 | 2011-05-04 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.28472 | Forced | KRAYN-NDX-PRT-0725 | 1 | 0.24306 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110504 | 1
KRAYN-WKO-NDX-20110506-01 | Maintenanceplan 80816 | 2011-05-06 | 2011-05-06 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.5764 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0682,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,4,4,2,6,3,2,17 | 1.016 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110506 | 1
KRAYN-WKO-NDX-20110506-02 | US_Highland_09WEA80832_Changed gear oil | 2011-05-06 | 2011-05-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.072917 | Forced | KRAYN-NDX-PRT-0325 | 1 | 0.052083 | Highland 1 | Nordex technicians replaced the gear oil filter. | KRAYN-WKO-NDX-20110506 | 1
KRAYN-WKO-NDX-20110506-03 | US_Highland_09WEA80832_Cleaned slip ring | 2011-05-06 | 2011-05-06 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.09375 | Forced |  |  | 0.086806 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110506 | 1
KRAYN-WKO-NDX-20110506-04 | Maintenanceplan 80809 | 2011-05-06 | 2011-05-06 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 3.9132 | Planned | KRAYN-NDX-PRT-0062 | 4 | 2.2299 | Highland 1 | Type 3 maintenance. | KRAYN-WKO-NDX-20110506 | 1
KRAYN-WKO-NDX-20110516-01 | Maintenance 80808 | 2011-05-16 | 2011-05-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2.0694 | Planned | KRAYN-NDX-PRT-0062 | 3 | 1.0035 | Highland 1 | Nordex technicians, along with J. Bennett began hub maintenance by greasing pitch blade bearings, performing various checks, and be | KRAYN-WKO-NDX-20110516 | 1
KRAYN-WKO-NDX-20110516-02 | Maintenance 80808 | 2011-05-16 | 2011-05-16 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.9444 | Planned | KRAYN-NDX-PRT-0062 | 3 | 1.1215 | Highland 1 | Nordex technicians, along with J. Bennett began hub maintenance by greasing pitch blade bearings, performing various checks, and be | KRAYN-WKO-NDX-20110516 | 1
KRAYN-WKO-NDX-20110517-01 | US-HIGHLAND-01WEA80808_ZargesLoopProtect | 2011-05-17 | 2011-05-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.17361 | Forced |  |  | 0.37639 | Highland 1 | install protective wire wrap. | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-02 | US-HIGHLAND-01WEA80808_ZargesLoopProtect | 2011-05-17 | 2011-05-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.17361 | Forced |  |  | 0.37639 | Highland 1 | install protective wire wrap. | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-03 | US-HIGHLAND-01WEA80808_ZargesLoopProtect | 2011-05-17 | 2011-05-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.29861 | Forced |  |  | 0.68889 | Highland 1 | install protective wire wrap. | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-04 | US_4330/4779_Rotor Overspeed Monitoring | 2011-05-17 | 2011-05-17 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.0625 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-05 | US_Highland_3875/4374_Prevention of Wate | 2011-05-17 | 2011-05-17 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.44444 | Forced | KRAYN-NDX-PRT-0929 | 2 | 0.43889 | Highland 1 | Install yaw water seal. | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-06 | US-HIGHLAND-WEA80810-FM1208 bad IGBT | 2011-05-17 | 2011-05-17 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1.7917 | Forced |  |  | 0.54167 | Highland 1 | Bad IGBT | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-07 | US-HIGHLAND-WEA80810-FM1208 bad IGBT | 2011-05-17 | 2011-05-17 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 1.7917 | Forced |  |  | 0.54167 | Highland 1 | Bad IGBT | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110517-08 | US-HIGHLAND-WEA80810-FM1208 bad IGBT | 2011-05-17 | 2011-05-17 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 2.4583 | Forced |  |  | 0.875 | Highland 1 | Bad IGBT | KRAYN-WKO-NDX-20110517 | 1
KRAYN-WKO-NDX-20110518-01 | US_4330/4779_Rotor Overspeed Monitoring | 2011-05-18 | 2011-05-18 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.0625 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110518 | 1
KRAYN-WKO-NDX-20110518-02 | US_Highland_3875/4374_Prevention of Wate | 2011-05-18 | 2011-05-18 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.35417 | Forced |  |  | 0.13611 | Highland 1 | Install yaw skirt. | KRAYN-WKO-NDX-20110518 | 1
KRAYN-WKO-NDX-20110518-03 | Maintenanceplan 80813 | 2011-05-18 | 2011-05-18 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.7917 | Planned | KRAYN-NDX-PRT-0062 | 12 | 0.98958 | Highland 1 | Nordex technicians began hub maintenance on turbine; greased the blade bearings, performed functions tests on pitch system, perform | KRAYN-WKO-NDX-20110518 | 1
KRAYN-WKO-NDX-20110518-04 | Maintenanceplan 80813 | 2011-05-18 | 2011-05-18 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.7917 | Planned | KRAYN-NDX-PRT-0062 | 12 | 0.98958 | Highland 1 | Nordex technicians began hub maintenance on turbine; greased the blade bearings, performed functions tests on pitch system, perform | KRAYN-WKO-NDX-20110518 | 1
KRAYN-WKO-NDX-20110518-05 | Maintenanceplan 80813 | 2011-05-18 | 2011-05-18 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4 | Planned | KRAYN-NDX-PRT-0062 | 12 | 1.5243 | Highland 1 | Nordex technicians began hub maintenance on turbine; greased the blade bearings, performed functions tests on pitch system, perform | KRAYN-WKO-NDX-20110518 | 1
KRAYN-WKO-NDX-20110520-01 | Maintenanceplan 80814 | 2011-05-20 | 2011-05-20 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 5.6896 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 4,2,1,1,1,1,1,4,2,1,12,5 | 2.1667 | Highland 1 | Nordex Technicians Greased Blade Bearings, Cleaned hub slip ring, performed various fuction tests, treated all ruber seals with sil | KRAYN-WKO-NDX-20110520 | 1
KRAYN-WKO-NDX-20110520-02 | US-HIGHLAND-06WEA80813_ZargesLoopProtect | 2011-05-20 | 2011-05-20 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.29306 | Highland 1 | inspect cable grabs, install cable wrap, install zares loop | KRAYN-WKO-NDX-20110520 | 1
KRAYN-WKO-NDX-20110520-03 | Maintenanceplan 80814 | 2011-05-20 | 2011-05-20 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.6424 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,5 | 1.316 | Highland 1 | Nordex Technicians Greased Blade Bearings, Cleaned hub slip ring, performed various fuction tests, treated all ruber seals with sil | KRAYN-WKO-NDX-20110520 | 1
KRAYN-WKO-NDX-20110520-04 | Maintenanceplan 80814 | 2011-05-20 | 2011-05-20 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 4.4688 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,5 | 1.7083 | Highland 1 | Nordex Technicians Greased Blade Bearings, Cleaned hub slip ring, performed various fuction tests, treated all ruber seals with sil | KRAYN-WKO-NDX-20110520 | 1
KRAYN-WKO-NDX-20110522-01 | US-HIGHLAND-21WEA80828_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.013889 | Forced |  |  | 0.013889 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-02 | US-HIGHLAND-21WEA80828_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.013889 | Forced |  |  | 0.013889 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-03 | US-HIGHLAND-22WEA80830_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.041667 | Highland 1 | Grinding Yaw Disck | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-04 | US-HIGHLAND-22WEA80830_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.041667 | Highland 1 | Grinding Yaw Disck | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-05 | US-HIGHLAND-23WEA80815_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.038194 | Forced |  |  | 0.034722 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-06 | US-HIGHLAND-24WEA80816_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.10069 | Forced |  |  | 0.09375 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-07 | US-HIGHLAND-24WEA80816_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 0.15278 | Forced |  |  | 0.14583 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-08 | US-HIGHLAND-25WEA80829_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.055556 | Forced |  |  | 0.052083 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-09 | US-HIGHLAND-17WEA80824_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.27083 | Forced |  |  | 0.13056 | Highland 1 | Scuff yaw disc. | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-10 | US-HIGHLAND-18WEA80825__Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.10486 | Forced |  |  | 0.10556 | Highland 1 | Scuff yaw disc to reduce noise. | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-11 | US-HIGHLAND-19WEA80826_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.084722 | Forced |  |  | 0.047917 | Highland 1 | Scuff yaw disc to reduce noise. | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-12 | US-HIGHLAND-20WEA80827_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.034722 | Forced |  |  | 0.03125 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-13 | US-HIGHLAND-21WEA80828_Scuff Disc | 2011-05-22 | 2011-05-22 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.013889 | Forced |  |  | 0.013889 | Highland 1 | Grinding Yaw Disk | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110522-14 | No work order description provided by contractor | 2011-05-22 | 2011-05-22 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.66667 | Planned |  |  | 0.35 | Highland 1 | Adjusted yaw brake pressure | KRAYN-WKO-NDX-20110522 | 1
KRAYN-WKO-NDX-20110523-01 | Type III Maintenance | 2011-05-23 | 2011-05-23 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 10 | Planned |  |  | 7.75 | Highland 1 | Type III maintenance on basement, change oils and lube in nacelle | KRAYN-WKO-NDX-20110523 | 1
KRAYN-WKO-NDX-20110523-02 | No work order description provided by contractor | 2011-05-23 | 2011-05-23 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.3 | Highland 1 | Hub door latch fell off. Retrieved and checked for damage | KRAYN-WKO-NDX-20110523 | 1
KRAYN-WKO-NDX-20110524-01 | Type III Maintenance | 2011-05-24 | 2011-05-24 | KRAYN-WGT07 | General Maintenance | Nordex USA OandM | 7.3 | Planned |  |  | 6.4 | Highland 1 | Torque and inspect nacelle cabin, torque and clean tower section, Type III maintenance on bottom box | KRAYN-WKO-NDX-20110524 | 1
KRAYN-WKO-NDX-20110524-02 | No work order description provided by contractor | 2011-05-24 | 2011-05-24 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 15.5 | Forced |  |  | 12.5167 | Highland 1 | Change yaw brake pads | KRAYN-WKO-NDX-20110524 | 1
KRAYN-WKO-NDX-20110524-03 | Change Yaw Brake Pads | 2011-05-24 | 2011-05-24 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 5.8 | Planned |  |  | 13.05 | Highland 1 | Change all yaw brake pads | KRAYN-WKO-NDX-20110524 | 1
KRAYN-WKO-NDX-20110525-01 | No work order description provided by contractor | 2011-05-25 | 2011-05-25 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 4.0833 | Highland 1 | Investigate hub noise (found broken bolt) | KRAYN-WKO-NDX-20110525 | 1
KRAYN-WKO-NDX-20110526-01 | No work order description provided by contractor | 2011-05-26 | 2011-05-26 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 1.5833 | Forced |  |  | 0.48333 | Highland 1 | Replaced micro logic in Q10 | KRAYN-WKO-NDX-20110526 | 1
KRAYN-WKO-NDX-20110526-02 | No work order description provided by contractor | 2011-05-26 | 2011-05-26 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1.3 | Planned |  |  | 0.58333 | Highland 1 | Replaced micro logic in Q10 | KRAYN-WKO-NDX-20110526 | 1
KRAYN-WKO-NDX-20110526-03 | No work order description provided by contractor | 2011-05-26 | 2011-05-26 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1.4167 | Planned |  |  | 0.66667 | Highland 1 | Replaced micro logic in Q10 | KRAYN-WKO-NDX-20110526 | 1
KRAYN-WKO-NDX-20110526-04 | No work order description provided by contractor | 2011-05-26 | 2011-05-26 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 3.1667 | Planned |  |  | 0.51667 | Highland 1 | Replaced micro logic in Q10 | KRAYN-WKO-NDX-20110526 | 1
KRAYN-WKO-NDX-20110526-05 | No work order description provided by contractor | 2011-05-26 | 2011-05-26 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 1.05 | Planned |  |  | 0.58333 | Highland 1 | Replaced micro logic in Q10 | KRAYN-WKO-NDX-20110526 | 1
KRAYN-WKO-NDX-20110527-01 | Maintenanceplan 80824 | 2011-05-27 | 2011-06-27 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 1.1042 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0322 | 4,2,1,4,1,1,1,4,4,6,3,2,17,1 | 0.66042 | Highland 1 | Maintenance 3 stage 2 | KRAYN-WKO-NDX-20110527 | 1
KRAYN-WKO-NDX-20110530-01 | No work order description provided by contractor | 2011-05-30 | 2011-05-30 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 2.6833 | Forced |  |  | 4 | Highland 1 | Pinned out hub for rope access | KRAYN-WKO-NDX-20110530 | 1
KRAYN-WKO-NDX-20110530-02 | No work order description provided by contractor | 2011-05-30 | 2011-05-30 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 1.3333 | Forced |  |  | 1.1667 | Highland 1 | Scuffed yaw disc | KRAYN-WKO-NDX-20110530 | 1
KRAYN-WKO-NDX-20110530-03 | No work order description provided by contractor | 2011-05-30 | 2011-05-30 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 3 | Planned |  |  | 4.3833 | Highland 1 | Pinned out hub for LM rope access | KRAYN-WKO-NDX-20110530 | 1
KRAYN-WKO-NDX-20110530-04 | No work order description provided by contractor | 2011-05-30 | 2011-05-30 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 2.5 | Planned |  |  | 4.3833 | Highland 1 | Started Zargus loop retro | KRAYN-WKO-NDX-20110530 | 1
KRAYN-WKO-NDX-20110530-05 | Gen Rotor RPM | 2011-05-30 | 2011-05-30 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 4 | Planned |  |  | 1.4167 | Highland 1 | Change high speed inductive sensors, inspect wires and connections, check connections on gen encoder | KRAYN-WKO-NDX-20110530 | 1
KRAYN-WKO-NDX-20110531-01 | US_LM 43.8 breaking bolts_WTG80828 | 2011-05-31 | 2011-05-31 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.094444 | Highland 1 | Removed broken blade bolt from the hub | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-02 | US_Highland_21WEA80828_broken blade bolt | 2011-05-31 | 2011-05-31 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.13889 | Forced |  |  | 0.027778 | Highland 1 | Nordex technicians went to investigate a noise coming from the hub; discovered a broken blade bolt. | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-03 | US_Highland_10WEA80817_Blade Repair | 2011-05-31 | 2011-05-31 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.11806 | Forced |  |  | 0.11806 | Highland 1 | LM Blade Repair | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-04 | Maintenanceplan 80817 | 2011-05-31 | 2011-05-31 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 0.62153 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,3,17 | 0.33403 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-05 | Maintenanceplan 80817 | 2011-05-31 | 2011-05-31 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1.0799 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,3,17 | 0.65347 | Highland 1 | Type III hub work | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-06 | Maintenanceplan 80817 | 2011-05-31 | 2011-05-31 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1.1215 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,1,1,3,17 | 0.89792 | Highland 1 | Type III hub work | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-07 | US_Highland_05WEA80812_Blade Repair | 2011-05-31 | 2011-05-31 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.23611 | Forced |  |  | 0.23611 | Highland 1 | LM Blaee Repair | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-08 | No work order description provided by contractor | 2011-05-31 | 2011-05-31 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 1.55 | Highland 1 | Type III Maintenance | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-09 | No work order description provided by contractor | 2011-05-31 | 2011-05-31 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 4 | Planned |  |  | 2.6667 | Highland 1 | Type III Maintenance | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-10 | No work order description provided by contractor | 2011-05-31 | 2011-05-31 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 0.91667 | Highland 1 | Inductive sensor troubleshooting | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110531-11 | No work order description provided by contractor | 2011-05-31 | 2011-05-31 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 1.0167 | Forced |  |  | 0.4 | Highland 1 | Control cabinet overtemp | KRAYN-WKO-NDX-20110531 | 1
KRAYN-WKO-NDX-20110601-01 | US_Highland_21WEA80828_Pitchmaster II | 2011-06-01 | 2011-06-01 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.34375 | Forced |  |  | 0.36458 | Highland 1 | Nordex Techncians troubleshot a pitch problem; examined various components, finally finding a limit switch malfunctioning due to br | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-02 | US_Highland_19WEA80826_Blade Repair | 2011-06-01 | 2011-06-11 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.027778 | Forced |  |  | 0.055556 | Highland 1 | LM Blade Repair | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-03 | US_Highland_19WEA80826_Blade Repair | 2011-06-01 | 2011-06-11 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.15278 | Forced |  |  | 0.18056 | Highland 1 | LM Blade Repair | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-04 | US_Highland_19WEA80826_Blade Repair | 2011-06-01 | 2011-06-11 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.40278 | Forced |  |  | 0.30556 | Highland 1 | LM Blade Repair | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-05 | US_Highland_13WEA80820_Blade Repair | 2011-06-01 | 2011-06-01 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.10764 | Forced |  |  | 0.09375 | Highland 1 | LM Blade Repair | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-06 | No work order description provided by contractor | 2011-06-01 | 2011-06-01 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 3.0333 | Highland 1 | Type III Maintenance | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110601-07 | FM1176 | 2011-06-01 | 2011-06-01 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.7 | Highland 1 | Picth fault | KRAYN-WKO-NDX-20110601 | 1
KRAYN-WKO-NDX-20110602-01 | No work order description provided by contractor | 2011-06-02 | 2011-06-02 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 8.8667 | Planned |  |  | 7.5667 | Highland 1 | clean gear oil from tower | KRAYN-WKO-NDX-20110602 | 1
KRAYN-WKO-NDX-20110602-02 | No work order description provided by contractor | 2011-06-02 | 2011-06-02 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 3.5833 | Forced |  |  | 3.1667 | Highland 1 | Replaced grounding brush on generator | KRAYN-WKO-NDX-20110602 | 1
KRAYN-WKO-NDX-20110603-01 | US_Highland_17WEA80824_GenRot RpmDiff H | 2011-06-03 | 2011-06-03 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.083333 | Highland 1 | Nordex technicians attended tower 17 to troubleshoot a recurring Gen RPM fault. Changed the Gen RPM P&F module with the Rotor RPM | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-02 | US_Highland_17WEA80824_GenRot RpmDiff H | 2011-06-03 | 2011-06-03 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.083333 | Highland 1 | Nordex technicians attended tower 17 to troubleshoot a recurring Gen RPM fault. Changed the Gen RPM P&F module with the Rotor RPM | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-03 | US_Highland_17WEA80824_GenRot RpmDiff H | 2011-06-03 | 2011-06-03 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.083333 | Highland 1 | Nordex technicians attended tower 17 to troubleshoot a recurring Gen RPM fault. Changed the Gen RPM P&F module with the Rotor RPM | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-04 | Maintenanceplan 80832 | 2011-06-03 | 2011-06-03 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 3.0625 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0009 | 4,2,1,4,1,1,1,4,4,6,3,2,17,1 | 0.58819 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-05 | US_Highland_23WEA80815_Blade Repair | 2011-06-03 | 2011-06-03 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.125 | Highland 1 | Blade Repair w/ LM | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-06 | No work order description provided by contractor | 2011-06-03 | 2011-06-03 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 34.5 | Planned |  |  | 7 | Highland 1 |  | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110603-07 | No work order description provided by contractor | 2011-06-03 | 2011-06-03 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.76667 | Highland 1 | Refill ALU, replace bolts on nacell roof | KRAYN-WKO-NDX-20110603 | 1
KRAYN-WKO-NDX-20110604-01 | Type III Maintenance | 2011-06-04 | 2011-06-04 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 30 | Planned |  |  | 8.45 | Highland 1 | Allign generator, tower and basement maintenance | KRAYN-WKO-NDX-20110604 | 1
KRAYN-WKO-NDX-20110605-01 | Type III Maintenance | 2011-06-05 | 2011-06-05 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 10 | Planned |  |  | 7.4167 | Highland 1 | Type III hub maintenance | KRAYN-WKO-NDX-20110605 | 1
KRAYN-WKO-NDX-20110605-02 | Type III Maintenance | 2011-06-05 | 2011-06-05 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 10 | Planned |  |  | 7.2 | Highland 1 | Type III hub maintenance and cleaning | KRAYN-WKO-NDX-20110605 | 1
KRAYN-WKO-NDX-20110606-01 | Maintenanceplan 80832 | 2011-06-06 | 2011-06-06 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 0.91667 | Planned | KRAYN-NDX-PRT-0009 | 1 | 0.29653 | Highland 1 | Mainternance type 3. | KRAYN-WKO-NDX-20110606 | 1
KRAYN-WKO-NDX-20110607-01 | Maintenanceplan 80815 | 2011-06-07 | 2011-06-07 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0.58333 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,1,4,1,1,1,1,4,6,3,2,17 | 0.48056 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110607 | 1
KRAYN-WKO-NDX-20110607-02 | Maintenanceplan 80815 | 2011-06-07 | 2011-06-07 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0.97917 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 3,2,4,4,1,1,1,4,4,4,6,3,2,17,4,1,1,1,1,1,3,4,4,6,2,17 | 0.70069 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110607 | 1
KRAYN-WKO-NDX-20110607-03 | Maintenanceplan 80816 | 2011-06-07 | 2011-06-07 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 0.10417 | Planned |  |  | 0.10417 | Highland 1 | Nordex technicians began safety functions. | KRAYN-WKO-NDX-20110607 | 1
KRAYN-WKO-NDX-20110607-04 | Maintenanceplan 80816 | 2011-06-07 | 2011-06-07 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 0.49306 | Planned |  |  | 0.49306 | Highland 1 | Nordex technicians began safety functions. | KRAYN-WKO-NDX-20110607 | 1
KRAYN-WKO-NDX-20110607-05 | Maintenanceplan 80816 | 2011-06-07 | 2011-06-07 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 0.73264 | Planned |  |  | 0.73264 | Highland 1 | Nordex technicians began safety functions. | KRAYN-WKO-NDX-20110607 | 1
KRAYN-WKO-NDX-20110608-01 | US_Highland_15WEA80822_FE 1130 | 2011-06-08 | 2011-06-08 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.20556 | Forced |  |  | 0.10278 | Highland 1 | Adjusted cam switch after everpower was in the turbine | KRAYN-WKO-NDX-20110608 | 1
KRAYN-WKO-NDX-20110608-02 | WTG System ok | 2011-06-08 | 2011-06-08 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 8.2333 | Highland 1 | Replace high speed and low speed inductive sensors, change low speed counting ring | KRAYN-WKO-NDX-20110608 | 1
KRAYN-WKO-NDX-20110609-01 | US_Highland_08WEA80831_Gen allignment | 2011-06-09 | 2011-06-09 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.20139 | Highland 1 | Nordex technicians attended tower 8 per EP request to re-align generator due to a vibration their SKF sensor picked up | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-02 | US_Highaland_10WEA80817_air scoop cleane | 2011-06-09 | 2011-06-09 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.11458 | Forced |  |  | 0.11458 | Highland 1 | Nordex technicians attended tower 10 per EP request due to dust and light oil spots on the air scoop. | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-03 | US_Highland_11WEA80818_Yaw motor / yaw d | 2011-06-09 | 2011-06-09 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.09375 | Forced |  |  | 0.052083 | Highland 1 | Nordex technicians attended tower after NCII displayed FM 490. | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-04 | US_Highland_11WEA80818_Yaw motor / yaw d | 2011-06-09 | 2011-06-09 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0.39931 | Forced |  |  | 0.052083 | Highland 1 | Nordex technicians attended tower after NCII displayed FM 490. | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-05 | US_Highland_17WEA80824_clean slip ring | 2011-06-09 | 2011-06-09 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.15972 | Forced |  |  | 0.20139 | Highland 1 | clean slip ring | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-06 | Maintenanceplan 80825 | 2011-06-09 | 2011-06-09 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 1.0444 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,13 | 0.73542 | Highland 1 | TYPE III hub work | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110609-07 | Maintenanceplan 80825 | 2011-06-09 | 2011-06-09 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.3563 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0682,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 4,2,1,4,1,15,1,1,4,4,2,6,3,2,17,12,13 | 0.93819 | Highland 1 | TYPE III hub work | KRAYN-WKO-NDX-20110609 | 1
KRAYN-WKO-NDX-20110610-01 | US_Highland_23WEA80815_align generator | 2011-06-10 | 2011-06-10 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.1875 | Forced |  |  | 0.17292 | Highland 1 | align generator | KRAYN-WKO-NDX-20110610 | 1
KRAYN-WKO-NDX-20110610-02 | US_Highland_25WEA80829_align generator | 2011-06-10 | 2011-06-10 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.059028 | Forced |  |  | 0.092361 | Highland 1 | align generator | KRAYN-WKO-NDX-20110610 | 1
KRAYN-WKO-NDX-20110612-01 | Maintenanceplan 80825 | 2011-06-12 | 2011-06-12 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 0.59375 | Planned |  |  | 0.30903 | Highland 1 | Type III | KRAYN-WKO-NDX-20110612 | 1
KRAYN-WKO-NDX-20110613-01 | US_Highland_23WEA80815_Type III Maintena | 2011-06-13 | 2011-06-13 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 2.2153 | Forced |  |  | 0.86806 | Highland 1 | Hub work/basebolts | KRAYN-WKO-NDX-20110613 | 1
KRAYN-WKO-NDX-20110613-02 | No work order description provided by contractor | 2011-06-13 | 2011-06-13 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 8.5 | Forced |  |  | 8.65 | Highland 1 | Type III maintenance on hub | KRAYN-WKO-NDX-20110613 | 1
KRAYN-WKO-NDX-20110614-01 | Maintenanceplan 80828 | 2011-06-14 | 2011-06-14 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1.0715 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0053,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0697,KRAYN-NDX-PRT-0363 | 4,2,1,4,1,1,1,1,4,4,6,3,2,17,0.5,8,4,25 | 0.96389 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110614-02 | US_Highland_23WEA80815_Type III Maintena | 2011-06-14 | 2011-06-14 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 1.0278 | Forced |  |  | 0.47222 | Highland 1 | Troubleshoot Hyd. System | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110614-03 | Maintenanceplan 80826 | 2011-06-14 | 2011-06-14 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 0.37847 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,15 | 0.33333 | Highland 1 | Type III hub work | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110614-04 | Maintenanceplan 80826 | 2011-06-14 | 2011-06-14 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 0.71181 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 5,2,1,1,1,1,1,4,2,1,12,15 | 0.66667 | Highland 1 | Type III hub work | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110614-05 | No work order description provided by contractor | 2011-06-14 |  | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 7.5667 | Highland 1 | yaw stack replacement-pulled ID #s from stack - took pictures of serial numbers of old stacks | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110614-06 | No work order description provided by contractor | 2011-06-14 | 2011-06-14 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 1.4167 | Forced |  |  | 1.05 | Highland 1 | Punchlist items | KRAYN-WKO-NDX-20110614 | 1
KRAYN-WKO-NDX-20110615-01 | US_Highland_23WEA80815_Type III Maintena | 2011-06-15 | 2011-06-15 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 0.77778 | Forced |  |  | 0.34722 | Highland 1 | Nordex technicians completed safety functions tests, torqued tower sections, top box checks, etc. | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-02 | US_Highland_19WEA80826_Yaw hyd brake fau | 2011-06-15 | 2011-06-15 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.36806 | Forced |  |  | 0.13889 | Highland 1 | Nordex technicians troubleshot and corrected a yaw hyd brake fault cause by a problematic valve. | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-03 | Maintenanceplan 80818 | 2011-06-15 | 2011-06-15 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 0.20833 | Highland 1 | Type III maintenance - MX2 | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-04 | Maintenanceplan 80818 | 2011-06-15 | 2011-06-15 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 1.2965 | Planned | KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062 | 2,1,1,1,1,4,4,6,3,2,17,1,1,1,1,1,1,1 | 0.75903 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-05 | Maintenanceplan 80818 | 2011-06-15 | 2011-06-15 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 1.5674 | Planned | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 1,1,1,1,1,1,1,2,1,1,1,1,4,4,6,3,2,17 | 1.1056 | Highland 1 | Type III maintenance - MX2 | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-06 | No work order description provided by contractor | 2011-06-15 |  | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0981,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062 | ,,,,,,,, | 7.5667 | Highland 1 | Type III maintenance section 2/nacelle maintenance | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110615-07 | No work order description provided by contractor | 2011-06-15 |  | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 7.5667 | Highland 1 | Yaw drive replacement | KRAYN-WKO-NDX-20110615 | 1
KRAYN-WKO-NDX-20110617-01 | US_Highland_19WEA80826_Ultra Sonic Anemo | 2011-06-17 | 2011-06-17 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.125 | Highland 1 | Replace Ultra Sonic Anemometer | KRAYN-WKO-NDX-20110617 | 1
KRAYN-WKO-NDX-20110617-02 | Maintenanceplan 80827 | 2011-06-17 | 2011-06-17 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 0.52778 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 4,2,1,1,1,1,1,4,2,1 | 0.475 | Highland 1 | Nordex technicians conducted type III maintenance in the nacelle and the bottom box. | KRAYN-WKO-NDX-20110617 | 1
KRAYN-WKO-NDX-20110617-03 | US_Highland_01WEA80808_Yaw disc scuffing | 2011-06-17 | 2011-06-17 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.041667 | Highland 1 | scuffed yaw disc per Everpower request | KRAYN-WKO-NDX-20110617 | 1
KRAYN-WKO-NDX-20110617-04 | WTG System ok | 2011-06-17 | 2011-06-17 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 10.75 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0363 | 12,1,2,2,14 | 10.8 | Highland 1 | Type III maintenance on wtg 20-hub maintenance | KRAYN-WKO-NDX-20110617 | 1
KRAYN-WKO-NDX-20110618-01 | WTG System ok | 2011-06-18 | 2011-06-18 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 8.5 | Forced | KRAYN-NDX-PRT-0053,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0964 | 0.1 gal,0.25gal,3,4,4,4qts. | 6.1667 | Highland 1 | Type III maintenance on WTG 24- MX4- cleaned nacelle and all tower decks | KRAYN-WKO-NDX-20110618 | 1
KRAYN-WKO-NDX-20110620-01 | US_Highland_15WEA80822_Gen. alignment | 2011-06-20 | 2011-06-20 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.86111 | Forced |  |  | 0.39306 | Highland 1 | Nordex technicians performed a difficult generator allignment. | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-02 | Maintenanceplan 80820 | 2011-06-20 | 2011-06-20 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.3125 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0363,KRAYN-NDX-PRT-0062 | 4,2,1,20,1,20,1,1,4,4,6,3,2,17,10,12 | 0.61181 | Highland 1 | Type 3 maintenance | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-03 | Maintenanceplan 80820 | 2011-06-20 | 2011-06-28 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.54167 | Planned |  |  | 0.27083 | Highland 1 | Clean Tower and Naccell, Paint | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-04 | Maintenanceplan 80820 | 2011-06-20 | 2011-06-20 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 5.1535 | Planned | KRAYN-NDX-PRT-0053,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0363,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0447,KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0348 | 4,4,10,12,4,2,1,20,1,1,1,4,3,17,20,4,6,2 | 1.4556 | Highland 1 | Clean Tower and Naccell, Paint | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-05 | Yaw HydBrk not closed | 2011-06-20 | 2011-06-20 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 4.4167 | Planned |  |  | 3.45 | Highland 1 | Troubleshoot FM419 Fault (Yaw HydBrk not closed) Changed relay 124k1 and yawed the turbine CW and CCW | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-06 | WTG System ok | 2011-06-20 | 2011-06-20 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 9.4333 | Highland 1 | Generator alignment. | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-07 | WTG System ok | 2011-06-20 | 2011-06-20 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 7 | Forced |  |  | 9.4333 | Highland 1 | Type III maintenance on wtg 15 - mx2 | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110620-08 | Yaw HydBrk not closed | 2011-06-20 | 2011-06-20 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 4.4167 | Planned |  |  | 3.45 | Highland 1 | Troubleshoot FM419 Fault (Yaw HydBrk not closed) Changed relay 124k1 and yawed the turbine CW and CCW | KRAYN-WKO-NDX-20110620 | 1
KRAYN-WKO-NDX-20110621-01 | Maintenanceplan 80828 | 2011-06-21 | 2011-06-21 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 0.68611 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363,KRAYN-NDX-PRT-0697,KRAYN-NDX-PRT-0053 | 8,25,4,0.5 | 0.57847 | Highland 1 | Completed stage 3 of the type 3 maint. and Butler completed section 15 tower. Also painted any scratches on the tower | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-02 | US_Highland_14WEA80821_Gen. alignment | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.15625 | Forced |  |  | 0.41667 | Highland 1 | gen. alignment | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-03 | Maintenanceplan 80821 | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.42708 | Planned |  |  | 0.38542 | Highland 1 | hub maintenance completed. | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-04 | Maintenanceplan 80821 | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.79167 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 3,2,1,2,1,1,1,4,2,1 | 0.38542 | Highland 1 | hub maintenance completed. | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-05 | Maintenanceplan 80821 | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.25 | Planned | KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0682 | 2,1,1,4,2,3,2,1,1,1 | 0.53819 | Highland 1 | hub maintenance completed. | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-06 | Maintenanceplan 80821 | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.2708 | Planned | KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0682 | 2,1,1,4,2,3,2,1,1,1 | 0.99097 | Highland 1 | hub maintenance completed. | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-07 | US_Highland_02WEA80809_BoreScope WTG2 | 2011-06-21 | 2011-06-21 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.20833 | Forced |  |  | 0.15 | Highland 1 | BoreScope/Gearbox Inspection | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-08 | US_Highland_02WEA80809_BoreScope WTG2 | 2011-06-21 | 2011-06-21 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.3125 | Forced |  |  | 0.21528 | Highland 1 | BoreScope/Gearbox Inspection | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-09 | WTG System ok | 2011-06-21 | 2011-07-05 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 11.5 | Forced |  |  | 7.5667 | Highland 1 | Blade bolt extraction on WTG 1 | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110621-10 | WTG System ok | 2011-06-21 | 2011-06-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 12.5 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0363 | 12,1,2,2,12 | 11 | Highland 1 | Type III hub maintenance-MX1 | KRAYN-WKO-NDX-20110621 | 1
KRAYN-WKO-NDX-20110622-01 | US_Highland_21WEA80828_FM1153 NC2_1.0 | 2011-06-22 | 2011-06-22 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.74375 | Forced | KRAYN-NDX-PRT-0683 | 1 | 0.90486 | Highland 1 | Techs went up tower to troubleshoot a Pitch problem in the hub. Things that were tried was adjustment of the cam switches of all th | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-02 | US_Highland_17WEA80824_FM 110 | 2011-06-22 | 2011-06-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.05 | Highland 1 | FM110_Replace Pepper&Fuchs Module | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-03 | US_Highland_17WEA80824_FM 110 | 2011-06-22 | 2011-06-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.05 | Highland 1 | FM110_Replace Pepper&Fuchs Module | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-04 | US_Highland_17WEA80824_FM 110 | 2011-06-22 | 2011-06-22 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.05 | Highland 1 | FM110_Replace Pepper&Fuchs Module | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-05 | Maintenanceplan 80818 | 2011-06-22 | 2011-06-22 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 0.39236 | Planned |  |  | 0.35764 | Highland 1 | hub maintenance completed. | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-06 | US_Highland_01WEA80808_BoreScope_WTG1 | 2011-06-22 | 2011-06-22 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.19792 | Forced |  |  | 0.15139 | Highland 1 | BoreScope/Gearbox Inspection | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-07 | No work order description provided by contractor | 2011-06-22 | 2011-06-22 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 19 | Planned |  |  | 8 | Highland 1 | Customer Request Vibration Sensor. Diagnose Vibration on WTG 8 per EverPower, Torqued down all Generator Bolts to spec and checked soft foot with the easylaser system. Removed cracked shaft cover and found I loose bolt on generator. | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-08 | No work order description provided by contractor | 2011-06-22 | 2011-06-22 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 19 | Planned |  |  | 8 | Highland 1 | Customer Request Vibration Sensor. Diagnose Vibration on WTG 8 per EverPower, Torqued down all Generator Bolts to spec and checked soft foot with the easylaser system. Removed cracked shaft cover and found I loose bolt on generator. | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-09 | WTG System ok | 2011-06-22 | 2011-06-22 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0363 | 12,1,2,2,12 | 8.65 | Highland 1 | Type III hub maintenance-MX1 | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-10 | GenRot RpmDiff H Stop | 2011-06-22 | 2011-06-22 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 5 | Planned | KRAYN-NDX-PRT-0568 | 1 | 1.2 | Highland 1 | FM 110_Replaced Pepper&Phuchs Module | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110622-11 | WTG System ok | 2011-06-22 | 2011-06-22 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0363 | 12,1,2,2,12 | 8.65 | Highland 1 | Type III hub maintenance-MX1 | KRAYN-WKO-NDX-20110622 | 1
KRAYN-WKO-NDX-20110623-01 | US_Highland_15WEA80822_BoreScope_WTG15 | 2011-06-23 | 2011-06-23 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.34653 | Forced |  |  | 0.15625 | Highland 1 | BoreScope/ Gearbox Inspection | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-02 | Maintenanceplan 80822 | 2011-06-23 | 2011-06-23 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 0.33681 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,10 | 0.29514 | Highland 1 | Nordex technicians performed rotor and pitch maintenance. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-03 | Maintenanceplan 80822 | 2011-06-23 | 2011-06-23 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 0.33681 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,10 | 0.29514 | Highland 1 | Nordex technicians performed rotor and pitch maintenance. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-04 | Maintenanceplan 80823 | 2011-06-23 | 2011-06-23 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.4375 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0447 | 4,2,1,3,4,1,1,1,6,3,17 | 0.28125 | Highland 1 | Type 3 maint/Stage 2 | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-05 | Maintenanceplan 80823 | 2011-06-23 | 2011-06-23 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.31597 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,10 | 0.27431 | Highland 1 | Nordex technicians completed type III maintenance on the rotor and pitch system. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-06 | Maintenanceplan 80823 | 2011-06-23 | 2011-06-23 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.31597 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,10 | 0.27431 | Highland 1 | Nordex technicians completed type III maintenance on the rotor and pitch system. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-07 | Maintenanceplan 80819 | 2011-06-23 | 2011-06-23 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.0181 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,4,1,15,1,1,4,4,6,3,2,17 | 0.84444 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-08 | Maintenanceplan 80819 | 2011-06-23 | 2011-06-23 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.7472 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0004,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0351,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0587,KRAYN-NDX-PRT-0046,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0348,KRAYN-NDX-PRT-0447 | 4,2,1,1,1,1,4,4,15,4,6,3,2,17 | 1.0458 | Highland 1 | Main. type 3 stage 2 | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-09 | US_Highland_07WEA80814_BoreScope_WTG7 | 2011-06-23 | 2011-06-23 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.10486 | Forced |  |  | 0.059722 | Highland 1 | BoreScope/Gearbox Inspection | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-10 | No work order description provided by contractor | 2011-06-23 | 2011-06-23 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 18.3333 | Planned |  |  | 8.5833 | Highland 1 | Customer Request Vibration Sensor. Found Cabnet side cone bearing bolts loose, Inspected rubber on cone bearings and torqued bolts, checked for soft foot and realigned Generator. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110623-11 | No work order description provided by contractor | 2011-06-23 | 2011-06-23 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 18.3333 | Planned |  |  | 8.5833 | Highland 1 | Customer Request Vibration Sensor. Found Cabnet side cone bearing bolts loose, Inspected rubber on cone bearings and torqued bolts, checked for soft foot and realigned Generator. | KRAYN-WKO-NDX-20110623 | 1
KRAYN-WKO-NDX-20110624-01 | WTG System ok | 2011-06-24 | 2011-06-24 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 10.5 | Forced | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0363 | 12,1,1,2,2 | 7.1 | Highland 1 | Type III hub maintenance-MX1. worked with charlie martin-11979 | KRAYN-WKO-NDX-20110624 | 1
KRAYN-WKO-NDX-20110627-01 | US_Highland_25WEA80829_PLC comm fault Ch | 2011-06-27 | 2011-06-27 | KRAYN-WTG25 | General Maintenance | Nordex USA OandM | 0.052083 | Forced |  |  | 0 | Highland 1 | Nordex technicians attended turbine to correct communications fault from the PLC. PLC was reset and put back into service. No sim | KRAYN-WKO-NDX-20110627 | 1
KRAYN-WKO-NDX-20110627-02 | Maintenanceplan 80819 | 2011-06-27 | 2011-06-27 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0.55972 | Planned |  |  | 0.53264 | Highland 1 | Completed stage 3 of the type 3 maint. And did a gen. alignment check. | KRAYN-WKO-NDX-20110627 | 1
KRAYN-WKO-NDX-20110627-03 | Maintenanceplan 80820 | 2011-06-27 | 2011-06-27 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.39583 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0363 | 12,10 | 0.35694 | Highland 1 | Nordex technicians completed rotor and pitch maintenance. | KRAYN-WKO-NDX-20110627 | 1
KRAYN-WKO-NDX-20110627-04 | WTG System ok | 2011-06-27 | 2011-06-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 12 | Forced |  |  | 8.5167 | Highland 1 | Maintenance Type III stage 2. Worked with daniel sibilab12546 | KRAYN-WKO-NDX-20110627 | 1
KRAYN-WKO-NDX-20110627-05 | No work order description provided by contractor | 2011-06-27 | 2011-06-27 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 20.3333 | Forced | KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0965 | 3,1,1,4 | 10.1667 | Highland 1 | Maintenance 3 Final Clean, Replaced 2 28x28 filter grills on bottom box, Replace light bulbs (2) on Deck 1, Work On maintenace punchlist | KRAYN-WKO-NDX-20110627 | 1
KRAYN-WKO-NDX-20110628-01 | Maintenanceplan 80824 | 2011-06-28 | 2011-06-28 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 0.39583 | Planned | KRAYN-NDX-PRT-0322 | 1 | 0.30556 | Highland 1 | Type III Hub work | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110628-02 | WTG System ok | 2011-06-28 | 2011-06-28 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 6.5 | Forced |  |  | 5 | Highland 1 | Maintenance Type III stage 2 | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110628-03 | No work order description provided by contractor | 2011-06-28 | 2011-06-28 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 4.3333 | Planned | KRAYN-NDX-PRT-0561,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965 | 1,1,1 | 4.0333 | Highland 1 | Replace main bearing AutoLuber, Then refilled with SHC 460 | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110628-04 | No work order description provided by contractor | 2011-06-28 | 2011-06-28 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 3.7667 | Forced | KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0053 | 2,2,1 | 4.0333 | Highland 1 | PunchList, Grind Rust off basement bolts , Coat bolts with molly coat | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110628-05 | No work order description provided by contractor | 2011-06-28 | 2011-06-28 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 4.0333 | Highland 1 | Maintenance 3 , Remove Low Speed shaft cover due to crack, Replace Hoist Cable holder, Remove 5 Gal XMP 320 from Gearbox | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110628-06 | No work order description provided by contractor | 2011-06-28 | 2011-06-28 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 1.5667 | Planned |  |  | 0.78333 | Highland 1 | Diagnose FM 268 Reset Valve Restart Turbine and Monitor | KRAYN-WKO-NDX-20110628 | 1
KRAYN-WKO-NDX-20110629-01 | WTG System ok | 2011-06-29 | 2011-06-29 | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 17.45 | Forced | KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0053,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0964 | 4,4,4,4,4 | 5.95 | Highland 1 | Type III Maintenance Final cleaning | KRAYN-WKO-NDX-20110629 | 1
KRAYN-WKO-NDX-20110630-01 | WTG System ok | 2011-06-30 | 2011-06-30 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 22.5 | Forced | KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0963 | 5ltr,5 bags,.25 gal,3 | 5.5833 | Highland 1 | Type III maintenance on WTG 16. MX 4-cleaned nacelle/ torqued Rotor | KRAYN-WKO-NDX-20110630 | 1
KRAYN-WKO-NDX-20110630-02 | WTG Manual Stop | 2011-06-30 | 2011-06-30 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 2.5 | Highland 1 |  | KRAYN-WKO-NDX-20110630 | 1
KRAYN-WKO-NDX-20110630-03 | WTG Manual Stop | 2011-06-30 | 2011-06-30 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.5 | Highland 1 |  | KRAYN-WKO-NDX-20110630 | 1
KRAYN-WKO-NDX-20110701-01 | US_HIGHLAND_10WEA80817_Gen Alignment | 2011-07-01 | 2011-07-01 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 0.31944 | Highland 1 | Gen. alignment | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-02 | US_Highland_13WEA80820_FM 310 Charles Ma | 2011-07-01 | 2011-07-01 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0 | Highland 1 | Nordex technicians corrected a long-standing FM 310 in conjunction with planned turbine stop-time associated with SEG warranty insp | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-03 | US_Highland_14WEA80821_FM 310 Charles Ma | 2011-07-01 | 2011-07-01 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.41667 | Forced |  |  | 0 | Highland 1 | Nordex technicians corrected a longstanding FM 310 in conjunction with planned turbine down-time associated with an SEG warranty in | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-04 | WTG System ok | 2011-07-01 | 2011-07-01 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 1.7833 | Planned | KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0966 | 1,1 | 0.95 | Highland 1 | Scuffed yaw disk on WTG 4 with dave mader | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-05 | WTG System ok | 2011-07-01 | 2011-07-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 1.2667 | Planned | KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0966 | 1,1 | 6.85 | Highland 1 | Scuffed yaw dis on WTG 8 with Dave Madder 12550. Apex was doing blade inspections so WTG was turned off when we got here. | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-06 | WTG System ok | 2011-07-01 | 2011-07-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 1.2667 | Planned | KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0966 | 1,1 | 6.85 | Highland 1 | Scuffed yaw dis on WTG 8 with Dave Madder 12550. Apex was doing blade inspections so WTG was turned off when we got here. | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-07 | WTG System ok | 2011-07-01 | 2011-07-01 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned | KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0965,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0964 | 4,4,.25 gal,4,4 ltr | 3.6667 | Highland 1 | Type III maintenance on WTG 10 - MX4. Worked with blake carlson 12668 | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110701-08 | No work order description provided by contractor | 2011-07-01 | 2011-07-01 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 15.1333 | Forced | KRAYN-NDX-PRT-0966,KRAYN-NDX-PRT-0054,KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0964 | 4,1,1,2 | 6.1833 | Highland 1 | Type III Final Cleaning | KRAYN-WKO-NDX-20110701 | 1
KRAYN-WKO-NDX-20110703-01 | US_Highland_21WEA80828 FM1208 NC2_1.0 | 2011-07-03 | 2011-07-03 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.95833 | Forced |  |  | 0.17083 | Highland 1 | Reset and recommission SEG | KRAYN-WKO-NDX-20110703 | 1
KRAYN-WKO-NDX-20110705-01 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-05 | 2011-07-07 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.31528 | Highland 1 | Replaced counting ring with counting ring retro. adjusted inductive sensors | KRAYN-WKO-NDX-20110705 | 1
KRAYN-WKO-NDX-20110705-02 | US-HIGHLAND-01WEA80808_Leaking Oil Clean | 2011-07-05 | 2011-07-05 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.125 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110705 | 1
KRAYN-WKO-NDX-20110705-03 | US_Highland_3875/4374_Prevention of Wate | 2011-07-05 | 2011-07-05 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.31528 | Highland 1 | installed water ingression retro | KRAYN-WKO-NDX-20110705 | 1
KRAYN-WKO-NDX-20110705-04 | US_Highland_3875/4374_Prevention of Wate | 2011-07-05 | 2011-07-05 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.375 | Forced |  |  | 0.44792 | Highland 1 | installed water ingression retro | KRAYN-WKO-NDX-20110705 | 1
KRAYN-WKO-NDX-20110706-01 | Maintenance 80808 | 2011-07-06 | 2011-07-06 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 0 | Planned |  |  | 0.16667 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110706 | 1
KRAYN-WKO-NDX-20110706-02 | US_HIGHLAND_03WEA80810_Door Louver | 2011-07-06 | 2011-07-06 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.10417 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0 | Highland 1 | Blake Carlson worked with Sibela and Martin on the door louver. | KRAYN-WKO-NDX-20110706 | 1
KRAYN-WKO-NDX-20110706-03 | WTG System ok | 2011-07-06 | 2011-07-06 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 33.5 | Planned |  |  | 7.1667 | Highland 1 | Placed new centa coupling on high speed shaft | KRAYN-WKO-NDX-20110706 | 1
KRAYN-WKO-NDX-20110707-01 | US_HIGHLAND_03WEA80810_Door Louver | 2011-07-07 | 2011-07-07 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.048611 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.073611 | Highland 1 | Install door louver for weather purposes | KRAYN-WKO-NDX-20110707 | 1
KRAYN-WKO-NDX-20110707-02 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-07 | 2011-07-07 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.03125 | Forced |  |  | 0.25694 | Highland 1 | install new slow speed counting ring | KRAYN-WKO-NDX-20110707 | 1
KRAYN-WKO-NDX-20110707-03 | No work order description provided by contractor | 2011-07-07 | 2011-07-07 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2.2667 | Forced |  |  | 3.4667 | Highland 1 | Installed Parameters into Turbine Yaw converter. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110707 | 1
KRAYN-WKO-NDX-20110707-04 | No work order description provided by contractor | 2011-07-07 | 2011-07-07 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 7.6 | Forced |  |  | 1.5167 | Highland 1 | Loaded Software and Yaw Parameters on computer. Installed Parameters into Turbine Yaw converter. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110707 | 1
KRAYN-WKO-NDX-20110708-01 | No work order description provided by contractor | 2011-07-08 | 2011-07-08 | KRAYN-WTG03 | Warranty Repair | Nordex USA OandM | 6 | Forced |  |  | 1.05 | Highland 1 | Installed Parameters into Turbine Yaw converter using drive windows 2.22. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110708 | 1
KRAYN-WKO-NDX-20110711-01 | US_Highland_3875/4374_Prevention of Wate | 2011-07-11 | 2011-07-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.10139 | Highland 1 | Installed water ingression retro | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-02 | US_HIGHLAND_04WEA80811_Yaw Parameters Go | 2011-07-11 | 2011-07-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.048611 | Highland 1 | Nordex technicians updated ABB Yaw parameters | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-03 | US_5_A_25_5634 Condensate Drain Topbox | 2011-07-11 | 2011-07-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.11111 | Forced |  |  | 0.10069 | Highland 1 | Blake Carlson, Shane sweeney, and Cory Butler also worked on the Drip pan. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-04 | US_HIGHLAND_05WEA80812_Door Louver | 2011-07-11 | 2011-07-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.03125 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.25764 | Highland 1 | Install door louver for weather purposes | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-05 | US_5_A_25_5634 Condensate Drain Topbox | 2011-07-11 | 2011-07-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0.25694 | Highland 1 | Install drip pan for ac unit in top box | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-06 | US_Highland_3875/4374_Prevention of Wate | 2011-07-11 | 2011-07-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.15347 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0.25694 | Highland 1 | Install yaw skirt, rotor cover,coumers for water ingression | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-07 | US_HIGHLAND_05WEA80812_Yaw Parameters Go | 2011-07-11 | 2011-07-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.10903 | Forced |  |  | 0.079861 | Highland 1 | Nordex technicians installed updated yaw parameters on the ABB Yaw converter. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-08 | US_HIGHLAND_06WEA80813_Yaw Parameters Go | 2011-07-11 | 2011-07-11 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.052083 | Highland 1 | Nordex techs updated yaw ABB parameters | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-09 | No work order description provided by contractor | 2011-07-11 | 2011-07-11 | KRAYN-WTG07 | Retrofit | Nordex USA OandM | 2.8 | Forced |  |  | 1.0167 | Highland 1 | Installed Parameters into Turbine Yaw converter using drive windows 2.22. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-10 | No work order description provided by contractor | 2011-07-11 | 2011-07-11 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 3.1667 | Forced |  |  | 1.2 | Highland 1 | Installed Parameters into Turbine Yaw converter using drive windows 2.22. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-11 | No work order description provided by contractor | 2011-07-11 | 2011-07-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6.4333 | Forced |  |  | 1.9167 | Highland 1 | Installed Parameters into Turbine Yaw converter using drive windows 2.22. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-12 | No work order description provided by contractor | 2011-07-11 | 2011-07-11 | KRAYN-WTG06 | Warranty Repair | Nordex USA OandM | 3.1 | Forced |  |  | 1.2667 | Highland 1 | Installed Parameters into Turbine Yaw converter using drive windows 2.22. Set up Data logger in Yaw converter. Yawed Turbine CW and CCW. | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-13 | WTG Manual Stop | 2011-07-11 | 2011-07-11 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 1.2333 | Forced |  |  | 0.61667 | Highland 1 | Updated the Yaw gold files | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-14 | WTG Manual Stop | 2011-07-11 | 2011-07-11 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 1.2333 | Forced |  |  | 0.61667 | Highland 1 | Updated the Yaw gold files | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-15 | WTG Manual Stop | 2011-07-11 | 2011-07-11 | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 5.3667 | Forced |  |  | 2.6833 | Highland 1 | Updated the Yaw gold files | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110711-16 | WTG Manual Stop | 2011-07-11 | 2011-07-11 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0 | Forced |  |  | 1.25 | Highland 1 | Updated the Yaw gold files | KRAYN-WKO-NDX-20110711 | 1
KRAYN-WKO-NDX-20110712-01 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.041667 | Forced | KRAYN-NDX-PRT-0883 | 4 | 0.48958 | Highland 1 | Install slow speed shaft counting ring and 4 new inductive sensors | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-02 | US_HIGHLAND_09WEA80832_Door Louver | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.041667 | Forced | KRAYN-NDX-PRT-0257 | 40 | 0.48958 | Highland 1 | Install door louver for weather purpose | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-03 | US-HIGHLAND-WEA80832 Condensate Drain | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0.48958 | Highland 1 | Install drip pan on top box cooler | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-04 | US_Highland_3875/4374_Prevention of Wate | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.1875 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0.48958 | Highland 1 | Install rotor cover, yaw skirt, and yaw stack coumers | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-05 | US_HIGHLAND_09WEA80832_Yaw Parameters Go | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.041667 | Forced |  |  | 0.48958 | Highland 1 | Install new yaw parameters | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-06 | US-HIGHLAND-09WEA80832_ZargesLoopProtect | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.48958 | Highland 1 | Cory Butler and Ken Hayes worked on the Zarges Cable Loop. | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110712-07 | US-HIGHLAND-09WEA80832_ZargesLoopProtect | 2011-07-12 | 2011-07-12 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 0.48958 | Highland 1 | Cory Butler and Ken Hayes worked on the Zarges Cable Loop. | KRAYN-WKO-NDX-20110712 | 1
KRAYN-WKO-NDX-20110713-01 | US-HIGHLAND-WEA80831Condensate Drain | 2011-07-13 | 2011-07-13 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0.16458 | Highland 1 | Install drip pan top box | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-02 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Prevention of Water Yaw Seal , Comers , Fiberglass shell of low speed shaft | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-03 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 3.6 | Highland 1 | Tighten shaft nut as per Maintenance Type III proceedure. Shaft nut type: Split shaft nut | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-04 | WTG System ok | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Installed drip pan | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-05 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Prevention of Water Yaw Seal , Comers , Fiberglass shell of low speed shaft | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-06 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Prevention of Water Yaw Seal , Comers , Fiberglass shell of low speed shaft | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-07 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 3.6 | Highland 1 | Inspected up tower cable grabs for wear. Installed Zarges cable wrap(Panduet). | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-08 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 3.6 | Highland 1 | Tighten shaft nut as per Maintenance Type III proceedure. Shaft nut type: Split shaft nut | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-09 | WTG System ok | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Installed drip pan | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-10 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Prevention of Water Yaw Seal , Comers , Fiberglass shell of low speed shaft | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-11 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 3.6 | Highland 1 | Prevention of Water Yaw Seal , Comers , Fiberglass shell of low speed shaft | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-12 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 3.6 | Highland 1 | Inspected up tower cable grabs for wear. Installed Zarges cable wrap(Panduet). | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110713-13 | No work order description provided by contractor | 2011-07-13 | 2011-07-13 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 2.45 | Planned |  |  | 0.75 | Highland 1 | Change out UPS.battery as a test to see if it is the problem | KRAYN-WKO-NDX-20110713 | 1
KRAYN-WKO-NDX-20110714-01 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.041667 | Forced | KRAYN-NDX-PRT-0883,KRAYN-NDX-PRT-0883 | 2,2 | 0.69722 | Highland 1 | install low speed counting ring and inductive sensors | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-02 | US_5_A_25_5634 Condensate Drain Topbox | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.24444 | Highland 1 | Install drip pan in top box | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-03 | US_Highland_3875/4374_Prevention of Wate | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.14583 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0.24444 | Highland 1 | install rotor cover, yaw skirt, and yaw stack coumers | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-04 | US-HIGHLAND-10WEA80817 Zarges Loop | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.10417 | Forced |  |  | 0.25139 | Highland 1 | Wrap LV cables with panduate and install chaffing ring | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-05 | Yaw HydBrk not closed | 2011-07-14 | 2011-07-14 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 1.7 | Highland 1 | Troubleshoot FM419. Reset hydraulic station. Start and monitor turbine. | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-06 | EmergStop MI Activated | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.7833 | Highland 1 | Adjusted inductive sensors and counting ring | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-07 | No work order description provided by contractor | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 2.05 | Forced |  |  | 4.8667 | Highland 1 | Removed old door louver plastic. Installed new door louver retrofit. | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-08 | No work order description provided by contractor | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 2.05 | Forced |  |  | 4.8667 | Highland 1 | Removed old door louver plastic. Installed new door louver retrofit. | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-09 | WTG System ok | 2011-07-14 | 2011-07-14 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 8.5 | Forced |  |  | 4.8667 | Highland 1 | spiral rap retro | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-10 | No work order description provided by contractor | 2011-07-14 | 2011-07-14 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 2.9 | Planned |  |  | 0.25 | Highland 1 | Change out UPS. Start and monitor turbine. | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110714-11 | No work order description provided by contractor | 2011-07-14 | 2011-07-14 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 2.9 | Planned |  |  | 0.25 | Highland 1 | Change out UPS. Start and monitor turbine. | KRAYN-WKO-NDX-20110714 | 1
KRAYN-WKO-NDX-20110715-01 | US_HIGHLAND_21WEA80828_Scuffed Yaw Disc | 2011-07-15 | 2011-07-15 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.030556 | Highland 1 | Scuff yaw disc for customer | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-02 | US-HIGHLAND-15WEA8082207_Scuff Disc | 2011-07-15 | 2011-07-15 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.072917 | Forced |  |  | 0.047222 | Highland 1 | Scuff yaw disc for customer | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-03 | US-HIGHLAND_05WEA80812_Scuffed Yaw Disc | 2011-07-15 | 2011-07-15 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.054167 | Highland 1 | Scuff yaw disc for customer | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-04 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 4.1667 | Planned |  |  | 1.3 | Highland 1 | Vacume carbon dust out of each yaw brake caliper. Clean yaw disc. Scuffed yaw disc with 80 grit grinding wheel. Yawed turbine CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-05 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 1.3833 | Highland 1 | Vacume carbon dust out of each yaw brake caliper. Clean yaw disc. Scuff yaw disc with 80 grit grinding wheel. Yaw turbine CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-06 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 1.3833 | Highland 1 | Vacume carbon dust out of each yaw brake caliper. Clean yaw disc. Scuff yaw disc with 80 grit grinding wheel. Yaw turbine CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-07 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 2.8333 | Planned |  |  | 0.9 | Highland 1 | Vacumed carbon dust out of each yaw brake caliper. Cleaned yaw dics. Scuff yaw disc with 80 grit grinding wheel. Yaw CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-08 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 1.1167 | Highland 1 | Vacumed Carbon dust out of each yaw brake. Clean yaw disc. Scuff yaw disc with 80 grit grinding wheel. Yaw CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-09 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 4.1667 | Planned |  |  | 1.3 | Highland 1 | Vacume carbon dust out of each yaw brake caliper. Clean yaw disc. Scuffed yaw disc with 80 grit grinding wheel. Yawed turbine CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110715-10 | No work order description provided by contractor | 2011-07-15 | 2011-07-15 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 1.25 | Highland 1 | Vacumed carbon dust out of each yaw brake caliper. Cleaned yaw disc. Scuff yaw disc with 80 grit grinding wheel. Yaw CW and CCW. | KRAYN-WKO-NDX-20110715 | 1
KRAYN-WKO-NDX-20110718-01 | US-HIGHLAND-WEA80820 ALU relay | 2011-07-18 | 2011-07-18 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.041667 | Forced | KRAYN-NDX-PRT-0105,0,0 | 3,1,1 | 0.30903 | Highland 1 | move 104 k1 and replace 156 k8,k9,k10 with new contactors | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-02 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.020833 | Forced | KRAYN-NDX-PRT-0883 | 4 | 0.30903 | Highland 1 | Install slow speed counting ring and inductive sensors on slow and high speed shaft | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-03 | US_HIGHLAND_13WEA80820_Door Louver | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.10417 | Forced | KRAYN-NDX-PRT-0257 | 40 | 0.30903 | Highland 1 | install door louver on main door for weather | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-04 | US-HIGHLAND-WEA80820 Condensate Drain | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0.30903 | Highland 1 | Install drip pan on top box | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-05 | US_Highland_3875/4374_Prevention of Wate | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.16667 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0.30903 | Highland 1 | Install rotor cover, yaw skirt and yaw stack coumers | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-06 | US-HIGHLAND-13WEA80820_ZargesLoopProtect | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.30903 | Highland 1 | wrap LV cables with panduate and install chaffing ring | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-07 | US_HIGHLAND_01WEA80808_Scuffed Yaw Disc | 2011-07-18 | 2011-07-18 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.041667 | Highland 1 | Scuffed the yaw disc per customer request | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-08 | US_Highland_02WEA80809_Scuff yaw disc | 2011-07-18 | 2011-07-18 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 0.0625 | Forced |  |  | 0.048611 | Highland 1 | Scuffed yaw disk per customer's request | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-09 | US-HIGHLAND_03WEA80810_Scuffed Yaw Disc | 2011-07-18 | 2011-07-18 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.076389 | Forced |  |  | 0.065972 | Highland 1 | Scuff yaw disc per customer request | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-10 | US-HIGHLAND_03WEA80810_Scuffed Yaw Disc | 2011-07-18 | 2011-07-18 | KRAYN-WTG03 | General Maintenance | Nordex USA OandM | 0.45139 | Forced |  |  | 0.12847 | Highland 1 | Scuff yaw disc per customer request | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-11 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 3.3333 | Planned |  |  | 1.0833 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-12 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 5.3333 | Planned |  |  | 1.4 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-13 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 1.0333 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-14 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 2.8333 | Planned |  |  | 1.1667 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-15 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 3.6667 | Planned |  |  | 1.55 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-16 | WTG System ok | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 20 | Planned |  |  | 7.4167 | Highland 1 | Took off the 5th yaw brake caliper from the right. Replaced it with a new one and changed the brake pads to the left and right of the new caliper. Found 6 caliper bolts that where not torqued to spec. Went through all caliper bolts to make sure that they where torqued to spec. cleaned up mess. | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-17 | WTG System ok | 2011-07-18 | 2011-07-18 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 20 | Planned |  |  | 7.4167 | Highland 1 | Took off the 5th yaw brake caliper from the right. Replaced it with a new one and changed the brake pads to the left and right of the new caliper. Found 6 caliper bolts that where not torqued to spec. Went through all caliper bolts to make sure that they where torqued to spec. cleaned up mess. | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-18 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 3.3333 | Planned |  |  | 1.0667 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-19 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 3.3333 | Forced |  |  | 1.0667 | Highland 1 | Vacuumed each yaw brake caliper. Cleaned yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW. | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-20 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 5.3333 | Planned |  |  | 1.4 | Highland 1 | Vacumed each yaw brake caliper. Cleaned Yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-21 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 4 | Forced |  |  | 1.4 | Highland 1 | Vacuumed each yaw brake caliper. Cleaned yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW. | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110718-22 | No work order description provided by contractor | 2011-07-18 | 2011-07-18 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 4.3333 | Forced |  |  | 1.0833 | Highland 1 | Vacuumed each yaw brake caliper. Cleaned yaw disc. Grind yaw disc using 80 grit grinding wheel. Yawed turbine CW and CCW. | KRAYN-WKO-NDX-20110718 | 1
KRAYN-WKO-NDX-20110719-01 | US_5_A_25_4744 Repl. of PLC - ALU relay | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.27083 | Forced | KRAYN-NDX-PRT-0105,KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0960 | 3,1,1 | 0.45278 | Highland 1 | Move 104k1 and replace 156 k8,k9,k10 with new contactors | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-02 | US_4330/4779_Rotor Overspeed Monitoring | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.020833 | Forced | KRAYN-NDX-PRT-0883 | 2 | 0.45278 | Highland 1 | install slow speed counting ring and new inductive sensors | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-03 | US_HIGHLAND_14WEA80821_Door Louver | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.048611 | Forced |  |  | 0.24306 | Highland 1 | Door louver retro | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-04 | US_5_A_25_5634 Condensate Drain Topbox | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.020833 | Forced |  |  | 0.24236 | Highland 1 | Install drip pan on top box | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-05 | US_Highland_3875/4374_Prevention of Wate | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.16667 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0.45278 | Highland 1 | Install rotor cover, yaw skirt, and coumings edges | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-06 | US-HIGHLAND-14WEA80821_ZargesLoopProtect | 2011-07-19 | 2011-07-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 0.083333 | Forced |  |  | 0.17986 | Highland 1 | Spiral wrap LV cables with panduat, install chaffing ring | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110719-07 | WTG Manual Stop | 2011-07-19 | 2011-07-19 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 11.1 | Forced | KRAYN-NDX-PRT-0568 | 1 | 11.05 | Highland 1 | Wtg 10 was having a RPM issue. Nordex techs went uptower to trouble shoot. The troubleshooting included checking the wires, check sheild and check the control modules. Techs then noticed they could not communicate with the controller for rpm monitors. | KRAYN-WKO-NDX-20110719 | 1
KRAYN-WKO-NDX-20110720-01 | HIGHLAND_14WEA80821_FM171 | 2011-07-20 | 2011-07-22 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 1.125 | Forced |  |  | -0.49167 | Highland 1 | Troubleshoot and replace pheonix contactor 155k5 | KRAYN-WKO-NDX-20110720 | 1
KRAYN-WKO-NDX-20110720-02 | No work order description provided by contractor | 2011-07-20 | 2011-07-20 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 6 | Forced |  |  | 6.2333 | Highland 1 | Customer Request. Up tower with customer to go over yaw disc scuff procedure. Check pressure of yaw, Adjust yaw pressure to 22 bar. Vacume each yaw caliper, clean yaw disc, scuff disc with 80 grit sanding wheel. Yaw turbine CW and CCW. | KRAYN-WKO-NDX-20110720 | 1
KRAYN-WKO-NDX-20110720-03 | Air Temp CtrlCab H Stop | 2011-07-20 | 2011-07-20 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 1.7 | Highland 1 | Fan Breaker 104F2 tripped in top box. Reset breaker, reset cooling unit. Wait for cabinet temp to drop below 45 degrees celsius, reset and start turbine. | KRAYN-WKO-NDX-20110720 | 1
KRAYN-WKO-NDX-20110721-01 | US_HIGHLAND_12WEA80819_FM 419 Yaw Hyd Br | 2011-07-21 | 2011-07-21 | KRAYN-WTG12 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.089583 | Highland 1 | Drain and cycle hyde station, reset turbine | KRAYN-WKO-NDX-20110721 | 1
KRAYN-WKO-NDX-20110721-02 | US_LM 43.8 breaking bolts_WTG80808 | 2011-07-21 | 2011-07-21 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.29861 | Forced |  |  | 0.21528 | Highland 1 | Blade bolt repair. | KRAYN-WKO-NDX-20110721 | 1
KRAYN-WKO-NDX-20110721-03 | No work order description provided by contractor | 2011-07-21 | 2011-07-21 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 21 | Forced |  |  | 5.1833 | Highland 1 | Blaid bolt repair. Remove blade bolts, ream out lightning grounding plate. Flip blade bolts, put back in and torque to 357 bar. | KRAYN-WKO-NDX-20110721 | 1
KRAYN-WKO-NDX-20110721-04 | Gear OilPress GearInlt L Stopp | 2011-07-21 | 2011-07-21 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 6 | Forced |  |  | 1.25 | Highland 1 | WTG 14 has a FM 171. techs went up tower and did the following. Checked all connection in the loop for 155k5, then found 2 loose milli-amp wires in the terminal strip for signal coming back from pressure sensor. The techs then noticed the a/c unit was set to 131 degrees change that back down to nordex specs. after that the techs then sawpped the relay with another relay. turbine will be watched | KRAYN-WKO-NDX-20110721 | 1
KRAYN-WKO-NDX-20110722-01 | US_HIGHLAND_16WEA80823_Cabinet Over Temp | 2011-07-22 | 2011-07-22 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.070139 | Highland 1 | Adjusted AC thermastat and restarted turbine | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-02 | US_HIGHLAND_10WEA80817_FM 54 MI e-stop | 2011-07-22 | 2011-07-22 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.27083 | Forced | KRAYN-NDX-PRT-0883 | 4 | 0.24097 | Highland 1 | FM 54: Replaced 4 inductive sensors, reset pepper and fooks, reset turbine | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-03 | US_HIGHLAND_10WEA80817_FM 54 MI e-stop | 2011-07-22 | 2011-07-22 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.26042 | Forced | KRAYN-NDX-PRT-0883 | 4 | 1.0583 | Highland 1 | FM 54: Replaced 4 inductive sensors, reset pepper and fooks, reset turbine | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-04 | US_HIGHLAND_04WEA80811_FM 419 Yaw Hyd Br | 2011-07-22 | 2011-07-23 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | -0.47847 | Highland 1 | Drain and cycle hyde station and reset turbine | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-05 | US_HIGHLAND_04WEA80811_FM 419 Yaw Hyd Br | 2011-07-22 | 2011-07-22 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.45833 | Forced |  |  | 0.28403 | Highland 1 | Replaced yaw brake hyde station solenoid with parted out defective part | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-06 | No work order description provided by contractor | 2011-07-22 | 2011-07-22 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 2.2833 | Highland 1 | Vacume carbon dust out of each yaw brake caliper. Clean yaw disc. Scuff yaw disc with 80 grit grinding wheel. Yaw turbine CW and CCW. | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110722-07 | WTG Manual Stop | 2011-07-22 | 2011-07-22 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 3 | Planned | KRAYN-NDX-PRT-0111 | 1 | 1 | Highland 1 | Change out the control board inside the UPS | KRAYN-WKO-NDX-20110722 | 1
KRAYN-WKO-NDX-20110723-01 | US_HIGHLAND_15WEA80822_FM 420 Yaw Hyd Br | 2011-07-23 | 2011-07-23 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.125 | Forced |  |  | 0.17708 | Highland 1 | Drain and cycle hyde station and reset turbine | KRAYN-WKO-NDX-20110723 | 1
KRAYN-WKO-NDX-20110723-02 | US_HIGHLAND_01WEA80808_FM 414 Yaw Motor | 2011-07-23 | 2011-07-23 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.45833 | Forced | KRAYN-NDX-PRT-0488 | 1 | 0.53056 | Highland 1 | Adjust yaw brake micro switch to close brakes and reset turbine | KRAYN-WKO-NDX-20110723 | 1
KRAYN-WKO-NDX-20110723-03 | US_HIGHLAND_01WEA80808_FM 414 Yaw Motor | 2011-07-23 | 2011-07-23 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 0.29167 | Forced | KRAYN-NDX-PRT-0488 | 1 | 0.14583 | Highland 1 | Quantity | KRAYN-WKO-NDX-20110723 | 1
KRAYN-WKO-NDX-20110725-01 | Yaw HydBrk not closed | 2011-07-25 | 2011-07-25 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 3.8333 | Forced | KRAYN-NDX-PRT-0107 | 1 | 2.25 | Highland 1 | R&R relay for low side yaw pressure valve. | KRAYN-WKO-NDX-20110725 | 1
KRAYN-WKO-NDX-20110725-02 | SafetyChain Activated | 2011-07-25 | 2011-07-24 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 2.6 | Forced | KRAYN-NDX-PRT-0567 | 1 | 5.2 | Highland 1 | Nordex techs changed out the PepperL + Fuchs module for the speed collector. | KRAYN-WKO-NDX-20110725 | 1
KRAYN-WKO-NDX-20110726-01 | US_HIGHLAND_06WEA80813_Door Louver | 2011-07-26 | 2011-07-26 | KRAYN-WTG06 | General Maintenance | Nordex USA OandM | 0.041667 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.017361 | Highland 1 | Install dooor louver for weather purpose | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-02 | US_HIGHLAND_07WEA80814_Door Louver | 2011-07-26 | 2011-07-26 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 0.21875 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.025 | Highland 1 | Install dooor louver for weather purpose | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-03 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 3.8333 | Forced |  |  | 0.93333 | Highland 1 | Check yaw brake pressure while yawing (22.9 Bar). Inspect yaw motor brake cover for rubbing.Vacume carbon out of each yaw brake. Clean yaw disc. Scuff yaw disc using 80 Grit sanding disc. Yaw turbine CW and CCW to check for noise. | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-04 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 0.41667 | Highland 1 | Installed Drip Pan Retro | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-05 | WTG System ok | 2011-07-26 | 2011-07-26 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.56667 | Highland 1 | Drip pan | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-06 | WTG Manual Stop | 2011-07-26 | 2011-07-26 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 6.1333 | Forced |  |  | 1.5333 | Highland 1 | Scuff the yaw disc for customer | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-07 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 0.36667 | Highland 1 | Install the Drip Pan Retro | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-08 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 5.3333 | Forced |  |  | 1 | Highland 1 | Installed yaw seal grease retrofit. | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-09 | WTG System ok | 2011-07-26 | 2011-07-26 | KRAYN-WTG06 | Warranty Repair | Nordex USA OandM | 0.41667 | Forced |  |  | 0.41667 | Highland 1 | Drip pan | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-10 | WTG System ok | 2011-07-26 | 2011-07-26 | KRAYN-WTG06 | Warranty Repair | Nordex USA OandM | 1.1333 | Forced | KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0971,KRAYN-NDX-PRT-0972,KRAYN-NDX-PRT-0973,KRAYN-NDX-PRT-0974,KRAYN-NDX-PRT-0975,KRAYN-NDX-PRT-0929 | 1,2,2,4,4,4,2 | 0.41667 | Highland 1 | Prevention of water | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-11 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.6 | Highland 1 | Installed Drip Pan Retro | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-12 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG07 | General Maintenance | Nordex USA OandM | 10.3 | Forced | KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0971,KRAYN-NDX-PRT-0972,KRAYN-NDX-PRT-0973,KRAYN-NDX-PRT-0974,KRAYN-NDX-PRT-0975 | 1,2,2,4,4,4 | 0.6 | Highland 1 | Prevention of Water Retro, Comers, Rotor Cover | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-13 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 3.3333 | Forced |  |  | 0.86667 | Highland 1 | Check yaw brake pressure while yawing.(20.5 Bar) Vacume carbon out of each yaw brake. Clean yaw disc. Scuff yaw disc using 80 Grit sanding disc. Yaw turbine CW and CCW to check for noise. | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-14 | No work order description provided by contractor | 2011-07-26 | 2011-07-26 | KRAYN-WTG08 | General Maintenance | Nordex USA OandM | 3.3333 | Forced |  |  | 0.86667 | Highland 1 | Check yaw brake pressure while yawing.(20.5 Bar) Vacume carbon out of each yaw brake. Clean yaw disc. Scuff yaw disc using 80 Grit sanding disc. Yaw turbine CW and CCW to check for noise. | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110726-15 | WTG System ok | 2011-07-26 | 2011-07-26 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 0.73333 | Forced |  |  | 0.3 | Highland 1 | Drip Pan | KRAYN-WKO-NDX-20110726 | 1
KRAYN-WKO-NDX-20110727-01 | US-HIGHLAND-WEA80823 ALU relay | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 0.083333 | Forced | KRAYN-NDX-PRT-0105,0,0 | 3,1,2 | 0 | Highland 1 | Installed ALU retro | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-02 | US_HIGHLAND_17WEA80824_Door Louver | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.083333 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0 | Highland 1 | install door louver | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-03 | US_Highland_3875/4374_Prevention of Wate | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 0.20833 | Forced | 0,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929 | 1,40,2 | 0 | Highland 1 | Install prevention water | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-04 | No work order description provided by contractor | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 3.5 | Forced | KRAYN-NDX-PRT-0257 | 7 | 5.5833 | Highland 1 | Installed Door Louver | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-05 | No work order description provided by contractor | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.5833 | Highland 1 | Installed Drip Pan Retro | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-06 | No work order description provided by contractor | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0970,KRAYN-NDX-PRT-0971,KRAYN-NDX-PRT-0972,KRAYN-NDX-PRT-0974,KRAYN-NDX-PRT-0975,KRAYN-NDX-PRT-0975,KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929,KRAYN-NDX-PRT-0976 | 1,2,2,4,4,4,1,40,2,1 | 5.5833 | Highland 1 | prevention of water | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-07 | No work order description provided by contractor | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.5833 | Highland 1 | Tightened the Shaft Nut | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-08 | No work order description provided by contractor | 2011-07-27 | 2011-07-27 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 5.5833 | Highland 1 | Installed Zargas Cable Loop Retro | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-09 | WTG System ok | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 3.75 | Forced | KRAYN-NDX-PRT-0977 | 3 | 5.8333 | Highland 1 | ALU | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-10 | WTG System ok | 2011-07-27 |  | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 5.8333 | Highland 1 | Counting ring | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-11 | WTG System ok | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.8333 | Highland 1 | Drip Pan | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-12 | WTG System ok | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.8333 | Highland 1 | Shaft nut | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-13 | WTG System ok | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.8333 | Highland 1 | Top Box Bracket | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-14 | WTG System ok | 2011-07-27 | 2011-07-27 | KRAYN-WTG17 | General Maintenance | Nordex USA OandM | 11 | Forced |  |  | 5.8333 | Highland 1 | Zargus Cable Loop retro | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-15 | MI class B Fault | 2011-07-27 | 2011-08-01 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 9.25 | Forced |  |  | 116.8 | Highland 1 | Troubleshot SEG fault. Checked gen rotor encoder and all wiring for ti with no defect noted at this time. | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-16 | MI class B Fault | 2011-07-27 | 2011-08-01 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 9.25 | Forced |  |  | 116.8 | Highland 1 | Troubleshot SEG fault. Checked gen rotor encoder and all wiring for ti with no defect noted at this time. | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110727-17 | WTG System ok | 2011-07-27 | 2011-08-02 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 3.65 | Highland 1 | Drip Pan | KRAYN-WKO-NDX-20110727 | 1
KRAYN-WKO-NDX-20110728-01 | MI class B Fault | 2011-07-28 | 2011-08-01 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 24 | Forced |  |  | 116.8 | Highland 1 | Troubleshot SEG fault. Replaced gen encoder with no fix, rechecked all wiring at encoder, in top box, down the tower, and in SEG box. All shielding was good and all of the wires rang good. Still no defects noted at this time. Had lightining on site had to leave. | KRAYN-WKO-NDX-20110728 | 1
KRAYN-WKO-NDX-20110729-01 | MI class B Fault | 2011-07-29 | 2011-08-01 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 18.5 | Forced |  |  | 116.8 | Highland 1 | Troubleshot SEG fault. R&R HUR trying 5 different HUR's from stock. NO fix but found resistor faulty on encoder plug on HUR. Had lightining move in and had to leave site. | KRAYN-WKO-NDX-20110729 | 1
KRAYN-WKO-NDX-20110730-01 | MI class B Fault | 2011-07-30 | 2011-08-01 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 9 | Forced |  |  | 116.8 | Highland 1 | Troubleshot SEG fault. Installed resistor. Could not commision HUR. | KRAYN-WKO-NDX-20110730 | 1
KRAYN-WKO-NDX-20110801-01 | No work order description provided by contractor | 2011-08-01 | 2011-08-01 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 10.6333 | Highland 1 | Drilled broken blade stud in blade 1. Worked along with 3 Energyworks techs Chris King, Jeff Burcham, and Randy Wigginton. | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-02 | WTG Manual Stop | 2011-08-01 | 2011-08-01 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 1.3333 | Forced |  |  | 1.8 | Highland 1 | Techs went up tower to investigate and work with engineers. Then got called down for lightning so techs did a quick check of a module and sparayed some cleaner on it. | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-03 | No work order description provided by contractor | 2011-08-01 | 2011-08-01 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 8.65 | Highland 1 | Installed Counting Ring Retro | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-04 | WTG System ok | 2011-08-01 |  | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1 | Forced |  |  | 8.65 | Highland 1 | Drip Pan Retro | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-05 | No work order description provided by contractor | 2011-08-01 | 2011-08-01 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 10.6333 | Highland 1 | Install door louver | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-06 | No work order description provided by contractor | 2011-08-01 |  | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929,KRAYN-NDX-PRT-0965 | 1,40,2,1 | 10.6333 | Highland 1 | prevention of water | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-07 | No work order description provided by contractor | 2011-08-01 |  | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 0 | Forced | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0257,KRAYN-NDX-PRT-0929,KRAYN-NDX-PRT-0965 | 1,40,2,1 | 10.6333 | Highland 1 | prevention of water | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-08 | No work order description provided by contractor | 2011-08-01 | 2011-08-01 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 7 | Forced |  |  | 10.6333 | Highland 1 | Tighted Down The Shaftnut on WTG 11 | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-09 | WTG System ok | 2011-08-01 | 2011-08-01 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 15.5 | Forced |  |  | 10.6333 | Highland 1 | Wrapped spiral wrap on cables coming through yaw deck. | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110801-10 | ALU GenBearPmp Fault | 2011-08-01 | 2011-08-01 | KRAYN-WTG | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 5.8333 | Highland 1 | Checked wiring on ALU relay found wire in wrong terminal | KRAYN-WKO-NDX-20110801 | 1
KRAYN-WKO-NDX-20110802-01 | No work order description provided by contractor | 2011-08-02 | 2011-08-02 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 9.25 | Forced |  |  | 6.95 | Highland 1 | Removed broken blade stud in blade 1. Worked along with 3 Energyworks techs Chris King, Jeff Burcham, and Randy Wigginton. | KRAYN-WKO-NDX-20110802 | 1
KRAYN-WKO-NDX-20110803-01 | EmergStop MI Activated | 2011-08-03 | 2011-08-03 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 6.3 | Planned | KRAYN-NDX-PRT-0570 | 1 | 2.3333 | Highland 1 | Trouble shoot Saftey chain | KRAYN-WKO-NDX-20110803 | 1
KRAYN-WKO-NDX-20110803-02 | EmergStop MI Activated | 2011-08-03 | 2011-08-03 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 6.3 | Planned | KRAYN-NDX-PRT-0570 | 1 | 2.3333 | Highland 1 | Trouble shoot Saftey chain | KRAYN-WKO-NDX-20110803 | 1
KRAYN-WKO-NDX-20110803-03 | No work order description provided by contractor | 2011-08-03 | 2011-08-03 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 4.0833 | Highland 1 | Visual inspection of front planetary gears in the gearbox. Performed with Everpower crew of Brad Foy and Robert Warner. | KRAYN-WKO-NDX-20110803 | 1
KRAYN-WKO-NDX-20110803-04 | No work order description provided by contractor | 2011-08-03 | 2011-08-03 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 2 | Forced |  |  | 4.95 | Highland 1 | Installed new Counting Ring Retro | KRAYN-WKO-NDX-20110803 | 1
KRAYN-WKO-NDX-20110804-01 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 1.3333 | Forced | KRAYN-NDX-PRT-0257 | 7 | 116.8 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-02 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 1.6667 | Forced | KRAYN-NDX-PRT-0257 | 7 | 1 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-03 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0257 | 7 | 1.3 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-04 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.46667 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-05 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0257 | 7 | 0.86667 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-06 | No work order description provided by contractor | 2011-08-04 | 2011-08-04 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 11.5 | Forced |  |  | 11.2833 | Highland 1 | Boroscope inspection of the gearbox. Performed with Energyworks crew of Jeff and Randy. | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-07 | No work order description provided by contractor | 2011-08-04 |  | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0257 | 7 | 11.2833 | Highland 1 | Installed Door Louver Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-08 | WTG System ok | 2011-08-04 |  | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 5 | Forced |  |  | 4.95 | Highland 1 | ALU Retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110804-09 | WTG System ok | 2011-08-04 | 2011-08-04 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 3.0333 | Forced |  |  | 3.65 | Highland 1 | ALU retro | KRAYN-WKO-NDX-20110804 | 1
KRAYN-WKO-NDX-20110805-01 | No work order description provided by contractor | 2011-08-05 | 2011-08-05 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 8.5 | Forced |  |  | 7.4667 | Highland 1 | Flipped blade bolts with energyworks crew of Jeff, Randy, and Chris. | KRAYN-WKO-NDX-20110805 | 1
KRAYN-WKO-NDX-20110805-02 | No work order description provided by contractor | 2011-08-05 |  | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 0.33333 | Forced | KRAYN-NDX-PRT-0883 | 4 | 116.8 | Highland 1 | inductive sensor | KRAYN-WKO-NDX-20110805 | 1
KRAYN-WKO-NDX-20110807-01 | Yaw SensTrack 2(0&deg | 2011-08-07 | 2011-08-13 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 126.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110807 | 1
KRAYN-WKO-NDX-20110808-01 | No work order description provided by contractor | 2011-08-08 | 2011-08-12 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 9.75 | Planned |  |  | 127.3667 | Highland 1 | Broken blade bolt extraction with Energy Works | KRAYN-WKO-NDX-20110808 | 1
KRAYN-WKO-NDX-20110809-01 | No work order description provided by contractor | 2011-08-09 |  | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 27.75 | Forced |  |  | 8.8333 | Highland 1 | Flipped blade bolts with Energyworks crew of Jeff, Randy and Chris. | KRAYN-WKO-NDX-20110809 | 1
KRAYN-WKO-NDX-20110809-02 | No work order description provided by contractor | 2011-08-09 | 2011-08-09 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.25 | Forced |  |  | 1.2833 | Highland 1 | Scuff yaw disc for Ever power ( Also took oil sample- SO# 600029791- only took 2 min) | KRAYN-WKO-NDX-20110809 | 1
KRAYN-WKO-NDX-20110809-03 | No work order description provided by contractor | 2011-08-09 | 2011-08-09 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 0.9 | Highland 1 | Scuff yaw disc for Ever Power ( Also took oil sample- SO# 600029792- only took 2 min) | KRAYN-WKO-NDX-20110809 | 1
KRAYN-WKO-NDX-20110809-04 | No work order description provided by contractor | 2011-08-09 | 2011-08-09 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 0.88333 | Highland 1 | Scuff yaw disc for Ever power ( Also took oil sample-SO# 600029794- only took 2 min) | KRAYN-WKO-NDX-20110809 | 1
KRAYN-WKO-NDX-20110810-01 | No work order description provided by contractor | 2011-08-10 |  | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 25 | Forced |  |  | 11.75 | Highland 1 | Flipped blade bolts with energyworks crew of Jeff, Randy and Chris. | KRAYN-WKO-NDX-20110810 | 1
KRAYN-WKO-NDX-20110811-01 | US_HIGHLAND_20WEA80827_Scuffed Yaw Disc | 2011-08-11 | 2011-08-11 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.09375 | Forced |  |  | 0.09375 | Highland 1 | Scuffed yaw disc to customers request | KRAYN-WKO-NDX-20110811 | 1
KRAYN-WKO-NDX-20110811-02 | No work order description provided by contractor | 2011-08-11 |  | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 26 | Forced | KRAYN-NDX-PRT-0959 | 10 | 8.8333 | Highland 1 | Flipped and replaced blade bolts. Replaced bolts 34 and 37 in blade 1. Replaced bolts 29, 30, and 33 in blade 2. Replaced 1,33,34,62, and 63 in blade 3. Work was performed with energyworks crew of Jeff, Randy and Chris. | KRAYN-WKO-NDX-20110811 | 1
KRAYN-WKO-NDX-20110812-01 | No work order description provided by contractor | 2011-08-12 |  | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 7.75 | Forced |  |  | 8.8333 | Highland 1 | Finished flipping blade bolts. Work was performed with energyworks crew of Jeff, Randy and Chris. | KRAYN-WKO-NDX-20110812 | 1
KRAYN-WKO-NDX-20110812-02 | Yaw SensTrack 2(0&deg | 2011-08-12 | 2011-08-13 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 78 | Forced |  |  | 126.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110812 | 1
KRAYN-WKO-NDX-20110814-01 | Yaw SensTrack 2(0&deg | 2011-08-14 | 2011-08-13 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 126.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110814 | 1
KRAYN-WKO-NDX-20110815-01 | LP (LightnProt) Gen | 2011-08-15 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 2.3667 | Highland 1 | Client repair grid damaged turbine. | KRAYN-WKO-NDX-20110815 | 1
KRAYN-WKO-NDX-20110815-02 | No work order description provided by contractor | 2011-08-15 |  | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 14.5 | Forced |  |  | 0.46667 | Highland 1 | Drilled broken blade bolt in blade 3. Work performed with Energyworks crew of Randy, Adam,and Masion. | KRAYN-WKO-NDX-20110815 | 1
KRAYN-WKO-NDX-20110816-01 | No work order description provided by contractor | 2011-08-16 |  | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 0.3 | Highland 1 | Paint touch ups. Secured various cables. Discovered many problems that had been fixed but had not been reported. | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-02 | No work order description provided by contractor | 2011-08-16 | 2011-08-16 | KRAYN-WTG12 | Warranty Repair | Nordex USA OandM | 2 | Forced |  |  | 2 | Highland 1 | punch list | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-03 | LP (LightnProt) Gen | 2011-08-16 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 10 | Forced |  |  | 2.3667 | Highland 1 | Client repair of grig damaged turbine. | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-04 | No work order description provided by contractor | 2011-08-16 | 2011-08-17 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 54.3667 | Highland 1 | Broken blade bolt extraction with Energy Works | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-05 | No work order description provided by contractor | 2011-08-16 |  | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 9.75 | Forced | KRAYN-NDX-PRT-0959 | 1 | 54.3667 | Highland 1 | Remove broken blade bolt from blade 3 position 33 with Energyworks. Installed new bolt and performed flipping on the adjacent 2 and three studs 180 degrees opposite. | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-06 | No work order description provided by contractor | 2011-08-16 | 2011-08-16 | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 0.5 | Highland 1 | COUNTING RING | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-07 | No work order description provided by contractor | 2011-08-16 | 2011-08-05 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 0.5 | Highland 1 | Generator cables were wrapped with panduit. | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-08 | Vib Z-direction eff. Stop | 2011-08-16 |  | KRAYN-WTG21 | General Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0172 | 1 | 0.5 | Highland 1 | R&R viberation sensor by the maintenance door under gearbox. | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110816-09 | No work order description provided by contractor | 2011-08-16 | 2011-08-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 43.2833 | Highland 1 | Broken blade bolt extraction with Energy Works | KRAYN-WKO-NDX-20110816 | 1
KRAYN-WKO-NDX-20110817-01 | LP (LightnProt) Gen | 2011-08-17 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 15 | Forced |  |  | 2.3667 | Highland 1 | Client repair of grid damaged turbine. | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-02 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 43.2833 | Highland 1 | Broken blade bolt extraction with Energy Works | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-03 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 13.5 | Forced | KRAYN-NDX-PRT-0959 | 5 | 43.0333 | Highland 1 | Drilled broken bolt but was unable to remove it from blade 1 position 33 and installed new bolt in position 1 blade 1 which was previously removed. Flipped bolts 32, 34, 2,and replaced bolts in positions 33 and 64 because of damaged threads, in blade 2 due to broken bolt in position 1. Could not drill or removed bolt in position 1 blade 2 due to broken tooling. Later recieved the proper tooling and removed bolt from position 33 blade 1. This work was performed with energy works crew of Randy, Adam, and Masion. | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-04 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 43.2833 | Highland 1 | Install drip pan | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-05 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 43.2833 | Highland 1 | Tighten shaft nut | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-06 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 43.2833 | Highland 1 | Install top box brackets | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-07 | No work order description provided by contractor | 2011-08-17 | 2011-08-18 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0929 | 2 | 43.2833 | Highland 1 | Install rotor cover and coumers | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110817-08 | GenRot RpmDiff H Stop | 2011-08-17 | 2011-08-17 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0883 | 1 | 4.6833 | Highland 1 | Replaced defective inductive sensor / Drained and cycle hyde station and checked rotor brake solinoid | KRAYN-WKO-NDX-20110817 | 1
KRAYN-WKO-NDX-20110818-01 | LP (LightnProt) PwrCab | 2011-08-18 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 51 | Forced | KRAYN-NDX-PRT-0122,KRAYN-NDX-PRT-0359,KRAYN-NDX-PRT-0644,KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0650,0,KRAYN-NDX-PRT-0648,KRAYN-NDX-PRT-0487,KRAYN-NDX-PRT-0668,KRAYN-NDX-PRT-0091,KRAYN-NDX-PRT-0180 | 3,3,3,3,1,3,3,3,1,3,1 | 2.3667 | Highland 1 | Client repair of grid damaged turbine. | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-02 | No work order description provided by contractor | 2011-08-18 | 2011-08-19 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0959 | 1 | 9.9667 | Highland 1 | Drilled and removed bolt from blade 1 position 32. Installed new bolt. Flipped surrounding bolts 31 and 33. Work performed with energyworks crew of Randy, Adam, and Masion. | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-03 | WTG System ok | 2011-08-18 | 2011-08-19 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 2.2167 | Forced |  |  | 7.2167 | Highland 1 | Blade Bolt Crew | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-04 | WTG System ok | 2011-08-18 | 2011-08-18 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 10.75 | Highland 1 | ALU Retro | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-05 | No work order description provided by contractor | 2011-08-18 |  | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 10.75 | Highland 1 | Broken blade bolt extraction with Energy Works | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-06 | WTG System ok | 2011-08-18 | 2011-08-18 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 5 | Forced |  |  | 10.75 | Highland 1 | Blade Bolt Crew | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-07 | WTG System ok | 2011-08-18 | 2011-08-18 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 4.5 | Forced |  |  | 10.75 | Highland 1 | Cable Wrap Retro | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110818-08 | No work order description provided by contractor | 2011-08-18 | 2011-08-18 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 5.75 | Forced | KRAYN-NDX-PRT-0959 | 1 | 43.0333 | Highland 1 | Drilled and removed broken bolt from position 1 in blade 2. Installed new bolt. | KRAYN-WKO-NDX-20110818 | 1
KRAYN-WKO-NDX-20110819-01 | SafetyChain Activated | 2011-08-19 | 2011-08-19 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 2.6167 | Highland 1 | Reset Fuse 104f4 | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-02 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.25 | Highland 1 | drip pan | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-03 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 1.5833 | Forced |  |  | 0.25 | Highland 1 | torque shafe nut | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-04 | IBS peripherals Fault | 2011-08-19 | 2011-08-20 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 27.8333 | Forced | KRAYN-NDX-PRT-0045 | 4 | 5.1333 | Highland 1 | Troubleshoot interbus system. Replace fuse on 105A2 and 105A3, flip tripped breaker 104f3. Releive pressure on hydraulic station to release rotor brake. Bring pressure back up on hydraulic station and test rotor brake. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-05 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG14 | General Maintenance | Nordex USA OandM | 5.1667 | Forced | KRAYN-NDX-PRT-0959 | 1 | 10.2333 | Highland 1 | Drilled broken blade bolt in position 32 in blade 1. Flipped bolt in position 33 and found that the bolt in position 31 was also broken in blade 1. Drilled bolt from position 31 in blade 1. Work performed with energy works crew of Randy, Adam, and Marsion. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-06 | LP (LightnProt) PwrCab | 2011-08-19 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 11 | Forced |  |  | 2.3667 | Highland 1 | Client repair of grid damaged turbine. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-07 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG18 | General Maintenance | Nordex USA OandM | 3.1667 | Forced |  |  | 9.9667 | Highland 1 | Flipped blade bolts 63, 64, and 1 in blade 1 due to broken blade bolt in blade 1 position 32. Work performed with energyworks crew of Randy, Adam, and Masion. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-08 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 2 | Planned | KRAYN-NDX-PRT-0961 | 1 | 3.9167 | Highland 1 | Swapped new counting ring for old. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-09 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned | KRAYN-NDX-PRT-0961 | 2 | 3.9167 | Highland 1 | Hydac and Gearbox oil samples taken. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-10 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 1 | Planned | KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0961,KRAYN-NDX-PRT-0961 | 1,2,2 | 3.9167 | Highland 1 | Installed rotor rain cover. | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-11 | WTG System ok | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 5.1667 | Forced |  |  | 3.75 | Highland 1 | Cable Wrap | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-12 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.25 | Highland 1 | drip pan | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-13 | No work order description provided by contractor | 2011-08-19 | 2011-08-19 | KRAYN-WTG20 | General Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 0.25 | Highland 1 | Yaw skirt water prevention retro, used a role of yaw skirting | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110819-14 | WTG System ok | 2011-08-19 | 2011-08-19 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 2.95 | Forced |  |  | 2.4833 | Highland 1 | Stop and Start Turbine for borescope | KRAYN-WKO-NDX-20110819 | 1
KRAYN-WKO-NDX-20110820-01 | IBS peripherals Fault | 2011-08-20 | 2011-08-19 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.3333 | Forced | KRAYN-NDX-PRT-0045 | 1 | 3.1667 | Highland 1 | Troubleshoot interbus system. Replace 5amp fuse on module 105A2 | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110820-02 | WTG System ok | 2011-08-20 |  | KRAYN-WTG15 | Warranty Repair | Nordex USA OandM | 2.5167 | Forced |  |  | 2.3667 | Highland 1 | Stop and start turbine for Bore Scope. Turbine was already down due to lightening on the 12th | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110820-03 | LP (LightnProt) PwrCab | 2011-08-20 | 2011-08-20 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 17.5 | Forced | KRAYN-NDX-PRT-0090,KRAYN-NDX-PRT-0668 | 1,1 | 118.9 | Highland 1 | Replace Q10p per SEG tech request. Replaced x33 supression diode that reads to high temp from transformer. | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110820-04 | WTG System ok | 2011-08-20 | 2011-08-21 | KRAYN-WTG15 | Warranty Repair | Nordex USA OandM | 5.3333 | Forced |  |  | 4.8333 | Highland 1 | Stop and start turbine for Bore Scope | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110820-05 | WTG System ok | 2011-08-20 | 2011-08-20 | KRAYN-WTG23 | General Maintenance | Nordex USA OandM | 7.4833 | Forced |  |  | 6.2333 | Highland 1 | Stop and Start Turbine for borescope | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110820-06 | IBS peripherals Fault | 2011-08-20 | 2011-08-20 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 2.3333 | Forced | KRAYN-NDX-PRT-0043 | 1 | 5.7 | Highland 1 | Troubleshoot interbus system. Replace fuse in 105A2. | KRAYN-WKO-NDX-20110820 | 1
KRAYN-WKO-NDX-20110821-01 | No work order description provided by contractor | 2011-08-21 |  | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 5.75 | Forced |  |  | 0.3 | Highland 1 | Moved tools up tower and locked out hub to locate broken blade bolt. Lock hub at appropriate position for bolt removal. It began to rain then lightening came in. Where down on lightening stand down from 21:30 to 24:00. | KRAYN-WKO-NDX-20110821 | 1
KRAYN-WKO-NDX-20110822-01 | No work order description provided by contractor | 2011-08-22 | 2011-08-22 | KRAYN-WTG04 | General Maintenance | Nordex USA OandM | 6.9167 | Forced | KRAYN-NDX-PRT-0959 | 2 | 10.6333 | Highland 1 | Drilled and removed broken blade bolt position 33 in blade 2. Flipped bolts 32, 34, 2, 64, and replaced bolt 1 due to damaged threads all in blade 2. | KRAYN-WKO-NDX-20110822 | 1
KRAYN-WKO-NDX-20110823-02 | WTG Manual Stop | 2011-08-23 | 2011-08-24 | KRAYN-WTG08 | Warranty Repair | Nordex USA OandM | 41.5 | Forced |  |  | 29.5667 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-03 | WTG Manual Stop | 2011-08-23 | 2011-08-24 | KRAYN-WTG08 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 29.5667 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-04 | WTG Manual Stop | 2011-08-23 | 2011-08-24 | KRAYN-WTG08 | Warranty Repair | Nordex USA OandM | 41.5 | Forced |  |  | 29.5667 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-05 | WTG Manual Stop | 2011-08-23 | 2011-08-23 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 4.4 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-06 | WTG Manual Stop | 2011-08-23 | 2011-08-23 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 4.4 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-07 | WTG Manual Stop | 2011-08-23 | 2011-08-23 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 4.4 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110823-09 | WTG Manual Stop | 2011-08-23 | 2011-08-24 | KRAYN-WTG08 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 29.5667 | Highland 1 |  | KRAYN-WKO-NDX-20110823 | 1
KRAYN-WKO-NDX-20110824-01 | MI class B Fault | 2011-08-24 | 2011-08-24 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.2167 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-02 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 5.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-03 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 9 | Forced |  |  | 5.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-04 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.9167 | Forced |  |  | 5.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-05 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 29.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-06 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 29.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110824-07 | WTG Manual Stop | 2011-08-24 | 2011-08-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.9167 | Forced |  |  | 5.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110824 | 1
KRAYN-WKO-NDX-20110825-01 | MI class B Fault | 2011-08-25 | 2011-08-25 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 2.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110825 | 1
KRAYN-WKO-NDX-20110825-02 | RotBrk AccuE_Press L Stopp | 2011-08-25 | 2011-08-25 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 5.3833 | Highland 1 |  | KRAYN-WKO-NDX-20110825 | 1
KRAYN-WKO-NDX-20110825-03 | yaw motor brake not closed | 2011-08-25 | 2011-08-25 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 3.15 | Highland 1 |  | KRAYN-WKO-NDX-20110825 | 1
KRAYN-WKO-NDX-20110826-01 | WTG Manual Stop | 2011-08-26 | 2011-08-26 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 12.1 | Forced |  |  | 3.1167 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-02 | WTG Manual Stop | 2011-08-26 | 2011-08-26 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-03 | No work order description provided by contractor | 2011-08-26 | 2011-08-26 | KRAYN-WTG15 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 1.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-04 | WTG Manual Stop | 2011-08-26 | 2011-08-26 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 3.1 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-05 | WTG Manual Stop | 2011-08-26 | 2011-08-26 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 0.33333 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-06 | Yaw MotBrake not closed | 2011-08-26 | 2011-08-26 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 2.1667 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110826-07 | No work order description provided by contractor | 2011-08-26 | 2011-08-26 | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.7833 | Highland 1 |  | KRAYN-WKO-NDX-20110826 | 1
KRAYN-WKO-NDX-20110829-01 | WTG Manual Stop | 2011-08-29 | 2011-08-30 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 3.1667 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-02 | WTG Manual Stop | 2011-08-29 | 2011-08-30 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 3.1667 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-03 | No work order description provided by contractor | 2011-08-29 | 2011-08-29 | KRAYN-WTG05 | Warranty Repair | Nordex USA OandM | 0.41667 | Forced |  |  | 2.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-04 | No work order description provided by contractor | 2011-08-29 | 2011-08-29 | KRAYN-WTG05 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 2.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-05 | WTG Manual Stop | 2011-08-29 | 2011-08-29 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 7.0333 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-06 | WTG Manual Stop | 2011-08-29 | 2011-08-29 | KRAYN-WTG23 | Warranty Repair | Nordex USA OandM | 3 | Forced |  |  | 7.0333 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-07 | No work order description provided by contractor | 2011-08-29 | 2011-08-29 | KRAYN-WTG23 | Warranty Repair | Nordex USA OandM | 0.13333 | Forced |  |  | 0.5 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-08 | WTG Manual Stop | 2011-08-29 | 2011-08-29 | KRAYN-WTG05 | Warranty Repair | Nordex USA OandM | 1.5 | Forced |  |  | 6.5 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110829-09 | WTG Manual Stop | 2011-08-29 | 2011-08-29 | KRAYN-WTG05 | Warranty Repair | Nordex USA OandM | 2.25 | Forced |  |  | 6.5 | Highland 1 |  | KRAYN-WKO-NDX-20110829 | 1
KRAYN-WKO-NDX-20110830-01 | WTG Manual Stop | 2011-08-30 | 2011-08-30 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 3 | Forced |  |  | 4.9667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-02 | Gear OilTemp Sump H Warn | 2011-08-30 | 2011-08-30 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 10.5 | Forced |  |  | 4.9667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-03 | No work order description provided by contractor | 2011-08-30 | 2011-08-30 | KRAYN-WTG01 | Warranty Repair | Nordex USA OandM | 0.25 | Forced |  |  | 4.9667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-04 | WTG Manual Stop | 2011-08-30 |  | KRAYN-WTG02 | Warranty Repair | Nordex USA OandM | 2.3333 | Forced |  |  | 126.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-05 | WTG Manual Stop | 2011-08-30 | 2011-08-30 | KRAYN-WTG03 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 2.15 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-06 | manual stop | 2011-08-30 | 2011-08-30 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 21 | Planned |  |  | 4.0667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-07 | MI class B Fault | 2011-08-30 | 2011-08-31 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 3.8833 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110830-08 | WTG Manual Stop | 2011-08-30 | 2011-08-30 | KRAYN-WTG15 | Warranty Repair | Nordex USA OandM | 8 | Forced |  |  | 4.0667 | Highland 1 |  | KRAYN-WKO-NDX-20110830 | 1
KRAYN-WKO-NDX-20110831-01 | WTG System ok | 2011-08-31 |  | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 9.9667 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-02 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-03 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.66667 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-04 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-05 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 7 | Forced |  |  | 4.25 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-06 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-07 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-08 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-09 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-10 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-11 | WTG Manual Stop | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-12 | No work order description provided by contractor | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 0.25 | Forced |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-13 | No work order description provided by contractor | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 0.16667 | Forced |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-14 | No work order description provided by contractor | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 0.25 | Forced |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110831-15 | No work order description provided by contractor | 2011-08-31 | 2011-08-31 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 0.16667 | Forced |  |  | 4.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110831 | 1
KRAYN-WKO-NDX-20110901-02 | WTG Manual Stop | 2011-09-01 | 2011-09-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 4.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110901 | 1
KRAYN-WKO-NDX-20110901-03 | WTG Manual Stop | 2011-09-01 | 2011-09-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 4.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110901 | 1
KRAYN-WKO-NDX-20110901-04 | WTG Manual Stop | 2011-09-01 | 2011-09-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 4.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110901 | 1
KRAYN-WKO-NDX-20110901-14 | WTG Manual Stop | 2011-09-01 | 2011-09-01 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 4.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110901 | 1
KRAYN-WKO-NDX-20110902-01 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 5.75 | Forced |  |  | 3.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-02 | No work order description provided by contractor | 2011-09-02 | 2011-09-02 | KRAYN-WTG10 | Warranty Repair | Nordex USA OandM | 0.16667 | Forced |  |  | 3.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-03 | No work order description provided by contractor | 2011-09-02 | 2011-09-02 | KRAYN-WTG10 | Warranty Repair | Nordex USA OandM | 0.33333 | Forced |  |  | 3.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-04 | No work order description provided by contractor | 2011-09-02 | 2011-09-02 | KRAYN-WTG10 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-05 | No work order description provided by contractor | 2011-09-02 | 2011-09-02 | KRAYN-WTG10 | Warranty Repair | Nordex USA OandM | 0.16667 | Forced |  |  | 3.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-06 | WTG Manual Stop | 2011-09-02 |  | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.1333 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-07 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 3.5167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-08 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG11 | Retrofit | Nordex USA OandM | 5.5 | Forced |  |  | 3.5167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-09 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG11 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 3.5167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-10 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG11 | Warranty Repair | Nordex USA OandM | 1.5 | Forced |  |  | 3.5167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-11 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG11 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.5167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-12 | Yaw HydBrk not closed | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 3.25 | Forced |  |  | 1.75 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-13 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 1.5333 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-14 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-15 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 0.83333 | Planned |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-16 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Warranty Repair | Nordex USA OandM | 1.25 | Forced |  |  | 1.5333 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-17 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Warranty Repair | Nordex USA OandM | 1.5 | Forced |  |  | 1.5333 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-18 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG12 | Warranty Repair | Nordex USA OandM | 1.25 | Forced |  |  | 1.5333 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-19 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 978918.5 | Forced |  |  | 2.8167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-20 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 3.65 | Planned |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-21 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110902-22 | WTG Manual Stop | 2011-09-02 | 2011-09-02 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 5 | Forced |  |  | 3.0167 | Highland 1 |  | KRAYN-WKO-NDX-20110902 | 1
KRAYN-WKO-NDX-20110903-01 | Air Temp CtrlCab H Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 1.6 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-02 | Air Temp CtrlCab H Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 0 | Forced |  |  | 2.7167 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-03 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 8.1 | Planned |  |  | 2.4 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-04 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 4.9 | Planned |  |  | 2.4 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-05 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 8.5 | Forced |  |  | 3.5 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-06 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1.25 | Forced |  |  | 3.3833 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-07 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 7.3 | Planned |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110903-08 | WTG Manual Stop | 2011-09-03 | 2011-09-03 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 2.3 | Planned |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20110903 | 1
KRAYN-WKO-NDX-20110904-01 | SafetyChain Activated | 2011-09-04 | 2011-09-05 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 6.6333 | Highland 1 |  | KRAYN-WKO-NDX-20110904 | 1
KRAYN-WKO-NDX-20110905-01 | No work order description provided by contractor | 2011-09-05 | 2011-09-05 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.78333 | Highland 1 |  | KRAYN-WKO-NDX-20110905 | 1
KRAYN-WKO-NDX-20110906-01 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-02 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-03 | WTG Manual Stop | 2011-09-06 |  | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-04 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-05 | WTG Manual Stop | 2011-09-06 |  | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-06 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-07 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 1 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-08 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-09 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.25 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-10 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.5 | Forced |  |  | 3.4167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-11 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 2.6167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-12 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 2.6167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-13 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG23 | Warranty Repair | Nordex USA OandM | 2.25 | Forced |  |  | 2.6167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-14 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 6.3333 | Forced |  |  | 2.4667 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-15 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 7.1667 | Forced |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-16 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-17 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 3 | Forced |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-18 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110906-19 | WTG Manual Stop | 2011-09-06 | 2011-09-06 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20110906 | 1
KRAYN-WKO-NDX-20110907-01 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 2.45 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-013 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG04 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-02 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 7.4 | Forced |  |  | 2.0333 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-03 | WTG Manual Stop | 2011-09-07 |  | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 2.0333 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-04 | WTG Manual Stop | 2011-09-07 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.2 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-05 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG04 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-06 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG04 | Warranty Repair | Nordex USA OandM | 3 | Forced |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-07 | MI class B Fault | 2011-09-07 | 2011-09-07 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 6.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-08 | Yaw HydBrk not closed | 2011-09-07 | 2011-09-07 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 4.2 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-09 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 2.3667 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-10 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG04 | Retrofit | Nordex USA OandM | 7 | Forced |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-11 | WTG Manual Stop | 2011-09-07 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.2 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110907-12 | WTG Manual Stop | 2011-09-07 | 2011-09-07 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20110907 | 1
KRAYN-WKO-NDX-20110908-01 | SafetyChain Activated | 2011-09-08 | 2011-09-09 | KRAYN-WTG01 | General Maintenance | Nordex USA OandM | 3 | Forced |  |  | 8.6667 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-02 | Pitch2 battery defect | 2011-09-08 | 2011-09-09 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 10 | Forced |  |  | 14.4333 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-03 | WTG Manual Stop | 2011-09-08 | 2011-08-08 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 3.5 | Forced |  |  | 1.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-04 | Gen CWPress L Stopp | 2011-09-08 | 2011-09-09 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 5 | Forced |  |  | 11.1167 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-05 | No work order description provided by contractor | 2011-09-08 | 2011-09-08 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 0.3 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-06 | WTG Manual Stop | 2011-09-08 | 2011-09-08 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 5.9 | Forced |  |  | 5.5833 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-07 | WTG Manual Stop | 2011-09-08 | 2011-09-08 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 6.5 | Forced |  |  | 10.8 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110908-08 | WTG Manual Stop | 2011-09-08 |  | KRAYN-WTG16 | Warranty Repair | Nordex USA OandM | 2.75 | Forced |  |  | 1.6167 | Highland 1 |  | KRAYN-WKO-NDX-20110908 | 1
KRAYN-WKO-NDX-20110909-01 | WTG Manual Stop | 2011-09-09 | 2011-09-09 | KRAYN-WTG06 | Warranty Repair | Nordex USA OandM | 5 | Forced |  |  | 3.1 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110909-02 | WTG Manual Stop | 2011-09-09 | 2011-08-09 | KRAYN-WTG07 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 2.9333 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110909-03 | WTG Manual Stop | 2011-09-09 | 2011-09-09 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.73333 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110909-04 | Yaw HydBrk not closed | 2011-09-09 | 2011-06-09 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.76667 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110909-05 | Yaw HydBrk not closed | 2011-09-09 | 2011-09-09 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.2333 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110909-06 | No work order description provided by contractor | 2011-09-09 | 2011-06-09 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0 | Highland 1 |  | KRAYN-WKO-NDX-20110909 | 1
KRAYN-WKO-NDX-20110912-01 | WTG Manual Stop | 2011-09-12 | 2011-09-12 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 5.5 | Forced |  |  | 1.5667 | Highland 1 |  | KRAYN-WKO-NDX-20110912 | 1
KRAYN-WKO-NDX-20110912-02 | WTG Manual Stop | 2011-09-12 | 2011-09-12 | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 7 | Forced |  |  | 4.3 | Highland 1 |  | KRAYN-WKO-NDX-20110912 | 1
KRAYN-WKO-NDX-20110912-03 | WTG Manual Stop | 2011-09-12 | 2011-09-12 | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 7 | Forced |  |  | 4.3 | Highland 1 |  | KRAYN-WKO-NDX-20110912 | 1
KRAYN-WKO-NDX-20110913-01 | WTG Manual Stop | 2011-09-13 | 2011-09-13 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 0.26667 | Highland 1 |  | KRAYN-WKO-NDX-20110913 | 1
KRAYN-WKO-NDX-20110913-02 | WTG Manual Stop | 2011-09-13 | 2011-09-13 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.75 | Planned |  |  | 0.43333 | Highland 1 |  | KRAYN-WKO-NDX-20110913 | 1
KRAYN-WKO-NDX-20110913-03 | WTG Manual Stop | 2011-09-13 | 2011-09-13 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2.1833 | Planned |  |  | 0.83333 | Highland 1 |  | KRAYN-WKO-NDX-20110913 | 1
KRAYN-WKO-NDX-20110913-04 | WTG Manual Stop | 2011-09-13 | 2011-09-13 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.1 | Planned |  |  | 0.31667 | Highland 1 |  | KRAYN-WKO-NDX-20110913 | 1
KRAYN-WKO-NDX-20110913-05 | WTG Manual Stop | 2011-09-13 | 2011-09-13 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 0.58333 | Planned |  |  | 0.35 | Highland 1 |  | KRAYN-WKO-NDX-20110913 | 1
KRAYN-WKO-NDX-20110914-01 | WTG Manual Stop | 2011-09-14 | 2011-09-14 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 22 | Forced |  |  | 7.2833 | Highland 1 |  | KRAYN-WKO-NDX-20110914 | 1
KRAYN-WKO-NDX-20110914-02 | WTG Manual Stop | 2011-09-14 | 2011-09-14 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 7.2833 | Highland 1 |  | KRAYN-WKO-NDX-20110914 | 1
KRAYN-WKO-NDX-20110914-03 | WTG Manual Stop | 2011-09-14 | 2011-09-14 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 7.2833 | Highland 1 |  | KRAYN-WKO-NDX-20110914 | 1
KRAYN-WKO-NDX-20110914-04 | WTG Manual Stop | 2011-09-14 | 2011-09-14 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 6.3333 | Planned |  |  | 2.3606 | Highland 1 |  | KRAYN-WKO-NDX-20110914 | 1
KRAYN-WKO-NDX-20110915-01 | MI class B Fault | 2011-09-15 | 2011-09-15 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.41667 | Highland 1 |  | KRAYN-WKO-NDX-20110915 | 1
KRAYN-WKO-NDX-20110915-02 | MI class B Fault | 2011-09-15 | 2011-09-15 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 5.75 | Planned |  |  | 4.5833 | Highland 1 |  | KRAYN-WKO-NDX-20110915 | 1
KRAYN-WKO-NDX-20110916-01 | Hyd OilLevel L Stopp | 2011-09-16 | 2011-09-16 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 8.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110916 | 1
KRAYN-WKO-NDX-20110916-02 | WTG Manual Stop | 2011-09-16 | 2011-09-16 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 1.55 | Forced |  |  | 0.58333 | Highland 1 |  | KRAYN-WKO-NDX-20110916 | 1
KRAYN-WKO-NDX-20110920-01 | No work order description provided by contractor | 2011-09-20 |  | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 6 | Forced |  |  | 8.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110920 | 1
KRAYN-WKO-NDX-20110920-02 | No work order description provided by contractor | 2011-09-20 |  | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 33 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20110920 | 1
KRAYN-WKO-NDX-20110920-03 | No work order description provided by contractor | 2011-09-20 | 2011-09-20 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.18333 | Highland 1 |  | KRAYN-WKO-NDX-20110920 | 1
KRAYN-WKO-NDX-20110920-04 | WTG Manual Stop | 2011-09-20 | 2011-09-20 | KRAYN-WTG24 | Warranty Repair | Nordex USA OandM | 3 | Forced |  |  | 2.85 | Highland 1 |  | KRAYN-WKO-NDX-20110920 | 1
KRAYN-WKO-NDX-20110921-01 | WTG Manual Stop | 2011-09-21 | 2011-09-21 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 3.25 | Forced |  |  | 1.7667 | Highland 1 |  | KRAYN-WKO-NDX-20110921 | 1
KRAYN-WKO-NDX-20110922-01 | WTG Manual Stop | 2011-09-22 | 2011-09-22 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.13333 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110922-02 | No work order description provided by contractor | 2011-09-22 |  | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 12 | Planned |  |  | 0.25 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110922-03 | Pitchangle 1 Diff.Set-Act | 2011-09-22 | 2011-09-22 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 8.4 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110922-04 | Pitchangle 1 Diff.Set-Act | 2011-09-22 | 2011-09-22 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 8.4 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110922-05 | Pitchangle 1 Diff.Set-Act | 2011-09-22 | 2011-09-22 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 2 | Forced |  |  | 8.4 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110922-06 | Pitchangle 1 Diff.Set-Act | 2011-09-22 | 2011-09-22 | KRAYN-WTG25 | Warranty Repair | Nordex USA OandM | 1.5 | Forced |  |  | 8.4 | Highland 1 |  | KRAYN-WKO-NDX-20110922 | 1
KRAYN-WKO-NDX-20110923-01 | No work order description provided by contractor | 2011-09-23 |  | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 15 | Planned |  |  | 0.25 | Highland 1 |  | KRAYN-WKO-NDX-20110923 | 1
KRAYN-WKO-NDX-20110927-01 | WTG Manual Stop | 2011-09-27 | 2011-09-27 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 5.5 | Planned |  |  | 3.55 | Highland 1 |  | KRAYN-WKO-NDX-20110927 | 1
KRAYN-WKO-NDX-20110927-02 | WTG Manual Stop | 2011-09-27 | 2011-09-27 | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 3.55 | Highland 1 |  | KRAYN-WKO-NDX-20110927 | 1
KRAYN-WKO-NDX-20110928-01 | WTG CustomerError 2 | 2011-09-28 | 2011-09-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110928 | 1
KRAYN-WKO-NDX-20110928-02 | WTG CustomerError 2 | 2011-09-28 | 2011-09-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110928 | 1
KRAYN-WKO-NDX-20110928-03 | WTG CustomerError 2 | 2011-09-28 | 2011-09-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 2.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110928 | 1
KRAYN-WKO-NDX-20110928-04 | WTG CustomerError 2 | 2011-09-28 | 2011-09-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.6833 | Highland 1 |  | KRAYN-WKO-NDX-20110928 | 1
KRAYN-WKO-NDX-20110929-01 | GenRot RpmMonitor Stop | 2011-09-29 | 2011-09-29 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.4 | Highland 1 |  | KRAYN-WKO-NDX-20110929 | 1
KRAYN-WKO-NDX-20110929-02 | GenRot RpmMonitor Stop | 2011-09-29 | 2011-09-29 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 1.0833 | Forced |  |  | 3.5333 | Highland 1 |  | KRAYN-WKO-NDX-20110929 | 1
KRAYN-WKO-NDX-20110930-01 | GenRot RpmMonitor Stop | 2011-09-30 | 2011-09-30 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 5.1333 | Highland 1 |  | KRAYN-WKO-NDX-20110930 | 1
KRAYN-WKO-NDX-20111003-01 | No work order description provided by contractor | 2011-10-03 | 2011-10-03 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 10.2 | Highland 1 |  | KRAYN-WKO-NDX-20111003 | 1
KRAYN-WKO-NDX-20111003-02 | No work order description provided by contractor | 2011-10-03 | 2011-10-03 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 24.25 | Planned | KRAYN-NDX-PRT-0325 | 1 | 10.2 | Highland 1 |  | KRAYN-WKO-NDX-20111003 | 1
KRAYN-WKO-NDX-20111003-03 | WTG Manual Stop | 2011-10-03 | 2011-10-03 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 10.2 | Highland 1 |  | KRAYN-WKO-NDX-20111003 | 1
KRAYN-WKO-NDX-20111003-04 | WTG Manual Stop | 2011-10-03 | 2011-10-03 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 10.2 | Highland 1 |  | KRAYN-WKO-NDX-20111003 | 1
KRAYN-WKO-NDX-20111003-05 | MI class B Fault | 2011-10-03 | 2011-10-03 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.2167 | Forced |  |  | 4.8167 | Highland 1 |  | KRAYN-WKO-NDX-20111003 | 1
KRAYN-WKO-NDX-20111004-01 | WTG Manual Stop | 2011-10-04 | 2011-10-04 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 7.5333 | Highland 1 |  | KRAYN-WKO-NDX-20111004 | 1
KRAYN-WKO-NDX-20111004-02 | WTG Manual Stop | 2011-10-04 | 2011-10-04 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 6.75 | Planned | KRAYN-NDX-PRT-0325 | 1 | 7.5333 | Highland 1 |  | KRAYN-WKO-NDX-20111004 | 1
KRAYN-WKO-NDX-20111004-03 | WTG Manual Stop | 2011-10-04 | 2011-10-04 | KRAYN-WTG04 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 5.3 | Highland 1 |  | KRAYN-WKO-NDX-20111004 | 1
KRAYN-WKO-NDX-20111005-01 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111005-02 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0697 | 20L,1,2 | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111005-03 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111005-04 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.41667 | Planned |  |  | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111005-05 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111005-06 | WTG Manual Stop | 2011-10-05 | 2011-10-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.41667 | Planned |  |  | 6.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111005 | 1
KRAYN-WKO-NDX-20111006-01 | WTG Manual Stop | 2011-10-06 | 2011-10-06 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 1.25 | Forced |  |  | 7.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-02 | WTG Manual Stop | 2011-10-06 | 2011-10-06 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 5.6667 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-03 | WTG Manual Stop | 2011-10-06 | 2011-10-06 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0697 | 40L,1,4 | 7.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-04 | Pitch1 battery defect | 2011-10-06 | 2011-10-07 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.4 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-05 | Hyd OilPmpSwitchingFrequency high | 2011-10-06 | 2011-10-06 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 5.75 | Forced |  |  | 8.8333 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-06 | WTG Manual Stop | 2011-10-06 | 2011-10-06 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 6.5 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111006-07 | WTG Manual Stop | 2011-10-06 | 2011-10-06 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 6.5 | Highland 1 |  | KRAYN-WKO-NDX-20111006 | 1
KRAYN-WKO-NDX-20111007-01 | Yaw HydBrk not open | 2011-10-07 | 2011-10-07 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 2.75 | Highland 1 |  | KRAYN-WKO-NDX-20111007 | 1
KRAYN-WKO-NDX-20111007-02 | IBS Interbus Stop | 2011-10-07 | 2011-10-08 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced |  |  | 4.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111007 | 1
KRAYN-WKO-NDX-20111008-01 | GenRot RpmDiff H Stop | 2011-10-08 | 2011-10-08 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 8.0167 | Highland 1 |  | KRAYN-WKO-NDX-20111008 | 1
KRAYN-WKO-NDX-20111010-01 | WTG Manual Stop | 2011-10-10 | 2011-10-10 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned | KRAYN-NDX-PRT-0325 | 1 | 6.35 | Highland 1 |  | KRAYN-WKO-NDX-20111010 | 1
KRAYN-WKO-NDX-20111010-02 | WTG Manual Stop | 2011-10-10 | 2011-10-10 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 8.5 | Forced |  |  | 5.4833 | Highland 1 |  | KRAYN-WKO-NDX-20111010 | 1
KRAYN-WKO-NDX-20111010-03 | WTG Manual Stop | 2011-10-10 | 2011-10-10 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 8.5 | Forced |  |  | 5.4833 | Highland 1 |  | KRAYN-WKO-NDX-20111010 | 1
KRAYN-WKO-NDX-20111010-04 | WTG Manual Stop | 2011-10-10 | 2011-10-10 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 6.35 | Highland 1 |  | KRAYN-WKO-NDX-20111010 | 1
KRAYN-WKO-NDX-20111010-05 | WTG Manual Stop | 2011-10-10 | 2011-10-10 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 0.75 | Planned |  |  | 6.35 | Highland 1 |  | KRAYN-WKO-NDX-20111010 | 1
KRAYN-WKO-NDX-20111011-01 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.75 | Forced |  |  | 7.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-02 | No work order description provided by contractor | 2011-10-11 | 2011-10-11 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-03 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 10.75 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 40L,1 | 8.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-04 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 8.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-05 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.41667 | Forced |  |  | 7.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-06 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-07 | WTG Manual Stop | 2011-10-11 | 2011-10-11 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 2.15 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111011-08 | System OK | 2011-10-11 | 2012-10-11 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.5 | Highland 1 |  | KRAYN-WKO-NDX-20111011 | 1
KRAYN-WKO-NDX-20111012-01 | WTG Manual Stop | 2011-10-12 | 2011-10-12 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 8 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 40L,1 | 4.65 | Highland 1 |  | KRAYN-WKO-NDX-20111012 | 1
KRAYN-WKO-NDX-20111012-02 | WTG Manual Stop | 2011-10-12 | 2011-10-12 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 0.41667 | Planned |  |  | 4.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111012 | 1
KRAYN-WKO-NDX-20111013-01 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 1.2167 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-02 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 1.2167 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-03 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 40L,1 | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-04 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-05 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-06 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-07 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-08 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 40L,1 | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-09 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-10 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-11 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-12 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 6.3833 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-13 | Gear OilTemp Sump H Warn | 2011-10-13 | 2011-10-13 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 1.15 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-14 | Gear OilTemp Sump H Warn | 2011-10-13 | 2011-10-13 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 0.75 | Planned |  |  | 1.2167 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-15 | Gear OilTemp Sump H Warn | 2011-10-13 | 2011-10-13 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.3333 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111013-16 | WTG Manual Stop | 2011-10-13 | 2011-10-13 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 0.43333 | Highland 1 |  | KRAYN-WKO-NDX-20111013 | 1
KRAYN-WKO-NDX-20111014-01 | WTG Manual Stop | 2011-10-14 | 2011-10-14 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 1.25 | Highland 1 |  | KRAYN-WKO-NDX-20111014 | 1
KRAYN-WKO-NDX-20111014-02 | WTG Manual Stop | 2011-10-14 | 2011-10-14 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.25 | Planned |  |  | 1.6 | Highland 1 |  | KRAYN-WKO-NDX-20111014 | 1
KRAYN-WKO-NDX-20111014-03 | WTG Manual Stop | 2011-10-14 | 2011-10-14 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned |  |  | 1.6 | Highland 1 |  | KRAYN-WKO-NDX-20111014 | 1
KRAYN-WKO-NDX-20111015-01 | SafetyChain Activated | 2011-10-15 | 2011-10-16 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 8.8333 | Forced |  |  | 12.5167 | Highland 1 |  | KRAYN-WKO-NDX-20111015 | 1
KRAYN-WKO-NDX-20111015-02 | SafetyChain Activated | 2011-10-15 | 2011-10-15 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.4333 | Highland 1 |  | KRAYN-WKO-NDX-20111015 | 1
KRAYN-WKO-NDX-20111015-03 | SafetyChain Activated | 2011-10-15 | 2011-10-15 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2.4833 | Highland 1 |  | KRAYN-WKO-NDX-20111015 | 1
KRAYN-WKO-NDX-20111015-04 | SafetyChain Activated | 2011-10-15 | 2011-10-15 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2.95 | Highland 1 |  | KRAYN-WKO-NDX-20111015 | 1
KRAYN-WKO-NDX-20111015-05 | Yaw Inverter Fault | 2011-10-15 | 2011-10-15 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111015 | 1
KRAYN-WKO-NDX-20111016-01 | MI class B Fault | 2011-10-16 | 2011-10-16 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.7667 | Highland 1 |  | KRAYN-WKO-NDX-20111016 | 1
KRAYN-WKO-NDX-20111017-01 | SafetyChain Activated | 2011-10-17 | 2011-10-17 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.45 | Highland 1 |  | KRAYN-WKO-NDX-20111017 | 1
KRAYN-WKO-NDX-20111017-02 | SafetyChain Activated | 2011-10-17 | 2011-10-17 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 2.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111017 | 1
KRAYN-WKO-NDX-20111018-01 | WTG Manual Stop | 2011-10-18 | 2011-10-18 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.3 | Highland 1 |  | KRAYN-WKO-NDX-20111018 | 1
KRAYN-WKO-NDX-20111018-02 | WTG Manual Stop | 2011-10-18 | 2011-10-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.5333 | Highland 1 |  | KRAYN-WKO-NDX-20111018 | 1
KRAYN-WKO-NDX-20111018-03 | WTG Manual Stop | 2011-10-18 | 2011-10-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 10.8333 | Planned |  |  | 5.5333 | Highland 1 |  | KRAYN-WKO-NDX-20111018 | 1
KRAYN-WKO-NDX-20111018-04 | WTG Manual Stop | 2011-10-18 | 2011-10-18 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 10.15 | Highland 1 |  | KRAYN-WKO-NDX-20111018 | 1
KRAYN-WKO-NDX-20111019-01 | SafetyChain Activated | 2011-10-19 | 2011-10-20 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 15.25 | Forced |  |  | 13.4 | Highland 1 |  | KRAYN-WKO-NDX-20111019 | 1
KRAYN-WKO-NDX-20111019-02 | SafetyChain Activated | 2011-10-19 | 2011-10-19 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 10.75 | Forced |  |  | 9.6667 | Highland 1 |  | KRAYN-WKO-NDX-20111019 | 1
KRAYN-WKO-NDX-20111020-01 | SafetyChain Activated | 2011-10-20 |  | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 13.4 | Highland 1 |  | KRAYN-WKO-NDX-20111020 | 1
KRAYN-WKO-NDX-20111020-02 | LV InsulatMonitor 660V Warn | 2011-10-20 | 2011-10-20 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 0.81667 | Highland 1 |  | KRAYN-WKO-NDX-20111020 | 1
KRAYN-WKO-NDX-20111020-03 | MI class B Fault | 2011-10-20 | 2011-10-21 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.2833 | Highland 1 |  | KRAYN-WKO-NDX-20111020 | 1
KRAYN-WKO-NDX-20111024-01 | MI class B Fault | 2011-10-24 | 2011-10-24 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 14.45 | Highland 1 |  | KRAYN-WKO-NDX-20111024 | 1
KRAYN-WKO-NDX-20111024-02 | WTG Manual Stop | 2011-10-24 | 2011-10-24 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 8.75 | Planned |  |  | 5.75 | Highland 1 |  | KRAYN-WKO-NDX-20111024 | 1
KRAYN-WKO-NDX-20111024-03 | WTG Manual Stop | 2011-10-24 | 2011-10-24 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.75 | Planned |  |  | 5.75 | Highland 1 |  | KRAYN-WKO-NDX-20111024 | 1
KRAYN-WKO-NDX-20111025-01 | SafetyChain Activated | 2011-10-25 |  | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 13.4 | Highland 1 |  | KRAYN-WKO-NDX-20111025 | 1
KRAYN-WKO-NDX-20111025-02 | WTG Manual Stop | 2011-10-25 | 2011-10-25 | KRAYN-WTG22 | Retrofit | Nordex USA OandM | 0.41667 | Forced |  |  | 1.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111025 | 1
KRAYN-WKO-NDX-20111025-03 | WTG Manual Stop | 2011-10-25 | 2011-10-25 | KRAYN-WTG22 | Retrofit | Nordex USA OandM | 1.6667 | Forced |  |  | 1.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111025 | 1
KRAYN-WKO-NDX-20111025-04 | WTG Manual Stop | 2011-10-25 | 2011-10-25 | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 1.35 | Highland 1 |  | KRAYN-WKO-NDX-20111025 | 1
KRAYN-WKO-NDX-20111025-05 | WTG Manual Stop | 2011-10-25 | 2011-10-25 | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 1.25 | Forced |  |  | 1.35 | Highland 1 |  | KRAYN-WKO-NDX-20111025 | 1
KRAYN-WKO-NDX-20111028-01 | WTG Manual Stop | 2011-10-28 | 2011-10-28 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.6667 | Forced |  |  | 0.76667 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111028-02 | WTG Manual Stop | 2011-10-28 | 2011-10-28 | KRAYN-WTG02 | General Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.43333 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111028-03 | MI ext. Hardware Error | 2011-10-28 | 2011-10-28 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 0.28333 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111028-04 | WTG Manual Stop | 2011-10-28 | 2011-10-28 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.78333 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111028-05 | MI ext. Hardware Error | 2011-10-28 | 2011-10-28 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111028-06 | MI class B Fault | 2011-10-28 | 2011-10-28 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 16.25 | Forced |  |  | 187.8475 | Highland 1 |  | KRAYN-WKO-NDX-20111028 | 1
KRAYN-WKO-NDX-20111029-01 | Hyd OilPmpRuntime long | 2011-10-29 | 2011-10-30 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced |  |  | 1.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111029 | 1
KRAYN-WKO-NDX-20111029-02 | Hyd OilPmpRuntime long | 2011-10-29 | 2011-10-30 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced |  |  | 1.0667 | Highland 1 |  | KRAYN-WKO-NDX-20111029 | 1
KRAYN-WKO-NDX-20111031-01 | WTG Manual Stop | 2011-10-31 | 2011-10-31 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 10 | Forced |  |  | 4.5 | Highland 1 |  | KRAYN-WKO-NDX-20111031 | 1
KRAYN-WKO-NDX-20111031-02 | MI class B Fault | 2011-10-31 | 2011-10-31 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.2833 | Highland 1 |  | KRAYN-WKO-NDX-20111031 | 1
KRAYN-WKO-NDX-20111101-01 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 2.2167 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-02 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 3.75 | Planned |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-03 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.58333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-04 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.16667 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-05 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-06 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.83333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-07 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-08 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.58333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-09 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.16667 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-10 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-11 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.83333 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-12 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 7.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-13 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 7.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-14 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 7.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-15 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned | KRAYN-NDX-PRT-0325 | 1 | 7.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-16 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 1.85 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111101-17 | WTG Manual Stop | 2011-11-01 | 2011-11-01 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 5.0386 | Highland 1 |  | KRAYN-WKO-NDX-20111101 | 1
KRAYN-WKO-NDX-20111102-01 | Pitchangle 1 Diff.Set-Act | 2011-11-02 | 2011-11-02 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 5.6 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-02 | WTG Manual Stop | 2011-11-02 | 2011-11-02 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 3.9167 | Planned |  |  | 2.45 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-03 | WTG Manual Stop | 2011-11-02 | 2011-11-02 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 5.5833 | Planned |  |  | 2.5167 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-04 | GenRot RpmDiff H Stop | 2011-11-02 | 2011-11-02 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 12.65 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-05 | LV UPSBatteryChange | 2011-11-02 | 2011-11-02 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 0.33333 | Forced |  |  | 0.28333 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-06 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 0.083333 | Planned |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-07 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 0.16667 | Planned |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-08 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 0.91667 | Planned |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-09 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-10 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-11 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Retrofit | Nordex USA OandM | 4 | Forced |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-12 | Pitch3 Batt.contactor Error | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-13 | WTG Manual Stop | 2011-11-02 | 2011-11-03 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 9.25 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 20 L,1 | 12.35 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111102-14 | WTG Manual Stop | 2011-11-02 | 2011-11-02 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 2.45 | Highland 1 |  | KRAYN-WKO-NDX-20111102 | 1
KRAYN-WKO-NDX-20111103-01 | WTG System ok | 2011-11-03 | 2011-11-03 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-02 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 2.4333 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-03 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-04 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-05 | No work order description provided by contractor | 2011-11-03 | 2011-11-03 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 1.75 | Planned |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-06 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 1.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-07 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 0.66667 | Planned |  |  | 5.0464 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-08 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG25 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 4.7333 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111103-09 | WTG Manual Stop | 2011-11-03 | 2011-11-03 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 7.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0034 | 9,1 gal,1,1gal,20l | 5.05 | Highland 1 |  | KRAYN-WKO-NDX-20111103 | 1
KRAYN-WKO-NDX-20111104-01 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 2.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-02 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 2.05 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-03 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 4.3 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-04 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-05 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-06 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 0.66667 | Planned |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-07 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 8.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0034 | 9,1 gal,1,1gal,20l | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-08 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 0.33333 | Planned |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-09 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111104-10 | WTG Manual Stop | 2011-11-04 | 2011-11-04 | KRAYN-WTG21 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 6 | Highland 1 |  | KRAYN-WKO-NDX-20111104 | 1
KRAYN-WKO-NDX-20111107-01 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2.75 | Planned |  |  | 2.4167 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-02 | No work order description provided by contractor | 2011-11-07 | 2011-11-07 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 2.1333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-03 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 1.75 | Planned |  |  | 2.3167 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-04 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-05 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-06 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-07 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-08 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-09 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111107-10 | WTG Manual Stop | 2011-11-07 | 2011-11-07 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 10.75 | Planned | KRAYN-NDX-PRT-0034,KRAYN-NDX-PRT-0325 | 40 L,1 | 7.2333 | Highland 1 |  | KRAYN-WKO-NDX-20111107 | 1
KRAYN-WKO-NDX-20111108-01 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-02 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-03 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-04 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-05 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0720 | 1,1 | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-06 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-07 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-08 | WTG Manual Stop | 2011-11-08 | 2011-11-09 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned |  |  | 12.55 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-09 | WTG Manual Stop | 2011-11-08 |  | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 12.55 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-10 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 1.75 | Planned |  |  | 2.3667 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-11 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 2.3 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111108-12 | WTG Manual Stop | 2011-11-08 | 2011-11-08 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 1.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111108 | 1
KRAYN-WKO-NDX-20111109-01 | Hyd OilLevel L Stopp | 2011-11-09 | 2011-11-09 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.25 | Forced |  |  | 2.65 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-02 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 5.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-03 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 7 | Planned | KRAYN-NDX-PRT-0034 | 20 L | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-04 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-05 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-06 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-07 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-08 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-09 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-10 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 7.8 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-11 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 1.7667 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-12 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-13 | No work order description provided by contractor | 2011-11-09 | 2011-11-09 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 1.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111109-14 | WTG Manual Stop | 2011-11-09 | 2011-11-09 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 2.15 | Highland 1 |  | KRAYN-WKO-NDX-20111109 | 1
KRAYN-WKO-NDX-20111110-01 | IBS Busquality Warning | 2011-11-10 | 2011-11-10 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.3333 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-02 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced |  |  | 2.4167 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-03 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced |  |  | 2.4167 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-04 | Gen CWPress L Stopp | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 2.1167 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-05 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 8 | Planned | KRAYN-NDX-PRT-0034 | 20 L | 6.3167 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-06 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-07 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-08 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-09 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-10 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111110-11 | WTG Manual Stop | 2011-11-10 | 2011-11-10 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111110 | 1
KRAYN-WKO-NDX-20111111-01 | Safety chain | 2011-11-11 | 2011-11-11 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 2.3333 | Highland 1 |  | KRAYN-WKO-NDX-20111111 | 1
KRAYN-WKO-NDX-20111111-02 | Yaw HydBrk not open | 2011-11-11 | 2011-11-12 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 15.25 | Forced |  |  | 15.3667 | Highland 1 |  | KRAYN-WKO-NDX-20111111 | 1
KRAYN-WKO-NDX-20111111-03 | MI External Hardware | 2011-11-11 | 2011-11-11 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 0.98333 | Highland 1 |  | KRAYN-WKO-NDX-20111111 | 1
KRAYN-WKO-NDX-20111113-01 | SafetyChain Activated | 2011-11-13 | 2011-11-13 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 3.5833 | Highland 1 |  | KRAYN-WKO-NDX-20111113 | 1
KRAYN-WKO-NDX-20111114-01 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 2.0333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-02 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 1.05 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-03 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 1.05 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-04 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-14 |  | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 0.78333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-05 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-06 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-07 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 27.25 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0034 | 1,5 gal | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-08 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-09 | WTG Manual Stop | 2011-11-14 | 2011-11-14 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 1.4167 | Planned |  |  | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111114-10 | GenRot RpmSensor CollFault | 2011-11-14 | 2011-11-14 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111114 | 1
KRAYN-WKO-NDX-20111115-01 | WTG Manual Stop | 2011-11-15 | 2011-11-15 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 6.4667 | Highland 1 |  | KRAYN-WKO-NDX-20111115 | 1
KRAYN-WKO-NDX-20111115-02 | WTG Manual Stop | 2011-11-15 | 2011-11-15 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 6.4667 | Highland 1 |  | KRAYN-WKO-NDX-20111115 | 1
KRAYN-WKO-NDX-20111115-03 | WTG Manual Stop | 2011-11-15 | 2011-11-15 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0034 | 40 L | 6.4667 | Highland 1 |  | KRAYN-WKO-NDX-20111115 | 1
KRAYN-WKO-NDX-20111115-04 | WTG Manual Stop | 2011-11-15 | 2011-11-15 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 980716.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0034 | 1,5 gal | 9.65 | Highland 1 |  | KRAYN-WKO-NDX-20111115 | 1
KRAYN-WKO-NDX-20111116-01 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-02 | Gen CWPress L Stopp | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-03 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-04 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-05 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 18.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0034 | 1,5 gal | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-06 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-07 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-08 | WTG Manual Stop | 2011-11-16 | 2011-11-16 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-09 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-16 |  | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 0.78333 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111116-10 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-16 |  | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 13 | Forced |  |  | 0.78333 | Highland 1 |  | KRAYN-WKO-NDX-20111116 | 1
KRAYN-WKO-NDX-20111117-01 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-17 | 2011-11-17 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 16 | Forced |  |  | 91.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111117 | 1
KRAYN-WKO-NDX-20111117-02 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-17 | 2011-11-17 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 16 | Forced |  |  | 91.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111117 | 1
KRAYN-WKO-NDX-20111117-03 | Yaw SensRuntimeToothToTooth TimeOut | 2011-11-17 | 2011-11-17 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 10.5 | Forced |  |  | 91.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111117 | 1
KRAYN-WKO-NDX-20111117-04 | No work order description provided by contractor | 2011-11-17 | 2011-11-17 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 91.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111117 | 1
KRAYN-WKO-NDX-20111117-05 | No work order description provided by contractor | 2011-11-17 | 2011-11-17 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 91.9167 | Highland 1 |  | KRAYN-WKO-NDX-20111117 | 1
KRAYN-WKO-NDX-20111118-01 | LV UPSBatteryChange | 2011-11-18 | 2011-11-18 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1 | Highland 1 |  | KRAYN-WKO-NDX-20111118 | 1
KRAYN-WKO-NDX-20111118-02 | LV UPSBatteryChange | 2011-11-18 | 2011-11-18 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1 | Highland 1 |  | KRAYN-WKO-NDX-20111118 | 1
KRAYN-WKO-NDX-20111118-03 | LV UPSBatteryChange | 2011-11-18 | 2011-11-18 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1 | Highland 1 |  | KRAYN-WKO-NDX-20111118 | 1
KRAYN-WKO-NDX-20111118-04 | LV UPSBatteryChange | 2011-11-18 | 2011-11-18 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.5 | Highland 1 |  | KRAYN-WKO-NDX-20111118 | 1
KRAYN-WKO-NDX-20111121-01 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-02 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-03 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 25.5 | Planned | KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017 | 1,1 | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-04 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-05 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 0.65 | Planned |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-06 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-07 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-08 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-09 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-10 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 1 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-11 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-12 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111121-13 | WTG Manual Stop | 2011-11-21 | 2011-11-21 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0325 | 1 | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111121 | 1
KRAYN-WKO-NDX-20111122-01 | Wind DirSlanting Stop(due YP50) | 2011-11-22 | 2011-11-23 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 6.9667 | Highland 1 |  | KRAYN-WKO-NDX-20111122 | 1
KRAYN-WKO-NDX-20111122-02 | SafetyChain Activated | 2011-11-22 | 2011-11-22 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111122 | 1
KRAYN-WKO-NDX-20111124-01 | Yaw HydBrk not closed | 2011-11-24 | 2011-11-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 6.3333 | Highland 1 |  | KRAYN-WKO-NDX-20111124 | 1
KRAYN-WKO-NDX-20111124-02 | Yaw HydBrk not closed | 2011-11-24 | 2011-11-24 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 6.3333 | Highland 1 |  | KRAYN-WKO-NDX-20111124 | 1
KRAYN-WKO-NDX-20111125-01 | SafetyChain Activated | 2011-11-25 | 2011-11-25 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.2833 | Highland 1 |  | KRAYN-WKO-NDX-20111125 | 1
KRAYN-WKO-NDX-20111127-01 | No work order description provided by contractor | 2011-11-27 |  | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.98333 | Highland 1 |  | KRAYN-WKO-NDX-20111127 | 1
KRAYN-WKO-NDX-20111128-01 | MI class B Fault | 2011-11-28 | 2011-11-28 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 0.8 | Highland 1 |  | KRAYN-WKO-NDX-20111128 | 1
KRAYN-WKO-NDX-20111129-01 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 4.5 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-02 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 2.2167 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-03 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG07 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-05 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 1.05 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-06 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 7.2833 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-07 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 7.2667 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-08 | SafetyChain Activated | 2011-11-29 | 2011-11-29 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 4.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-09 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG11 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 0.83333 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-10 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 1.5 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-11 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 7.4167 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-12 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG14 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 6.1667 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-13 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 6.9333 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-14 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG17 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 9.65 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-15 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 8.3 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-16 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 8.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-17 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG23 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 4.8167 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-18 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-19 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 2.0333 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111129-20 | No work order description provided by contractor | 2011-11-29 |  | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 1.05 | Highland 1 |  | KRAYN-WKO-NDX-20111129 | 1
KRAYN-WKO-NDX-20111130-02 | Yaw MotBrake not open | 2011-11-30 | 2011-11-30 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6667 | Highland 1 |  | KRAYN-WKO-NDX-20111130 | 1
KRAYN-WKO-NDX-20111130-05 | Yaw MotBrake not open | 2011-11-30 | 2011-11-30 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6667 | Highland 1 |  | KRAYN-WKO-NDX-20111130 | 1
KRAYN-WKO-NDX-20111201-01 | WTG Manual Stop | 2011-12-01 | 2011-12-01 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 7.5167 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111201-02 | WTG Manual Stop | 2011-12-01 | 2011-12-01 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 7.65 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111201-03 | LV UPSBatteryLow | 2011-12-01 | 2011-12-01 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 7.5 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111201-04 | MI class B Fault | 2011-12-01 | 2011-12-01 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 7.65 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111201-05 | MI class B Fault | 2011-12-01 | 2011-12-01 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 7.65 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111201-06 | WTG Manual Stop | 2011-12-01 | 2011-12-01 | KRAYN-WTG16 | General Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 1.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111201 | 1
KRAYN-WKO-NDX-20111202-01 | Pitch PowerVolt. Fault | 2011-12-02 | 2011-12-02 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 3.5333 | Highland 1 |  | KRAYN-WKO-NDX-20111202 | 1
KRAYN-WKO-NDX-20111203-01 | Pitch3 DC.link Overcurrent | 2011-12-03 | 2011-12-03 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 12 | Forced |  |  | 15.35 | Highland 1 |  | KRAYN-WKO-NDX-20111203 | 1
KRAYN-WKO-NDX-20111205-01 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111205-02 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 5.5 | Forced |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111205-03 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111205-04 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.45 | Planned |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111205-05 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111205-06 | WTG Manual Stop | 2011-12-05 | 2011-12-05 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 3.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111205 | 1
KRAYN-WKO-NDX-20111206-01 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 6.5 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-02 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-03 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-04 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 3.0833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-05 | No work order description provided by contractor | 2011-12-06 | 2011-12-06 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 3.0833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-06 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 3.0833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-07 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 3.5 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-08 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111206-09 | WTG Manual Stop | 2011-12-06 | 2011-12-06 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111206 | 1
KRAYN-WKO-NDX-20111207-01 | WTG Manual Stop | 2011-12-07 | 2011-12-07 | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 4.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-02 | WTG Manual Stop | 2011-12-07 | 2011-12-07 | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 3.5 | Forced |  |  | 4.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-03 | WTG Manual Stop | 2011-12-07 | 2011-12-07 | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 4.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-04 | WTG Manual Stop | 2011-12-07 | 2011-12-07 | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 4.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-05 | WTG Manual Stop | 2011-12-07 | 2011-12-07 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 4.6167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-06 | MI class B Fault | 2011-12-07 | 2011-12-08 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.3167 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-07 | MI class B Fault | 2011-12-07 | 2011-12-08 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.4833 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-08 | MI class B Fault | 2011-12-07 | 2011-12-08 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.2 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111207-09 | MI class B Fault | 2011-12-07 | 2011-12-08 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2 | Highland 1 |  | KRAYN-WKO-NDX-20111207 | 1
KRAYN-WKO-NDX-20111208-01 | MI Initialization Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 6.75 | Forced |  |  | 14.0167 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-02 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2.4167 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-03 | Wind Speed unequal Power | 2011-12-08 | 2011-12-08 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 3.05 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-04 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-05 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-06 | Hyd OilLevel L Stopp | 2011-12-08 | 2011-12-08 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 6.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-07 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-09 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-10 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-11 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG10 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-12 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 3.7 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-13 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.65 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-14 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.5667 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-15 | Yaw MotBrake not closed | 2011-12-08 | 2011-12-09 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 2.25 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-16 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.65 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-17 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG15 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 3.65 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-18 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.25 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-19 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.35 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-20 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.7833 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-21 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.85 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-22 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-23 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.4333 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-24 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.15 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-25 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.4333 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111208-26 | MI class B Fault | 2011-12-08 | 2011-12-08 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3 | Highland 1 |  | KRAYN-WKO-NDX-20111208 | 1
KRAYN-WKO-NDX-20111209-01 | No work order description provided by contractor | 2011-12-09 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.2833 | Highland 1 |  | KRAYN-WKO-NDX-20111209 | 1
KRAYN-WKO-NDX-20111212-01 | WTG Manual Stop | 2011-12-12 | 2011-12-12 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111212 | 1
KRAYN-WKO-NDX-20111212-02 | WTG Manual Stop | 2011-12-12 | 2011-12-12 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 3.25 | Forced |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111212 | 1
KRAYN-WKO-NDX-20111212-03 | WTG Manual Stop | 2011-12-12 | 2011-12-12 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111212 | 1
KRAYN-WKO-NDX-20111213-01 | WTG Manual Stop | 2011-12-13 | 2011-12-13 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 5.05 | Highland 1 |  | KRAYN-WKO-NDX-20111213 | 1
KRAYN-WKO-NDX-20111215-01 | SafetyChain Activated | 2011-12-15 | 2011-12-15 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.8333 | Highland 1 |  | KRAYN-WKO-NDX-20111215 | 1
KRAYN-WKO-NDX-20111215-02 | MI class B Fault | 2011-12-15 | 2011-12-15 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.4833 | Highland 1 |  | KRAYN-WKO-NDX-20111215 | 1
KRAYN-WKO-NDX-20111216-01 | MI class C (Service!) Fault | 2011-12-16 | 2011-12-15 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 5.0833 | Highland 1 |  | KRAYN-WKO-NDX-20111216 | 1
KRAYN-WKO-NDX-20111217-01 | MI class C (Service!) Fault | 2011-12-17 | 2011-12-17 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 11.3167 | Highland 1 |  | KRAYN-WKO-NDX-20111217 | 1
KRAYN-WKO-NDX-20111218-01 | MI class C (Service!) Fault | 2011-12-18 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 14.5 | Forced |  |  | 6.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111218 | 1
KRAYN-WKO-NDX-20111219-01 | No work order description provided by contractor | 2011-12-19 |  | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 0.75 | Forced |  |  | 1.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111219-02 | No work order description provided by contractor | 2011-12-19 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 2.9833 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111219-03 | No work order description provided by contractor | 2011-12-19 |  | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 2.45 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111219-04 | MI class C (Service!) Fault | 2011-12-19 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 16.5 | Forced |  |  | 6.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111219-05 | No work order description provided by contractor | 2011-12-19 |  | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 5.05 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111219-06 | No work order description provided by contractor | 2011-12-19 |  | KRAYN-WTG04 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 1.85 | Highland 1 |  | KRAYN-WKO-NDX-20111219 | 1
KRAYN-WKO-NDX-20111220-01 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0603 | 1 | 2.2 | Highland 1 | Replaced and realigned ultrasonic anemometer | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-02 | MI class C (Service!) Fault | 2011-12-20 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 6.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-04 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 1.2167 | Highland 1 | Installed Fan Cover retro. | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-05 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.2167 | Highland 1 | Adjusted yaw brakes. | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-06 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.91667 | Forced | KRAYN-NDX-PRT-0358,KRAYN-NDX-PRT-0501 | 1,1 | 1.2167 | Highland 1 | Replaced Module 115 V2 | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-07 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 1.2167 | Highland 1 | Installed Fan Cover retro. | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-08 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 1.2167 | Highland 1 | Adjusted yaw brakes. | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-09 | MI class C (Service!) Fault | 2011-12-20 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 24.5 | Forced |  |  | 6.6833 | Highland 1 |  | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111220-10 | FM6 / WTG Manual Stop | 2011-12-20 | 2011-12-20 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.91667 | Forced | KRAYN-NDX-PRT-0358,KRAYN-NDX-PRT-0501 | 1,1 | 1.2167 | Highland 1 | Replaced Module 115 V2 | KRAYN-WKO-NDX-20111220 | 1
KRAYN-WKO-NDX-20111221-01 | FM1209 / MI class C (Service!) Fault | 2011-12-21 | 2011-12-21 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 11.5 | Forced |  |  | 90.0167 | Highland 1 | Troubleshoot IGBT. Upper rack and new IGBT bad. Running at 1/2 power on lower rack. | KRAYN-WKO-NDX-20111221 | 1
KRAYN-WKO-NDX-20111222-01 | #N/A | 2011-12-22 | 2011-12-22 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2.8667 | Forced | KRAYN-NDX-PRT-0280 | 1 | 0.93333 | Highland 1 | Replaced 124 K1 relay to prevent yaw hyd break not open fault from re occuring. | KRAYN-WKO-NDX-20111222 | 1
KRAYN-WKO-NDX-20111222-02 | #N/A | 2011-12-22 | 2011-12-23 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 13.75 | Forced |  |  | 13.3333 | Highland 1 | Picked up IGBT from Alaquippa PA. Touble shoot WTG 06. Multiple trips to shop for parts | KRAYN-WKO-NDX-20111222 | 1
KRAYN-WKO-NDX-20111222-03 | Yaw HydBrk not closed | 2011-12-22 | 2011-12-22 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 2.6333 | Highland 1 |  | KRAYN-WKO-NDX-20111222 | 1
KRAYN-WKO-NDX-20111222-04 | FM1153 / Pitchangle 1 Diff.Set-Act | 2011-12-22 | 2011-12-22 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 4.7833 | Highland 1 | Troubleshot FM 1153. Found pitch breaker tripped. Atemped to reset breaker which didn't work. Entered hub and found the slipring to have severe arcing. Replaced slip ring with no defects noted at this time. | KRAYN-WKO-NDX-20111222 | 1
KRAYN-WKO-NDX-20111223-01 | FM741 / IBS peripherals Fault | 2011-12-23 | 2011-12-23 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced | KRAYN-NDX-PRT-0414 | 1 | 5.4833 | Highland 1 | Troubleshoot IBS 105A5, found interbus module over heated and faulty. Installed new interbus module and reset turbine. | KRAYN-WKO-NDX-20111223 | 1
KRAYN-WKO-NDX-20111223-02 | FM6 / WTG Manual Stop | 2011-12-23 | 2011-12-23 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 6.5333 | Forced |  |  | 3.7 | Highland 1 | Continued troubleshooting SEG issue with top IGBT rack. Main Chokes where isolated and meggered (good), then main chokes where swapped and the turbine ran. No issues with running on the other choke. Moved filters down from bad rack to good rack one at a time to see if any where causeing the issue which resulted in no change all filters operated correctly. Came back to thisd turbine later and crossed the ribbon IGBT connections on the FIT board which used the top rack portion of the FIT to run the bottom IGBT which checked out good. Placed turbine back into service running at 20% (500 KW MAX) until further support can arrive. | KRAYN-WKO-NDX-20111223 | 1
KRAYN-WKO-NDX-20111228-01 | FM6 / WTG Manual Stop | 2011-12-28 | 2011-12-29 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 14 | Forced |  |  | 11.3833 | Highland 1 | Today techs came on site with Paul to work on WTG 6 issue. The day started with us reviewing what all has been done and changed. Once this was completed Paul wanted to see what was going on with the convertor. After he heard/saw what was going on we started to walk through and talk about why wer changed what we did and how did it help or not help the turbine. The next step is we started to take measurements on anything that was part of on the lines for the gen. This all checked out good, at this point we started to put the IGBT back together and take triggers. We then started the turbine up and started to commission the HUR and got to stage 3.2 in the procedure and we heard a bad noise in the choke area so we took a live trigger. At this point we looked at the trigger and noticed again a problem on phase 3 of the MSC side. We then started to check the connections on the fit board, anything from the fiber to the cabling. After this was done we then did another try at commissioning, the turbine still made the same noise but we kept going and it fault at 4.1 in the procedure syncs fault. We took the triggers again and checked them out. We found once again phase 3 on msc was looking bad. Next step was to check IGBT cables and choke, all was fine. At this point we decided to change out the fit board and try to commission again. The turbine then faulted with the same sync problem, so we decided to change out the Fit adap board. We changed the board then tried to comission again, once again it faulted on sync issue. We took triggers and looked at them to notice that phase 3 on msc had to current, at this point we started to swap out the line filters to see if problem will follow. After swap we had to try and comission again, it faulted once again at the sync fault. Took triggers and still no current on phase 3 MSC, then we decide to run a test with a amp clamp and put it on the phase that was missing to see if it was missing. We put an amp clamp on the phase 3 MSC and did the comissioning, it faulted again on sync with no current on phase 3 MSC. We walked over to check the amp clamp to find that it saw 156 amps just like the other phases. So with seeing this we started to move forward with moving the amp clamp and ribbon cable from phase 3 of MSC to phase 2 MSC to see if problem followed.We then started to comission again and it faulted on sync again, but this time it has a current isssue on phase 2 MSC. The trigger showed us the problem has followed the ribbun cable with the trigger saying no current and the amp clamp was reading 163 amps. At this point we have decided it has to be the ribbun cable,so we sent techs back to get ribbun cables while techs start to out the old ribbun cable. After the broken ribbun cable was replaced we started the comissioning procedure again, but this time everything sounded good and it made it all the way through and came online. Techs then shut the trubine down and started to put all the doors back on and clean the turbine up. once all this was done the turbine was brought back online and the techs went home for the day. | KRAYN-WKO-NDX-20111228 | 1
KRAYN-WKO-NDX-20111229-01 | FM1213 / MI ext. Hardware Error | 2011-12-29 | 2011-12-29 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.0833 | Highland 1 | Checked and reset tripped breaker. | KRAYN-WKO-NDX-20111229 | 1
KRAYN-WKO-NDX-20111229-02 | #N/A | 2011-12-29 | 2011-12-29 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.76667 | Highland 1 | replaced ups battery pack. The battery pack that was replaced on 12 was tested and we cannot find anything wrong with it. | KRAYN-WKO-NDX-20111229 | 1
KRAYN-WKO-NDX-20111229-03 | FM744 / IBS Busquality Warning | 2011-12-29 | 2011-12-29 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 2.95 | Highland 1 | replaced slip ring | KRAYN-WKO-NDX-20111229 | 1
KRAYN-WKO-NDX-20111229-04 | FM853 / Hyd OilTemp L Warn | 2011-12-29 |  | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 12.35 | Highland 1 | Cycled Hydac via manuel yaw. Temp climbed. Turbine was not shut down. | KRAYN-WKO-NDX-20111229 | 1
KRAYN-WKO-NDX-20111230-01 | FM307 / Gen brushWear Warn | 2011-12-30 | 2011-12-30 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced |  |  | 3.4667 | Highland 1 | Went to turbine. Opened the Q10P break. Applied lock out tag out equipment. Went up turbine. Opened generator brush access box. Traced wires to terminal block on side of generator and to top cabinet. When tracing wires, found that the sensors for the brushes were jumpered together from the factory making it impossible to isolate individual sensors. Jumpered terminal 13 and 14 on the X15 terminal block in top cabinet. The jumpered wires cleared the fault until a new sensor assebly can be applied. Closed up all compartments. Went back down turbine. Removed the LOTO equipment. Reset the Q10P breaker. Reset Turbine. Called tech will 400 level NCII access to reset turbine. Started Turbine. Returned to office. | KRAYN-WKO-NDX-20111230 | 1
KRAYN-WKO-NDX-20120101-01 | FM1208 / MI class B Fault | 2012-01-01 | 2012-01-02 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.4167 | Highland 1 | Arrived at turbine and manually reset safety chain at bottom box after a vib. sensor was tripped. Sean Illig was contacted for remote reset. | KRAYN-WKO-NDX-20120101 | 1
KRAYN-WKO-NDX-20120101-02 | FM700 / IBS Interbus Stop | 2012-01-01 | 2012-01-01 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.7667 | Highland 1 | Drove to turbine and ran Diag+. Results indicated a problem with 105A1 in the top box. Upon Asending tower 102F3 was found tripped. It was reset and with the lack of power in the Topbox it was determined that something down tower was also tripped. 34F2 was reset in the bottom box and power was restored. The first attempt to restart the turbine failed and displyed a MI class B fault. Dustin Till was contacted and turbine was reset only to throw a ups batt. low alarm. The battery was tested and inspected and found to be in good condition. This series of events happened twice more. Both Josh M. and Sean Illig were contacted for a reset. After Illig reset it the final time the alarm did not reappear and the turbine started up successfully. | KRAYN-WKO-NDX-20120101 | 1
KRAYN-WKO-NDX-20120102-02 | FM414 / Yaw MotBrake not open | 2012-01-02 | 2012-01-02 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 5.85 | Highland 1 | Reviewed Logs on NC II. Reset faults and yawed turbine remotely with no defects noted. Then witnessed turbine fault with the same fault implying that the motor brakes had not opened for a yawing command. At this time the turbine was placed in a Manual stop and the switch rights taken to avoid any more resets from a remote operator. Drove into the shop and got a truck and traveled out to site. Reviewed the faults again with another tech. Went up tower and found through troubleshooting that the RH (Right Hand) yaw motor brake mircoswitch was just loose enough to allow it to be out of adjustment. Refered to Nordex proceedures for the adjustment of the switch. Adjusted yaw motor brake microswitch on the RH yaw motor brake. Performed the same actions on the LH (Left Hand) Yaw motor brake to assure that it too was adjusted to the proper dimention. Manually activated the yaw motor brakes and verified that the relays 163AK1 and 163AK2, (Feedback from yaw motor brakes microswitches LH and RH), operated properly. This verified that the proper feedback signal from the yaw motor brake microswitchs made it to the PLC digital Inputs, which then allowed the PLC to not fault for the FM 414 ,yaw motor brakes not open, when the brakes where actually open. No further defects noted at this time. Returned down tower and placed the turbine into start mode with no further faults at this time. | KRAYN-WKO-NDX-20120102 | 1
KRAYN-WKO-NDX-20120102-03 | FM55 / GenRot RpmMonitor Stop | 2012-01-02 | 2012-01-02 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 3.5 | Highland 1 | Approached turbine and found safety chain activated and had to be reset up tower. Adjusted inductive sensors on rotor side and checked holding arm for no movement. Reset Pepperl+Fuchs, reset safety chain. Reset and started turbine. | KRAYN-WKO-NDX-20120102 | 1
KRAYN-WKO-NDX-20120102-06 | FM414 / Yaw MotBrake not open | 2012-01-02 | 2012-01-02 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 5.85 | Highland 1 | Reviewed Logs on NC II. Reset faults and yawed turbine remotely with no defects noted. Then witnessed turbine fault with the same fault implying that the motor brakes had not opened for a yawing command. At this time the turbine was placed in a Manual stop and the switch rights taken to avoid any more resets from a remote operator. Drove into the shop and got a truck and traveled out to site. Reviewed the faults again with another tech. Went up tower and found through troubleshooting that the RH (Right Hand) yaw motor brake mircoswitch was just loose enough to allow it to be out of adjustment. Refered to Nordex proceedures for the adjustment of the switch. Adjusted yaw motor brake microswitch on the RH yaw motor brake. Performed the same actions on the LH (Left Hand) Yaw motor brake to assure that it too was adjusted to the proper dimention. Manually activated the yaw motor brakes and verified that the relays 163AK1 and 163AK2, (Feedback from yaw motor brakes microswitches LH and RH), operated properly. This verified that the proper feedback signal from the yaw motor brake microswitchs made it to the PLC digital Inputs, which then allowed the PLC to not fault for the FM 414 ,yaw motor brakes not open, when the brakes where actually open. No further defects noted at this time. Returned down tower and placed the turbine into start mode with no further faults at this time. | KRAYN-WKO-NDX-20120102 | 1
KRAYN-WKO-NDX-20120103-01 | #N/A | 2012-01-03 | 2012-01-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 9 | Forced |  |  | 0.65 | Highland 1 | Drove to WTG8. Manually stopped turbine. Opened bottom box (Nordex Side) dissconected 230V heating supply, wire W120, terminal X1, 230V interbus supply, wire W121, terminal X,. Interbus bus connection to remote bus interface IN at module 23.0 wire W122 and Fiberoptic's. Removed deck plate to access basement. Pulled W120, W121 & W122 out of bottom box, through the basement and back up under Measurement Interface (Messbox). Ziptied Wires to (Messbox) and loaded it in the truck. Restarted WTG8. | KRAYN-WKO-NDX-20120103 | 1
KRAYN-WKO-NDX-20120103-02 | #N/A | 2012-01-03 | 2012-01-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 9 | Forced |  |  | 0.65 | Highland 1 | Drove to WTG8. Manually stopped turbine. Opened bottom box (Nordex Side) dissconected 230V heating supply, wire W120, terminal X1, 230V interbus supply, wire W121, terminal X,. Interbus bus connection to remote bus interface IN at module 23.0 wire W122 and Fiberoptic's. Removed deck plate to access basement. Pulled W120, W121 & W122 out of bottom box, through the basement and back up under Measurement Interface (Messbox). Ziptied Wires to (Messbox) and loaded it in the truck. Restarted WTG8. | KRAYN-WKO-NDX-20120103 | 1
KRAYN-WKO-NDX-20120103-03 | FM414 / Yaw MotBrake not open | 2012-01-03 | 2012-01-03 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.6 | Highland 1 | Arrived on site to respond to a FM414 fault. Dismantled yaw motors and checked brake clearance after jumping pins 15 and 18 on 124K2. Clearance was found to be within .05 mm of .4 mm target gap. Micro switches were checked and readjusted. Yaw motor on left side of nacelle was found to be slighly off. With the brakes jumped open the disks were rotated to check for even wear pattern...all was well. The turbine was started back up with out incident after decent. | KRAYN-WKO-NDX-20120103 | 1
KRAYN-WKO-NDX-20120103-04 | FM1213 / MI ext. Hardware Error | 2012-01-03 | 2012-01-03 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 5.8167 | Highland 1 | Arrived on site to respond to FM1213. Located tripped breaker Q43 reset and adjusted amperage to 8.5a. Contacted Josh H. and Sean Illig for 400 level access restart. | KRAYN-WKO-NDX-20120103 | 1
KRAYN-WKO-NDX-20120104-01 | FM420 / Yaw HydBrk not open | 2012-01-04 | 2012-01-04 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 14.6 | Forced |  |  | 0.71667 | Highland 1 | Manually stoped turbine and disabled switch rights to stop anyone form trying to reset FM 420. Replaced 124 K1 relay to prevent yaw hyd break not open fault from re occuring. Gathered parts during prep work. Signed out Phoenix Contactor Relay No. 29 66 595 for the 124K1 position. Drove to site, accended turbine and replaced Phoenix Contactor Relay No. 29 66 595. The fault cleared. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120104 | 1
KRAYN-WKO-NDX-20120104-02 | FM420 / Yaw HydBrk not open | 2012-01-04 | 2012-01-04 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced |  |  | 5.7667 | Highland 1 | Remotely placed machine in manual stop state and disabled switch rights to keep other remote users from trying to reset the FM 420 Yaw Hyd. Brake NOT Open fault. Gathered numerious suspect parts during prework at the shop. Loaded brake clean and rags for cleaning the valves if they where stuck, signed out a throttle valve incase it was releasing to slowly or not at all, and also signed out a new Phoenix Contact Relay No. 29 66 595 for the 124K1 position. Traveled out to site ascended the turbine. Started the troubleshooting process with the most likely suspect which was the 124K1 relay, installed the new Phoenix Contact Relay No. 29 66 595 in the 124K1 position and reset the turbine. Fault cleared so we then manually yawed the turbine and found that the relaxed yaw hyd brake pressure was at 27.78 ish bar, which is too high when this system is to be set at 22.00 bar +/- 2 bar. Adjust yaw hyd. brake pressure to 20.97 ish bar per nordex proceedure. Manually yawed the turbine CW and CCW numerious times with no defects noted at this time. Returned down tower and started the turbine. Found while trying to shut the turbine door that it would not shut. The door seal had filled with water which through physics and cold weather froze in to ice. So we cut the seal to release all of the ice pieces and got the turbine door to shut completely. | KRAYN-WKO-NDX-20120104 | 1
KRAYN-WKO-NDX-20120105-01 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 2.25 | Highland 1 | In side each blade root locate and document each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. Damaged blade seals were documented and photographed. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120105-02 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 6.5 | Forced |  |  | 2.25 | Highland 1 | Approached turbine and put it in a manual stop. Asend the tower and locked out rotor for hub entry. L.O.T.O 100 s1, 102 f2 and 102 f3 breakers. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Unlock breakers and desend tower. Call Sean Illig for reset of the 1208 MI B fault. Started turbine. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120105-03 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 3.75 | Forced |  |  | 2.2833 | Highland 1 | Approached turbine and put it in a manual stop. Asend the tower and locked out rotor for hub entry. L.O.T.O 100 s1, 102 f2 and 102 f3 breakers. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Unlock breakers and desend tower. Call Sean Illig for reset of the 1208 MI B fault. Started turbine. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120105-04 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG24 | General Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 4.2833 | Highland 1 | Inspected blade bearing seals for leakage. Found Leakage on all three external blade bearing seals. Traveled into hub to retreive the Serial numbers of these affected bearings but wonce in the blade root it was found to NOT have a bearing data plate. This was the case in all three of the blades on this turbine. After exiting the hub I took a few pictures of the leaking external blade bearing seals. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120105-05 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 4.2833 | Highland 1 | Turbine was seen on NC II running with an FM 853 Hyd Oil Temp L Warning. It also had an FM 744 IBS BusQuality Warning in this weeks history. So as a crew was installing a new hub slip ring I began to troubleshoot the FM 853 Hyd Oil Temp L Warning. I started by simpling checking the operation of the external electric heater which was great because it wasn't pluged in. But.... as I plugged the cord into the top cabinet a breaker instantly tripped. I visually looked in the top cabinet for the tripped breaker, which was found to be 112F2 which after checking the top box schematics to assure that is was the corrisonding breaker, which it was. So I unplugged the extention cord for the external electric hyd station heater and reset the tripped FM 112F2 breaker. From there I isolated the heater itself from the equation by simply unplugging it from the cord, which was to make sure that the extention cord wasn't pinched and shorted anywhere. With this completed I plugged the extention cord back in with out the other end electricly connected. The 112F2 Breaker did not trip with this configuration, which pointed to the problem being the external electric hyd station heater itself. Having thought of this during prework I had one with me. I removed the old and installed a new External electric hyd station heater. I unplugged the extention cord from the top box and plugged in the new external electric hyd station heater to the other end of the extention cord so that I could be with in hearing distance incase the 112F2 breaker tripped again. I then plugged the extention cord in to the top box and the breaker 112F2 did NOT trip and the external electric hyd station heater began to operate. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120105-06 | FM6 / WTG Manual Stop | 2012-01-05 | 2012-01-05 | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 6.25 | Forced |  |  | 4.2833 | Highland 1 | Approached turbine and put it in a manual stop. Asend the tower and locked out rotor for hub entry. L.O.T.O 100 s1, 102 f2 and 102 f3 breakers. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Unlock breakers and desend tower. Call Sean Illig for reset of the 1208 MI B fault. Started turbine. | KRAYN-WKO-NDX-20120105 | 1
KRAYN-WKO-NDX-20120106-01 | No work order description provided by contractor | 2012-01-06 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 4.5 | Forced |  |  | 2.25 | Highland 1 | Disassemble old slip ring and clean and lube per Mersen operation and maintenance manual. ( BA_USDK248.1_REV02_DE-EN.doc) | KRAYN-WKO-NDX-20120106 | 1
KRAYN-WKO-NDX-20120106-02 | FM420 / Yaw HydBrk not open | 2012-01-06 | 2012-01-07 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 4.45 | Highland 1 | Contacted CSO East Mastertech Sean Illig and he remotely investigated the situation. After a few checks, it was determined that it was nessiccary to travel to the machine. During prework we gathered the typical parts for the FM 420, consisting of the 124K1 Relay, a throttle valve, and cleaner and rags for if a valve was sticking. Traveled to site and ascended the tower. To begin the troubleshooting I did the easiest and most common thing which was the 124K1 relay replacement. I removed the original relay and installed the new on provided by engineering for this situation, (Phoenix Contact No. 29 66 595). I then reset the machine which cleared the FM 420 Yaw Hyd Brake NOT Open, but the real test was to manually yaw the turbine while watching the yaw hyd brake pressure on NC II by going to WTG 08, Monitor, Press./Sym. Doing this revealed no discrepencies present and the turbine yawed perfectly showing the yaw hyd brake pressure at 20.17 BAR. I continued to yaw the machine out of the wind. I then got the key back on NC II and placed the turbine to auto yaw and started the machine. This made the turbine do all of the normal steps to yaw the nacelle and function as would would in normal operation. So with it yawed out of the wind it auto yawed into the wind after it's rotor brake test. This proceedure showed no descrepencies so at this time I placed the turbine back in manual stop and prepared to decend the tower. After arriving down tower I recorded the numbers and started the machine. | KRAYN-WKO-NDX-20120106 | 1
KRAYN-WKO-NDX-20120106-03 | FM420 / Yaw HydBrk not open | 2012-01-06 | 2012-01-07 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 4.45 | Highland 1 | Contacted CSO East Mastertech Sean Illig and he remotely investigated the situation. After a few checks, it was determined that it was nessiccary to travel to the machine. During prework we gathered the typical parts for the FM 420, consisting of the 124K1 Relay, a throttle valve, and cleaner and rags for if a valve was sticking. Traveled to site and ascended the tower. To begin the troubleshooting I did the easiest and most common thing which was the 124K1 relay replacement. I removed the original relay and installed the new on provided by engineering for this situation, (Phoenix Contact No. 29 66 595). I then reset the machine which cleared the FM 420 Yaw Hyd Brake NOT Open, but the real test was to manually yaw the turbine while watching the yaw hyd brake pressure on NC II by going to WTG 08, Monitor, Press./Sym. Doing this revealed no discrepencies present and the turbine yawed perfectly showing the yaw hyd brake pressure at 20.17 BAR. I continued to yaw the machine out of the wind. I then got the key back on NC II and placed the turbine to auto yaw and started the machine. This made the turbine do all of the normal steps to yaw the nacelle and function as would would in normal operation. So with it yawed out of the wind it auto yawed into the wind after it's rotor brake test. This proceedure showed no descrepencies so at this time I placed the turbine back in manual stop and prepared to decend the tower. After arriving down tower I recorded the numbers and started the machine. | KRAYN-WKO-NDX-20120106 | 1
KRAYN-WKO-NDX-20120106-04 | No work order description provided by contractor | 2012-01-06 |  | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 4.2833 | Highland 1 | Disassemble old slip ring and clean and lube per Mersen operation and maintenance manual. ( BA_USDK248.1_REV02_DE-EN.doc) | KRAYN-WKO-NDX-20120106 | 1
KRAYN-WKO-NDX-20120109-01 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 2.3167 | Highland 1 | In side each blade root locate and document each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. Damaged blade seals were documented and photographed. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-02 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 7.25 | Forced |  |  | 2.3167 | Highland 1 | Responded to several warnings (FM 700 and FM 750) present on 1/8/2012 at 10:35 when the turbine was remotly reset. Performed manual stop after arriving at turbine. Ascended turbine and locked out rotor hub via Hydac station. Rotor switch on topbox was set to manuel then pitch power (100 S1) and breakers 102F2 and 102F3 were placed in L.O.T.O. Hub entry commenced with use of hub rope. Comm. cable from the faulting slipring was disconnected from Pitch Box 1 along with all other slipring cables. the main body of the slip ring was then unbolted and placed in the hub bag. The replacement slipring was then attached. Replacement slipring is brand new and was lubbed according to maintenance instructions prior to installation. Power was returned to the hub after exiting and unpinning rotor. After decending tower Sean Illig was contacted for a restart. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-03 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 5.15 | Highland 1 | Approached turbine and put it in a manual stop. Asend the tower and locked out rotor for hub entry. L.O.T.O 100 s1, 102 f2 and 102 f3 breakers. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Unlock breakers and desend tower. Call Sean Illig for reset of the 1208 MI B fault. Started turbine. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-04 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7.1667 | Forced |  |  | 2.6667 | Highland 1 | Manually stopped turbine and accended tower. Secured nacell lid with brace, locked out the hub and locked out 102F2, 102F3 & 400 Pitch(all power to hub). Entered hub with new SlipRing and tools. Replaced old SlipRing with new SlipRing and torqued SlipRing bolts to 41NM. Zip tied all SlipRing Cables neatly, cleand up old zip ties and exited hub with old SlipRing and tools. Secured hub door, released hub pin and lowered nacell lid. Restored power to hub, decended tower, loded truck and turbine runs. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-05 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 2.25 | Forced |  |  | 2.6667 | Highland 1 | Went to top of turbine. Released pressure in hydraulic station. Disconnected valve from wires: W901, W902, W904, W 905. Removed valves. Cleaned and replaced valves. Reconnected wires. Built up pressure. Yawed turbine to check pressures. Pressures were good at 24.17. Packed up tools and went down turbine. Drove back to the O&M building and unloaded truck of parts/tools. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-06 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.8333 | Highland 1 | Climbed into the hub to get the Serial numbers from the 3 bearings. Blade 1: 8000106-0335; Blade 2: 8000106-0334; Blade 3: 8000106-0332. All 3 bearings looked good, no grease leaking from seals. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-07 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG22 | Warranty Repair | Nordex USA OandM | 0.25 | Forced |  |  | 2.8333 | Highland 1 | We went up tower to complete the lighting brush retro, but when we got up tower we saw that the retro was already complete. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120109-08 | FM6 / WTG Manual Stop | 2012-01-09 | 2012-01-09 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 8.1667 | Forced |  |  | 2.8333 | Highland 1 | Manually stopped turbine and accended tower. Secured nacell lid with brace, locked out the hub and locked out 102F2, 102F3 & 400 Pitch(all power to hub). Entered hub with new SlipRing and tools. Replaced old SlipRing with new SlipRing and torqued SlipRing bolts to 41NM. Zip tied all SlipRing Cables neatly, cleand up old zip ties and exited hub with old SlipRing and tools. Secured hub door, released hub pin and lowered nacell lid. Restored power to hub, decended tower, loded truck and turbine runs. | KRAYN-WKO-NDX-20120109 | 1
KRAYN-WKO-NDX-20120110-01 | No work order description provided by contractor | 2012-01-10 |  | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 5 | Forced |  |  | 2.3606 | Highland 1 | Overhauled removed slip ring to prepare it for the next installation. | KRAYN-WKO-NDX-20120110 | 1
KRAYN-WKO-NDX-20120110-02 | No work order description provided by contractor | 2012-01-10 |  | KRAYN-WTG12 | Retrofit | Nordex USA OandM | 5.5 | Forced |  |  | 2.6333 | Highland 1 | Overhauled removed slip ring to prepare it for the next installation. This is postwork to the slip ring change from yesterday. | KRAYN-WKO-NDX-20120110 | 1
KRAYN-WKO-NDX-20120110-03 | No work order description provided by contractor | 2012-01-10 |  | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 7 | Forced |  |  | 2.5 | Highland 1 | Overhauled removed slip ring to prepare it for the next installation. This is postwork to the slip ring change a few weeks ago. | KRAYN-WKO-NDX-20120110 | 1
KRAYN-WKO-NDX-20120112-01 | FM741 / IBS peripherals Fault | 2012-01-12 | 2012-01-12 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced | KRAYN-NDX-PRT-0634 | 1 | 3.9 | Highland 1 | Approached down turbine, trouble shoot IBS Fault, Replace HUR | KRAYN-WKO-NDX-20120112 | 1
KRAYN-WKO-NDX-20120115-01 | FM358 / LV UPSBatteryChange | 2012-01-15 | 2012-01-15 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0138 | 4 | 5.4833 | Highland 1 | Met at the shop and gathered PPE, tools and UPS battery rack for FM 358/LV UPSBatteryChange. Arrived to WTG6 shut down LPC, replaced battery rack and adjusted thermostat in IGBT cabinet to 5 degrees. UPS battery rack didn't turn the UPS on right away so we thought the UPS needed to be replaced. We then returned to shop, got new battery rack and UPS. Back on site we replaced UPS and switched out anoter battery rack. The new UPS didn't come with a new data card so we used the data card from the old UPS. We ran our test and the UPS was still unresponsive. We returned to shop one final time to get a new data card then returened to WTG6 and found that the UPS battery rack had a sufficient charge so the UPS kicked on and turbine runs. | KRAYN-WKO-NDX-20120115 | 1
KRAYN-WKO-NDX-20120116-01 | FM727 / Wind Speed Left-hand CableCut | 2012-01-16 | 2012-01-16 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0414 | 1 | 1.4833 | Highland 1 | WTG3 faulted on an FM727 & FM728 wind speed left/right-hand cable cut. Accended tower checked wire connections on 105A5 module. All wires where secure so we then pulled pins 1 & 2 to create the fault to see if fault cleared. The fault cleared but we replaced the 105A5 to see if that would keep keep the faoult from re-occuring. Fault did not re-occure we then decended tower and turbine runs. | KRAYN-WKO-NDX-20120116 | 1
KRAYN-WKO-NDX-20120116-02 | FM359 / LV UPSBatteryLow | 2012-01-16 | 2012-01-16 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 0.9 | Highland 1 | Replaced UPS data card to fix FM359, but did not correct the issue. Do not consume Ups data card. Accended tower, installed heater to raise hyd oil temp. Decended tower turbine runs. | KRAYN-WKO-NDX-20120116 | 1
KRAYN-WKO-NDX-20120117-01 | FM359 / LV UPSBatteryLow | 2012-01-17 | 2012-01-17 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 1.9 | Highland 1 | Arrived at WTG6. Looked up module 151A3 in bottom box schematics removed jumper from pins 9 & 25 and signal went low. We then pluged in signal wire to pin 9 and signal went high. We ran the turbine up and as soon as it cut in the signal blinked low, high, low and then faulted. After the turbine faulted we triped 153F3 and 153F4 brakers to kill power to the 151A3 module. We then replaced 151A3 with a new module and restored power. Our next step was to replace the battery rack in the UPS with a fully charged battery rack when we noticed arck marck's in the plug form the battery pack to the UPS. We replaced the marked up plug with a new plug which made a stronger connection. We ran the turbine up and the fault cleared. We waited thirty minutes to make sure fault didn't return. | KRAYN-WKO-NDX-20120117 | 1
KRAYN-WKO-NDX-20120118-01 | FM741 / IBS peripherals Fault | 2012-01-18 | 2012-01-19 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 3.2 | Highland 1 | Arrived at tower in response to FM736. Diag+ was run and component HU 72A1 was identified. HUR was hard reset and the fault cleared. Kelly Miller was contacted for an MI Class B reset and the turbine was started without faults. | KRAYN-WKO-NDX-20120118 | 1
KRAYN-WKO-NDX-20120120-01 | FM402 / Yaw CableTwist Limitswitch reached | 2012-01-20 | 2012-01-21 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 25.75 | Forced |  |  | 20.4833 | Highland 1 | Prework consisted of preparing a yaw position encoder (cam switch) for installation. This was decided because of the fact that the turbine faulted for the limit switch instead of performing a cable rewind. Drove to WTG 12. Accended the tower and began the removal and replacement of the yaw cam switch encoder. We yawed the turbine off of the limit switch by depressing the yaw override button and manually yawing turbine. Once the turbine was yawed back to the zero cable twist we verified that it visually by going down to the service deck and looking at the cable drip. Once verified we began the actvual removal of the yaw cam switch encoder. To do this the interbus was shut down using the breakers 104F2 and 104F3 so that the interbus would not get damaged during the removal. After the original encoder was removed the new encoder was electricly connected and the 104F2 and 104F3 where reset. With that the new encoder was spun until it should 0 degrees of cable twist. Once that was obtained the encoder could have its cams aligned. To do this the gear on the encoder is turned 37 times CW then the switchs for CW are adjusted S1 to just open and S3 to just close. Then after that spin the encoder gear CCW 74 times and adjust the CCW switches S2 to be just opening and S4 to be just closing. After this is complete the encoder can be physical installed on the yaw gear. Once the installation is complete we performed a 990 degree test to see if the turbine would cable rewind or fault for the limit switch. So at 1180 degrees i manually stop the turbine from yawing becasue the cam switch did not. With this we atenpted to adjust the encoder cam switches again then spin it to 1180 and install the encoder. This did not work! So we manually yawed the turbine back towards 0 and visually checked the cable twist and stopped it at 0. Preformed the cam adjustment one more time at 0 and installed the encoder. This time the numbers appeared correct and we manually yawed the turbine. The 990 degree test was not performed due to the lack of time. The wind speeds where rising and the temp was falling. Returned down tower and reset the turbine then had Daniel Sibla reset the 1209 MI class B fault so that I could start the machine. | KRAYN-WKO-NDX-20120120 | 1
KRAYN-WKO-NDX-20120121-01 | FM50 / SafetyChain Activated | 2012-01-21 | 2012-01-21 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 3.25 | Forced |  |  | 12.0333 | Highland 1 | Technicians pulled trigger files from SEG 5.2; compared micrologic on Q10 with another turbine, re-engaged breakers and returned turbine to service. Returned to shop, forwarded trigger files in consultation with Master Tech. Will continue to monitor. | KRAYN-WKO-NDX-20120121 | 1
KRAYN-WKO-NDX-20120122-01 | FM6 / WTG Manual Stop | 2012-01-22 | 2012-01-23 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 14.0667 | Highland 1 | Engineer's Charles Stauffer and Rob Todd where testing the generator heater retro in WTG22. | KRAYN-WKO-NDX-20120122 | 1
KRAYN-WKO-NDX-20120123-02 | FM55 / GenRot RpmMonitor Stop | 2012-01-23 | 2012-01-24 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.4833 | Highland 1 | Looked at the turbine on NC II and discovered that in the logs they show that there was an FM 55 GenRot RPMMonitor Stop. This usually points towards the inductive sensors on the Rotor side but not always so I then fast logged all of the speed sensors and the gen encoder for compairision. The FM 50 safety chain was also placed on the fast log to illistrate when the faults began. The fast log looked very good but sometimes just the slightest hick-up with those sensors can cause this set of faults. So with this we grabbed two sensors and headed out to site. Apon arrival at the site we took extra time to evaluate the surrounding conditions due to the heavy ice that was seen earlier. It was determined safe and clean of ice so we went up. Once in the nacelle we inspected the inductive sensors and there mounting arm. The system failed the "Shake" test and we loosened both of the sensors and adjusted both of them to 4mm's of gap and tighened the sensors back down. Performed the shake test and it was good. Returned down tower and started the turbine with no further defects noted. | KRAYN-WKO-NDX-20120123 | 1
KRAYN-WKO-NDX-20120123-03 | FM1208 / MI class B Fault | 2012-01-23 | 2012-01-23 | KRAYN-WTG11 | General Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 3.25 | Highland 1 | Gathered safety equipment and loaded truck. Drove to WTG #11. While on location Brad Foy of EP decided that with the icy weather conditions and fog that the park was unsafe to travel or work on. Force Majure was instated. The service techs returned to shop and unloaded vehicle. Everpower contacted Sean illig (once the park was deemed safe) to restart the turbine. | KRAYN-WKO-NDX-20120123 | 1
KRAYN-WKO-NDX-20120123-04 | FM55 / GenRot RpmMonitor Stop | 2012-01-23 | 2012-01-24 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.4833 | Highland 1 | Looked at the turbine on NC II and discovered that in the logs they show that there was an FM 55 GenRot RPMMonitor Stop. This usually points towards the inductive sensors on the Rotor side but not always so I then fast logged all of the speed sensors and the gen encoder for compairision. The FM 50 safety chain was also placed on the fast log to illistrate when the faults began. The fast log looked very good but sometimes just the slightest hick-up with those sensors can cause this set of faults. So with this we grabbed two sensors and headed out to site. Apon arrival at the site we took extra time to evaluate the surrounding conditions due to the heavy ice that was seen earlier. It was determined safe and clean of ice so we went up. Once in the nacelle we inspected the inductive sensors and there mounting arm. The system failed the "Shake" test and we loosened both of the sensors and adjusted both of them to 4mm's of gap and tighened the sensors back down. Performed the shake test and it was good. Returned down tower and started the turbine with no further defects noted. | KRAYN-WKO-NDX-20120123 | 1
KRAYN-WKO-NDX-20120124-01 | FM6 / WTG Manual Stop | 2012-01-24 | 2012-01-24 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 0.78333 | Highland 1 | Prepared to go shut down the turbine after engineering's request to inspect the yaw brake retro which was previously installed. Apon arrival at the turbine Rob the engineer recorded the yawing function and sounds from the exterior before we shut down the turbine. Once finished with that we stopped the turbine and Rob climbed the tower to inspect the installation during which the turbine was manually yawed CW and CCW. With his DATA gathered Rob returned down tower and the machine was started. | KRAYN-WKO-NDX-20120124 | 1
KRAYN-WKO-NDX-20120124-02 | FM0 / WTG System ok | 2012-01-24 |  | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 6.25 | Forced |  |  | 12.0333 | Highland 1 | Nordex Technicians took operating trigger files and pulled an SUR error file in order to troubleshoot FM1208s from Friday, Saturday, and Monday. Sean illig worked with SEG after going to the turbine to figure out what the next steps would be. 1/25/12, today Sean Illig went out to the tower to reformat the card and get it ready to run at full power to get more triggers. | KRAYN-WKO-NDX-20120124 | 1
KRAYN-WKO-NDX-20120125-01 | FM1208 / MI class B Fault | 2012-01-25 | 2012-01-26 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 3.65 | Highland 1 | Turbine faulted after being started a few hours earlier after a generator grounding ring replacement. From NC II logs I found that the turbine never ran due to low winds and when it tried to cut in it faulted. This pointed to something cause by the previous work that day. With that the only thing relate between the MI fault and the previous work was the generator shaft encoder. So we traveled to site and tried to commission the convertor which balances the generator shaft encoder. After a long wait the winds came up just enough to get in the speed window to commission. During the last step the convertor faulted again. The wind speeds had falling and the generator speed was near 930RPM so we thought maybe it faulted becasue of the low wind but where not clear. So I climbed the tower and double checked the generator shaft encoder for proper installation and found it to have no defects to note. After resting and climbing back down tower we tried again to commission the convertor but the winds where very low. We kept the turbine spinning until finally we got enough wind to sustain the speed window and finish the commissioning work. Started the turbine with no defects noted at this time. Returned to the shop. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-02 | FM6 / WTG Manual Stop | 2012-01-25 | 2012-01-25 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 5.3833 | Highland 1 | Gathered all tooling to perform a removal and replacement of the generator grounding slip ring. Travel to everpower and obtained the proper permit to preform the hot work necessary for the task of removing and replaceing the generator grounding slip ring. Travel to site. Tripped the Q10P and placed in the OFF position with the proper PPE and LOTO. Climbed the turbine and set up the chain hoist then lowered the chain. We were able to send all of the necessay tooling and equipment in one trip with the chain hoist. Removed the generator covers around the slip ring area and verified no voltage on the rotor. Ran an extention cord to the yaw deck and plugged it into a hot plate then laid the new grounding ring on the hoty plate. Removed the entire aft section of the slip ring box including the shaft encoder to expose the MV cabling and other retaining parts. Removed the MV cabling and the bung for the shaft encoder. Installed the slip ring removal devices and attached the hydraulic ram to them. With a enerpac pump attached to the ram we slowly pulled the slip ring off of its tappered shaft. Installed heat blankes all over the slip ring box inter and outer area to protect everything from the hot work. Set up the torch and began to heat the original grounding slip ring which after about 5 minutes was ready to easily be pulled of of the shaft by hand. After an inpection of the shaft and surrounding area the new slip ring was taken from the hot plate and installed smoothy by hand onto the tappered shaft. With that in place we cleaned the rotor slip ring and installed it onto the alignment tooling and slid it onto the tapper shaft aligning the key and key way while slideing the rings on. To finish the installation more tooling is installed to pull the ring assembly back flush to the grounding slip ring. Removed all of the equipment and pulling devise from the back of the generator. Installed corrisponding hardware and MV cables. Re-assembled the aft section of the slip ring box and installed the safety devices on the bolt heads. Installed new grounding ring brushes and performed the cleaning of the generator slip ring actions. Closed up the generator slip ring area and orginized tools and equipment to lower down tower with the chain hoist. Lowered tooling and equipment down tower and returned the chain hoist to its stowed position. Removed the roof supports and closed the roof and latched. Climbed down tower and removed LOTO for the Q10P and placed it into ON with the apropriate PPE. Cleared alarms and started the turbine. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-03 | FM1208 / MI class B Fault | 2012-01-25 | 2012-01-25 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.58333 | Highland 1 | Had to do a grid disconnect to be able to work on the Micro logics.Replaced the micro logic on the Q10 breaker to the new style | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-04 | FM6 / WTG Manual Stop | 2012-01-25 | 2012-01-25 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7.75 | Forced |  |  | 4.9167 | Highland 1 | After turbine was placed in manuel stop the turbine was ascended and yawed manually to set acuall cable twist to zero. Parameter P15.02 was given a different value and NC2 confirmed that cable twist was 0 degrees. P15.02 was then set to 0. The nacelle was yawed to meet the predetermined north. Cable twist was then determined through NC2 and the value was given to P15.00. The nacelle was then manually yawed to the limit switch without triggering it. The yaw position was determined through NC2 and this value was entered into P15.01. The yaw encoder cam switches were adjusted. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-05 | FM6 / WTG Manual Stop | 2012-01-25 | 2012-01-25 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 4.3833 | Highland 1 | Main bearing has been running warm. WTG # 13 was shut down and ascended in order to determine wheather or not the ALU has been working properly. The ALU was forced both high and low and was determined to be operable. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-06 | FM6 / WTG Manual Stop | 2012-01-25 | 2012-01-25 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 4.3833 | Highland 1 | A skylight was discovered broken. Parts and tools were delivered from shop and hoisted via jib crane into the nacelle. Pieces of the old skylight were unbolted and removed. The old silkaflex was scraped off and fresh was applied. The new skylight was adhered to the roof and fresh holes were drilled to accomidate larger bolts. The skylight was then bolted down and fresh caulk was applied to the bolt holes and the edges. Cracks in the nearby skylight were also caulked as well as a hole left from a missing roof hatch latch. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120125-07 | FM172 / Gear BypFliterPmp Fuse Trip | 2012-01-25 | 2012-01-25 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.43333 | Highland 1 | Climbed up tower, opened topbox and switiched 112AQ1 gearbox bypass oil filter fuse back on. Climbed down tower, cleared fault and wind was below start condition. | KRAYN-WKO-NDX-20120125 | 1
KRAYN-WKO-NDX-20120127-01 | FM1173 / Pitch1 Batt.contactor Error | 2012-01-27 | 2012-01-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 24.2333 | Highland 1 | Approached WTG and found blade one pitched at 8 degrees and turbine yawed 90 degrees out of the wind. Listened for sounds coming out of the hub and heard nothing due to yaw position of the naccelle. Winds to high to enter the hub or the turbine. Informed Everpower and checked forcast for an open window in the wind to troubleshoot hub, informed Jennings Lynch (on call) about the situation. Forcast showed a window for 1/28/2012 in the moring and we planned to start at 6:00 am. | KRAYN-WKO-NDX-20120127 | 1
KRAYN-WKO-NDX-20120128-01 | FM1173 / Pitch1 Batt.contactor Error | 2012-01-28 | 2012-01-28 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 24.2333 | Highland 1 | Climbed turbine. Locked out hub. Applied manual rotor brake. Climbed out into the hub. Inspected all blade areas, cables, pitch blocks, pitch drives, and cabinets. Found broken blade bolt in Pitch area 2. Bolt's location was from pitch are 3, Position 31. Removed broken blade bolt with nut and washer. Found multiple broken bottles. Replaced 6 bottles. Wiped/cleaned excess grease off of entry points, cables, and any other areas necessary. Collected all materials. Climbed back out to the nacelle. Unlocked rotor brakes. Unpinned rotor. Climbed back down turbine. Reset faults. Restarted Turbine. | KRAYN-WKO-NDX-20120128 | 1
KRAYN-WKO-NDX-20120202-01 | FM6 / WTG Manual Stop | 2012-02-02 | 2012-02-02 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.1667 | Highland 1 | Nordex technicians approached turbine to change slip ring. Upon climbing turbine, Martin discovered chain hoist control cable to be severed. Needing another technician downtower to maintain the tag line during hoist of slip ring, Martin had to climb down to acquire specific tools to repair cable. Did so. Then climbed back up to repair cable. Butt spliced severed conductors. Then drove on. | KRAYN-WKO-NDX-20120202 | 1
KRAYN-WKO-NDX-20120202-02 | FM6 / WTG Manual Stop | 2012-02-02 | 2012-02-02 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 8.2333 | Highland 1 | While in Hub; took hammer and lightly tapped each blade bolt for sound. Each bolt had a slight pinging sound. No bolt was determined to be damaged per this test. | KRAYN-WKO-NDX-20120202 | 1
KRAYN-WKO-NDX-20120202-03 | FM6 / WTG Manual Stop | 2012-02-02 | 2012-02-02 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 5.5 | Forced |  |  | 8.2333 | Highland 1 | After troubleshooting and repairing hoist; lifted slipring and tools is basket. Asend the tower and locked out rotor for hub entry. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Went back out to the nacelle. Faults did not clear from a FM705. Slip ring was determined to be the issue. Had other techs bring neew slip ring. Lowered basket attached to hoist for slip ring. Brought up new slip ring. Took the next cleaned/reconditioned slip ring out to HUB. Installed reconditioned slip ring. Faults cleared on this attempt. brought all tools out of hub. Did other required inspections. | KRAYN-WKO-NDX-20120202 | 1
KRAYN-WKO-NDX-20120202-04 | FM6 / WTG Manual Stop | 2012-02-02 | 2012-02-02 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 8.2333 | Highland 1 | In side each blade root located and documented each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. Damaged blade seals were documented and photographed. | KRAYN-WKO-NDX-20120202 | 1
KRAYN-WKO-NDX-20120203-01 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 6.2833 | Highland 1 | Took pictures of blade SN. Blade1 SN:1516. Blade2 SN:1511. Blade3 SN:1515. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-02 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 6.2833 | Highland 1 | Ping tested blade bolts and all blade bolts passed. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-03 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.2833 | Highland 1 | Shut down turbine and accended tower. Locked out hub, killed 102F2, 102F3, 400V pitch (all power to hub). Replaced old slip ring with new slipring, zip tied cables neatly. Exited hub with old slipring and tools, colosed hub door. Cleared MI class B and turbine runs. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-04 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.2833 | Highland 1 | Replaced Old snap hooks with new snap hooks. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-05 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 6.2833 | Highland 1 | Took pictures of blade SN. Blade1 SN:1516. Blade2 SN:1511. Blade3 SN:1515. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-06 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 6.2833 | Highland 1 | Ping tested blade bolts and all blade bolts passed. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-07 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6.2833 | Highland 1 | Shut down turbine and accended tower. Locked out hub, killed 102F2, 102F3, 400V pitch (all power to hub). Replaced old slip ring with new slipring, zip tied cables neatly. Exited hub with old slipring and tools, colosed hub door. Cleared MI class B and turbine runs. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-08 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.2833 | Highland 1 | Replaced Old snap hooks with new snap hooks. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-09 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 5.3833 | Highland 1 | Upon arrival uptower, Martin found copious amounts of oil on yaw deck, origin: offline oil filter. Estimate appx. 1 gallon. After changing slip ring (see other Service Order), Martin and Huss had rags and cleaner sent up. Area under filter housing cleaned, as well as pooled oil on yaw deck. Due to a time constraint, further work will be required to clean the rest. All connections were tightened. The offline filter pump was forced high and observed, no further leakage detected. Will make note of further cleaning need and attend at next servicing or maintenance. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-10 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 5.35 | Highland 1 | While in Hub; took hammer and lightly tapped each blade bolt for sound. Each bolt had a slight pinging sound. No bolt was determined to be damaged per this test. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-11 | FM6 / WTG Manual Stop | 2012-02-03 | 2012-02-03 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 5.25 | Forced |  |  | 5.35 | Highland 1 | After troubleshooting and repairing hoist; lifted slipring and tools is basket. Asend the tower and locked out rotor for hub entry. Using hub rope, entered hub with tools and slip ring. Procceded to disassemble old slip ring and install new slip ring. Did check of the hub for tools and parts, secured hub door. Went back out to the nacelle. Cleared faults. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120203-12 | No work order description provided by contractor | 2012-02-03 |  | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 7.3833 | Highland 1 | Overhauled old slipring for new installation per engineering and new Dietrich instructions. | KRAYN-WKO-NDX-20120203 | 1
KRAYN-WKO-NDX-20120204-01 | FM6 / WTG Manual Stop | 2012-02-04 | 2012-02-04 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 5.75 | Forced |  |  | 2.5 | Highland 1 | Removed hub slip ring and installed cleaned and lubed unit. Installed unit has been cleaned, inspected, and lubed per the dietrich manual and Nordex Engineering. While performing this we also ping tested the blade bolts to assure no broken bolts and to aviod any damage that a broken bolt cause. This only takes a few minutes for all three blades ping tests. After returning to the shop the removed slip ring was broke down, cleaned, inspected, lubed, and rebuilt. | KRAYN-WKO-NDX-20120204 | 1
KRAYN-WKO-NDX-20120204-02 | FM6 / WTG Manual Stop | 2012-02-04 | 2012-02-04 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 2.5 | Highland 1 | BL1:Date:03-08 SN:8000106-024 BL2:Date:12-07 SN:0040096500-0008 BL3:Date:03-08 SN:8000166-0273 All three blade bearings looked clean on the inside and the outside, no excessive greese. | KRAYN-WKO-NDX-20120204 | 1
KRAYN-WKO-NDX-20120204-03 | FM6 / WTG Manual Stop | 2012-02-04 | 2012-02-04 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.43333 | Forced |  |  | 2.5 | Highland 1 | Took appart lowspeed shaft covers and lowered with hoist. | KRAYN-WKO-NDX-20120204 | 1
KRAYN-WKO-NDX-20120204-04 | FM6 / WTG Manual Stop | 2012-02-04 | 2012-02-04 | KRAYN-WTG17 | Retrofit | Nordex USA OandM | 6.5 | Forced |  |  | 2.4833 | Highland 1 | Removed hub slip ring and installed cleaned and lubed unit. Installed unit has been cleaned, inspected, and lubed per the dietrich manual and Nordex Engineering. While performing this we also ping tested the blade bolts to assure no broken bolts and to aviod any damage that a broken bolt cause. This only takes a few minutes for all three blades ping tests. After returning to the shop the removed slip ring was broke down, cleaned, inspected, lubed, and rebuilt. | KRAYN-WKO-NDX-20120204 | 1
KRAYN-WKO-NDX-20120206-01 | FM6 / WTG Manual Stop | 2012-02-06 | 2012-02-06 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 3 | Highland 1 | Nordex Technicians replaced 124K1 with new relay during the scheduled slip ring changeout (different service order). | KRAYN-WKO-NDX-20120206 | 1
KRAYN-WKO-NDX-20120206-02 | FM6 / WTG Manual Stop | 2012-02-06 | 2012-02-06 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 3 | Highland 1 | Nordex Technicians changed snap-rings on the hub hatch during the scheduled slip ring changeout (different service order). | KRAYN-WKO-NDX-20120206 | 1
KRAYN-WKO-NDX-20120206-03 | FM6 / WTG Manual Stop | 2012-02-06 | 2012-02-06 | KRAYN-WTG19 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 2.9667 | Highland 1 | In side each blade root located and documented each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. Damaged blade seals were documented and photographed if needed. | KRAYN-WKO-NDX-20120206 | 1
KRAYN-WKO-NDX-20120206-04 | FM6 / WTG Manual Stop | 2012-02-06 | 2012-02-06 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0725 | 1 | 2.9667 | Highland 1 | Shut down turbine, accended tower via ladder, lifted and secured nacelle lid. Lowered hoist and lifted tools, hub rope and New SlipRing into nacelle. Killed 102F2, 102F3, 400V Pitch (all power to hub). Locked out rotor. Carried tools and Cleaned SlipRing into hub. Repalced SlipRing, Lowered Dirty SlipRing, secured hoist, un locked rotor and restored all power to hub. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120206 | 1
KRAYN-WKO-NDX-20120207-01 | FM6 / WTG Manual Stop | 2012-02-07 | 2012-02-07 | KRAYN-WTG14 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 4.4 | Highland 1 | Traveled to site with cleaned and lubed slip ring. Performed ground support duties by loading and rigging chain hoist to craning bucket and tough bags for hoisting. Then took on the tag line control duties by assuring the load stayed clear of the tower and nacelle during its chain up commad. Performed the same duties during the chain down command with the tag line. Once the load reached the pad I unsecured the load and gave the chain up command and controled the tag line unitl it was raised back to to nacelle. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120207-02 | FM50 / SafetyChain Activated | 2012-02-07 | 2012-02-07 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 0.81667 | Highland 1 | Arrived at turbine in response to FM 50. Hit safety chain reset button on the bottom box which cleared the safety chain. NC2 faults all cleared after a few minutes and the turbine started up without faults or warnings. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120207-03 | FM6 / WTG Manual Stop | 2012-02-07 | 2012-02-07 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 3.7667 | Highland 1 | Trouble shot FM 386 and 385. began down tower with W1001 terminations in the HUR. The ferrals were removed from W1001 was placed back into terminal strip X4 as bare wires. After climbing tower this same process was done to W1001 at terminal strip X9 in the topbox. The wiring of all termination points was checked including W1000 into X9 in the topbox. All wiring was found to be correct and intact. After Master Sean Illig changed a parameter in the HUR the faults cleared and the turbine ran. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120207-04 | FM6 / WTG Manual Stop | 2012-02-07 | 2012-02-07 | KRAYN-WTG21 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 3.7667 | Highland 1 | Went to hub entrance hatch. Checked the condition of the carabiners attached to the spring for the hub door latches. Condition was determined to be in poor quality. Replaced snap hooks/carabeaner on spring. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120207-05 | FM6 / WTG Manual Stop | 2012-02-07 | 2012-02-07 | KRAYN-WTG21 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 3.7667 | Highland 1 | Used Procedure/service document to apply "Warning" and "Danger" stickers to top box, pitch box, and generator. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120207-06 | FM6 / WTG Manual Stop | 2012-02-07 | 2012-02-07 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.7667 | Highland 1 | Shut down turbine, accended tower via ladder, lifted and secured nacelle lid. Lowered hoist and lifted tools, hub rope and New SlipRing into nacelle. Killed 102F2, 102F3, 400V Pitch (all power to hub). Locked out rotor. Carried tools and Cleaned SlipRing into hub. Repalced SlipRing, Recorded blade bearing serial numbers and installed new snap hooks. Ping tested all blade bolts then lowered dirty SlipRing, secured hoist, un locked rotor and restored all power to hub. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120207 | 1
KRAYN-WKO-NDX-20120208-01 | FM1210 / MI Synchronization TimeOut | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 1.3667 | Highland 1 | Balanced gen encoder with the SEG touchscreen. Started the turbine and it never cut in then timed out. Found the SEG control still in maintenance so we put it to auto and started the turbine. Still did not cut in and timed out again. Re-balanced the encoder and completed the commissining steps and placed the SEG in Auto. Started the turbine and no further defects noted at this time. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-02 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 2.25 | Forced |  |  | 3.8333 | Highland 1 | Opened cabinet. Took out old 124K1 relay. Installed brand new black 124K1 relay for preventative maintenance. Turned power back on. cleared faults. Put tools on hoist to send down. Set hoist back up in stow position. Unpinned rotor. Closed lid. Climbed back down. Started turbine. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-03 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 3.8333 | Highland 1 | In side each blade root located and documented each blade bearing serial number. Un pin the hub and pinwheel rotor to inspect all blade seals. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-04 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 3.8333 | Highland 1 | Used Procedure/service document to apply "Warning" and "Danger" stickers to top box, pitch box, and generator. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-05 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0501 | 1 | 3.8333 | Highland 1 | Tripped braker 104F3 killing power to 105A2 module and 115V2 or A2 module. Replaced old 115V2 module with new module and landed all wires in propper pin. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-06 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 3.8333 | Highland 1 | Removed low speed shaft covers and break cover on high speed side then hooked them up to hoist. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-07 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.8333 | Highland 1 | Shut down turbine, accended tower via ladder, lifted and secured nacelle lid. Lowered hoist and lifted tools, hub rope and New SlipRing into nacelle. Killed 102F2, 102F3, 400V Pitch (all power to hub). Locked out rotor. Carried tools and Cleaned SlipRing into hub. Repalced SlipRing, Recorded blade bearing serial numbers and installed new snap hooks. Ping tested all blade bolts then lowered dirty SlipRing, secured hoist, un locked rotor and restored all power to hub. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-08 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 4.0667 | Highland 1 | Replaced 124K1 | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-09 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 4.0667 | Highland 1 | Documented information (serial numbers and manufature dates) for blade bearings. Also inspected blade bearing seals and took a photo of a bad seal. See below for blade bearing information… | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-10 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced | KRAYN-NDX-PRT-0358,KRAYN-NDX-PRT-0501 | 1,1 | 4.0667 | Highland 1 | Replaced 115V2 (overvoltage protection) after isolating power at 104F3. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-11 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3.1667 | Forced |  |  | 4.0667 | Highland 1 | While rotor lock and brake remained engaged, the shaft covers connected to the gearbox were removed and sent down tower via jib crane for weld repairs/reinforcements. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120208-12 | FM6 / WTG Manual Stop | 2012-02-08 | 2012-02-08 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 0.16667 | Forced |  |  | 4.0667 | Highland 1 | Adhered top box (2), pitch box (6), and generator stator box (1) stickers according to procedure. | KRAYN-WKO-NDX-20120208 | 1
KRAYN-WKO-NDX-20120209-01 | No work order description provided by contractor | 2012-02-09 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 2.25 | Highland 1 | Tore down the hub slip ring which was removed the previous day. Cleaned, inspected, and lubed slip ring and placed on shielf. | KRAYN-WKO-NDX-20120209 | 1
KRAYN-WKO-NDX-20120212-01 | FM50 / SafetyChain Activated | 2012-02-12 | 2012-02-12 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 14.1333 | Highland 1 | Reset an FM 50: reset Q10P, pushed the reset button on the Q10. Made observations about an abnormality on the Q10P phases. (Master Tech Illig notified). Called someone with 400 access to reset it. (Kelly Miller). | KRAYN-WKO-NDX-20120212 | 1
KRAYN-WKO-NDX-20120212-02 | FM853 / Hyd OilTemp L Warn | 2012-02-12 | 2012-02-12 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 10.75 | Highland 1 | Accended turbine, noticed no heater which caused hyd station to fault out for being too cold. Decended tower, went back to shop for new heater. Returened to site, accended tower, wired up new heater and turned it on. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120212 | 1
KRAYN-WKO-NDX-20120212-03 | FM50 / SafetyChain Activated | 2012-02-12 | 2012-02-12 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 4.0833 | Highland 1 |  | KRAYN-WKO-NDX-20120212 | 1
KRAYN-WKO-NDX-20120213-01 | FM0 / WTG System ok | 2012-02-13 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 14.1333 | Highland 1 | Pulled triggers from the SUR from 2.12.2012. Copied the event logs. Sent this information to the CSO East Mastertech Sean Illig. | KRAYN-WKO-NDX-20120213 | 1
KRAYN-WKO-NDX-20120213-02 | FM0 / WTG System ok | 2012-02-13 |  | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 2.8333 | Highland 1 | Pulled triggers from the SUR from 2.12.2012. Copied the event logs. Sent this information to the CSO East Mastertech Sean Illig. | KRAYN-WKO-NDX-20120213 | 1
KRAYN-WKO-NDX-20120215-01 | FM50 / SafetyChain Activated | 2012-02-15 | 2012-02-15 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 2.7833 | Highland 1 | Reviewed logs after fault and noticed they pointed at the slip moduals. Gathered one of each of the moduals and headed for site. This machine has had a short history of related faults which lead us to believe there could be a connection problem but took the moduals just incase. Arrived at the tower and climbed to the nacell. After arriving at the top box we found one wire "10" on modual 142A6 not completly in its connection. Performed the tug test which showed two things, one that the wire was loose and that the corrisponding light on the interbus would flicker on and off, (105A3 position 48). We relanded all wires on the slip moduals which showed that all three wire on the same connector where not tightened. Assured all connections where tight and good and returned down tower. Started the turbine and returned to the shop. | KRAYN-WKO-NDX-20120215 | 1
KRAYN-WKO-NDX-20120216-01 | FM50 / SafetyChain Activated | 2012-02-16 | 2012-02-16 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 8.05 | Highland 1 | Looked at fault logs and trends on NCII at shop to see what we may need in field. Drove to turbine. Climbed up turbine. Found that the 142A6 module energizes the DIN rail via its 24 V connection at pins 11 and 12; and the DIN rail energizes 142A7, A8, A9. Checked for a problem with the energization of the DIN rail and modules attached. These signals were not disrupted and appeared to be in synch throughout the fault. We duplicated an FM 55 by pulling a sensor plug from 142A9 (the gen inductive sensor) at 16:45:06. This error list appeared identical and in the same order as the fault that occurred at 9:38. This shows that the fault at 9:38 was due to a perceived slip between rotor and gen speeds. We tested connections at 105A3 pins 48 and 64 and at 142A6 pins 7 & 10, the connection appeared solid. We tested the connection of the modules at the DIN rail, all appeared solid. We checked the spacing and connections of the 4 inductive sensors, tightening the electrical connections slightly on a few, and adjusting the spacing of one of the rotor side sensors. We switched all the sensor wires with their connections at 142A7 and A8, with their corresponding connections on A9 to troubleshoot if the module or sensor is bad . The sensor fault will be demonstrated clearly on an NCII fast log, because the bad sensor will be directed to the analog input module 105A6 or 105A5. Then, climbed back down turbine. Reset faults. Restarted turbine. Drove to EP to double check that there were no faults; as EP is on the way. Drove back to O&M building. | KRAYN-WKO-NDX-20120216 | 1
KRAYN-WKO-NDX-20120217-01 | FM493 / Yaw SensTrack 1(90&deg | 2012-02-17 |  | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 2.4333 | Highland 1 | Looked at the fault logs and reset the turbine. The turbine started and cut in but faulted after receiving the yaw command. Tried to manually yaw the turbine but faulted. Traveled to the tower and climbed up to the nacell. Once there we used the manual control to yaw which activated the yaw motor brakes, yaw hydro brakes and finally the yaw motors which all worked properly until the turbine faulted. Removed the top fan covers on the yaw motors and jumped out the motors brakes to release them. Turned each yaw motor by hand and made 40 revolutions on both motors. Should have only been 20 so we moved down into the belly and manually yawed which revealed that the motors where turning but the drives where not. NEEDS NEW YAW DRIVES! Retuned down tower and disabled switch rights. Returned to the shop. | KRAYN-WKO-NDX-20120217 | 1
KRAYN-WKO-NDX-20120218-01 | FM493 / Yaw SensTrack 1(90&deg | 2012-02-18 |  | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 2.4333 | Highland 1 | Gathered all tools and equipment needed to remove the yaw drives. Loaded the truck and traveled to site. One tech climbed up and lowered the chain hoist while the other controled the tag line and attached the tools and equipment. Once the chain hoist arrived up to the nacelle with the tools and equipment the other tech on the ground climbed up into the nacelle. We then began to remove the neccessary things to allow for the yaw drives to be removed. The deck plates around the drives were removed along with the the oil lines on the drives. Next the 400 VAC and 24 VDC was LOTO'ed and the motors where unwired and removed. From there we used the hytorc and the MXT1 with a 36MM socket and loosened all of the yaw drive bolts then removed all of the bolts with an impact gun leaving 2 bolts in each drive tighened with the impact for easy removal when the drives get changed. Marked the backlash ring and returned down tower. | KRAYN-WKO-NDX-20120218 | 1
KRAYN-WKO-NDX-20120218-02 | FM414 / Yaw MotBrake not open | 2012-02-18 | 2012-02-19 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 3.0333 | Highland 1 | Approached down turbine and checked yaw motor brakes on NC2, climbed tower and checked yaw motor brakes for release, found yaw motor by the hoist to have a loose jam nut on the micro switch asjustment screw. Readjusted screw and checked other moter for same thing, checked for simotanios release of both brakes, reset turbine and tested yaw. Climbed down and started turbine. | KRAYN-WKO-NDX-20120218 | 1
KRAYN-WKO-NDX-20120220-01 | FM6 / WTG Manual Stop | 2012-02-20 | 2012-02-20 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 5 | Highland 1 | Assisted SKF employee Michael in setting up test equiptment. | KRAYN-WKO-NDX-20120220 | 1
KRAYN-WKO-NDX-20120220-02 | FM493 / Yaw SensTrack 1(90&deg | 2012-02-20 |  | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 15.5 | Forced |  |  | 2.0833 | Highland 1 | Ascended turbine with WTS and their previously untested crane system in an attempt to perform two yaw stack change outs. After assembling the final crane the first pick was attempted. The crane managed to pull the first yaw stack out of the turbine and over the side. As it was being slowly lowered the cable began to birdcage and the pick was aborted. The stack was brought back into the turbine and set back into it's rightful place. The cranes were then dissasambled but left uptower. The operation will be reattempted when WTS secures a new cable and completes correspondence with Nordex's engineering department. | KRAYN-WKO-NDX-20120220 | 1
KRAYN-WKO-NDX-20120220-03 | FM100 / GenRot RpmSensor CollFault | 2012-02-20 | 2012-02-20 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 3.8167 | Highland 1 | Climbed turbine. Double checked the high speed shaft for physical slip. Set up computer to reload parameters into the Pepperl & Fuchs module. Made connection with plug. Software on the computer was not connecting to the module. Had to restore everythign to how it was to return later with correct software. climbed down turbine. Restarted turbine. | KRAYN-WKO-NDX-20120220 | 1
KRAYN-WKO-NDX-20120221-01 | FM347 / LV InsulatMonitor 660V Warn | 2012-02-21 | 2012-02-21 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 1.9167 | Highland 1 | Went out to EP's shop to pick up Michael Hon, SKF representative sent out to fix the FM 347. Went over the JSA with him, drove to site, ascended tower, downloaded data, prepared his PQA for the next day's data acquisition. Dropped Hon off back at EP's shop, returned to Geistown. | KRAYN-WKO-NDX-20120221 | 1
KRAYN-WKO-NDX-20120222-01 | FM254 / Hyd OilPmpRuntime long | 2012-02-22 | 2012-02-23 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0029 | 30 | 8.75 | Highland 1 | Climbed turbine. Moved hyd oil up tower. Disassembled hydraulic brake lines to drain hyd station. Removed yaw hydraulic brake valve, replaced with cap. Filled system with flushing fluid and ran hyd pump for several minutes. Drained flushing hydraulic fluid. Refilled hyd station. moved jugs of hyd fluid downtower. | KRAYN-WKO-NDX-20120222 | 1
KRAYN-WKO-NDX-20120222-02 | FM100 / GenRot RpmSensor CollFault | 2012-02-22 | 2012-02-22 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced | KRAYN-NDX-PRT-0567 | 1 | 9.1 | Highland 1 | Climbed turbine. Set up computer to reload parameters into the Pepperl & Fuchs module. Replaced 142A6. Also switched the 105A2 and the 105A3 Module for confirmation that the modules were good. Made connection with plug in the 142A9. Software on the computer was not connecting to the module. Climbed down turbine. Restarted turbine. | KRAYN-WKO-NDX-20120222 | 1
KRAYN-WKO-NDX-20120223-01 | FM493 / Yaw SensTrack 1(90&deg | 2012-02-23 | 2012-02-24 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 16.5 | Forced |  |  | 151.5333 | Highland 1 | Approached down turbine, WTS was in the process of erecting there in naccelle crain and exchanging lifting cable. Procceded with yaw stack change out. Installed new yaw stacks and yaw motors. Rewired and reassembled turbine. Tested yaw with a CW and CCW test. desended tower. Reset and started turbine | KRAYN-WKO-NDX-20120223 | 1
KRAYN-WKO-NDX-20120223-02 | FM1208 / MI class B Fault | 2012-02-23 | 2012-02-23 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.36667 | Highland 1 | Approached down turbine, took trigger files for Sean Illig. Reset and started turbine | KRAYN-WKO-NDX-20120223 | 1
KRAYN-WKO-NDX-20120223-03 | FM700 / IBS Interbus Stop | 2012-02-23 | 2012-02-23 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 11.75 | Forced | KRAYN-NDX-PRT-0044 | 2 | 12.5 | Highland 1 | Technicians responded to what was initially a blown Phoenix Contact interbus fuse. This was corrected relatively quickly, but the problem then deteriorated to a rotor brake not opening issue, which manifested itself on NCII in several misleading ways, including low accumulator faults. Nordex technicians returned to Geistown in order to retreive material to check accumulators and begin electric troubleshooting. Accumulators were checked and determined to be fine, accumulator pressure sensors checked and also determined to work; contactors, relays, solenoids, and valves checked and determined to work. Finally, We powered down the interbus uptower and restarted it, determining that whatever had blown the fuse on 105A2 had also further disrupted the system. Turbine worked thereafter. | KRAYN-WKO-NDX-20120223 | 1
KRAYN-WKO-NDX-20120223-04 | FM50 / SafetyChain Activated | 2012-02-23 | 2012-02-23 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 3.5167 | Highland 1 | Drove to turbine #25. Climbed turbine. Checked fuses and breakers in the interbus module. Found that the 143F4 was down. Turned breaker back on. All faults cleared. Climbed back down turbine. Restarted turbine. | KRAYN-WKO-NDX-20120223 | 1
KRAYN-WKO-NDX-20120225-01 | FM50 / SafetyChain Activated | 2012-02-25 | 2012-02-26 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.3667 | Highland 1 | Arrived at turbine in response to FM 50. Saftey chain would not reset down tower via bottom box button. Turbine was ascended and the pepper & fukhs module was reset. The safety chain was then successfully reset along with all faults via NC2 and the turbine was restarted without issue. | KRAYN-WKO-NDX-20120225 | 1
KRAYN-WKO-NDX-20120225-02 | FM416 / Yaw Inverter Fault | 2012-02-25 | 2012-02-25 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 1.8167 | Highland 1 | Arrived at turbine in response to FM416. Shut off power to the yaw system via 34F2 and F3 in the bottom box. After the hard reset was complete, the RFC rebooted and all faults cleared in NC2. The turbine was restarted without incident. | KRAYN-WKO-NDX-20120225 | 1
KRAYN-WKO-NDX-20120225-03 | FM55 / GenRot RpmMonitor Stop | 2012-02-25 | 2012-02-25 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 10.1333 | Highland 1 | Responded to turbine 23's apparent P&F fault. Ascended tower, reset the 142A6 fuse. Descended tower, restarted. | KRAYN-WKO-NDX-20120225 | 1
KRAYN-WKO-NDX-20120227-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-02-27 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 8.6333 | Highland 1 | Arrived at turbine in response to a series of faults that generally indicate a broken yaw stack. These include FM 406, 490, 492 and 493. After ascending tower the appropriate time delay relay was jumped out in order to release the yaw motor brakes. The brakes were then spun via fan to check for resistance. The right stack was found to be intact but the left stack was not. This was reported immediatly to Kelly Miller and the turbine was left in FM6 with Switch Rights Disabled. | KRAYN-WKO-NDX-20120227 | 1
KRAYN-WKO-NDX-20120227-02 | FM1173 / Pitch1 Batt.contactor Error | 2012-02-27 | 2012-02-27 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 9.4333 | Highland 1 | Drove to turbine, Climbed up tower. Found that it was missing new relay. Replaced 124K1 relay. | KRAYN-WKO-NDX-20120227 | 1
KRAYN-WKO-NDX-20120227-03 | FM1002 / Wind Speed LessThanStartCondition | 2012-02-27 | 2012-02-27 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 0.15 | Highland 1 | Drove to the turbine. Resent the RFC on the Nordex side. Upon entering the turbine noticed that the "system OK" light was flashing red on the SEG side. Reset the HUR. Once botht he HUR and the RFC were reset and cylced, refreshed the fault log. There were no more errors. Restarted the Turbine. | KRAYN-WKO-NDX-20120227 | 1
KRAYN-WKO-NDX-20120227-04 | FM1173 / Pitch1 Batt.contactor Error | 2012-02-27 | 2012-02-27 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 10.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 9.4333 | Highland 1 | Arrived at the tower and reset turbine. Found that it would emergency pitch back then forward and back with no faults. Climbed the tower and locked out the hub. Climbed into the hub and troubleshot the emergency system with no defects noted. Climbed out to nacelle to remove power from hub and LOTO. Climbed back into the hub and removed the slip ring covers and inspected with no defects noted. Secured everything in the hub and returned to the nacelle. Removed LOTO and reset breakers. Manually pitched the turbine and had no defects so we started the turbine and it cut in then faulted with no fault?????? Had a hub slip ring delivered and removed power from the hub and LOTO'ed. Climbed into the hub and R&R the slip ring. Returned to the nacelle removing the LOTO and reseting the breakers again. Started the turbine which cut in and ran for several minutes. Stoped the machine and returned down tower. Started the turbine and returned to the shop. | KRAYN-WKO-NDX-20120227 | 1
KRAYN-WKO-NDX-20120228-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-02-28 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 10 | Forced |  |  | 8.6333 | Highland 1 | Ascended turbine and prepped for yaw stack change out. Yaw motors and surrounding floor plates were dismantled and relocated. All tools needed for changeout were craned up tower via jib crane. | KRAYN-WKO-NDX-20120228 | 1
KRAYN-WKO-NDX-20120228-02 | FM492 / Yaw SensTrack 2(0&deg | 2012-02-28 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 8.6333 | Highland 1 | Ascended turbine and prepped for yaw stack change out. Yaw motors and surrounding floor plates were dismantled and relocated. All tools needed for changeout were craned up tower via jib crane. | KRAYN-WKO-NDX-20120228 | 1
KRAYN-WKO-NDX-20120228-03 | FM400 / Wind DirSlanting Stop(due YP50) | 2012-02-28 |  | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 2.25 | Highland 1 | Drove to turbine. Climbed up tower for yaw stack prep. Found that the 124K1 relay was not previously changed. Changed out relay. Continued to work on yaw stacks. | KRAYN-WKO-NDX-20120228 | 1
KRAYN-WKO-NDX-20120301-01 | FM1209 / MI class C (Service!) Fault | 2012-03-01 | 2012-03-02 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 4.3833 | Highland 1 | Arrived at turbine in response to fm 1209. Convertor gave a M2IGBT overload fault. Fault was cleared and turbine was started up only to fault again. Trigger files were pulled and sent to Sean Illig. The FIT board was then replaced and the system was commissioned. The FIT board replacement did not fix the problem....more triggers were pulled and the turbine was set to restricted production and started up without faults. | KRAYN-WKO-NDX-20120301 | 1
KRAYN-WKO-NDX-20120301-02 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-01 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 9.85 | Highland 1 | completed hytorquing of yaw stacks and other prep work. | KRAYN-WKO-NDX-20120301 | 1
KRAYN-WKO-NDX-20120301-03 | FM420 / Yaw HydBrk not open | 2012-03-01 | 2012-03-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 2.1167 | Highland 1 | Went to turbine #20. Climbed up turbine. Changed out the 124K1 relay. Climbed back down turbine. Manually yawed to make sure the brake was releasing. The yaw break was functioning properly. Restarted turbine. | KRAYN-WKO-NDX-20120301 | 1
KRAYN-WKO-NDX-20120301-04 | FM50 / SafetyChain Activated | 2012-03-01 | 2012-03-01 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.71667 | Highland 1 | Loaded trucks with PPE and fire exinquishers. Saw Turbine #19 went down. Drove to Turbine #19 first. Reset PLC. All faults cleared. Restarted turbine. | KRAYN-WKO-NDX-20120301 | 1
KRAYN-WKO-NDX-20120302-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-02 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 8.25 | Forced |  |  | 2.9833 | Highland 1 | Nordex technicians drove to tower 3 to assemble WTS's hydraulic hoist for yaw drive removal. WTS arrived at appx. 6:30. Began off-loading hoist components from trucks, electrical preparation, and safety briefings. Nordex and WTS technicians moved uptower at appx. 08:00 and began moving hoist components uptower via Nordex onboard hoist. Components for WTS's small hoist assemebled and used to move in the components for the larger hoist. Wind conditions prevented assembly of large hydraulic hoist and removal of the drives, so task was abandoned (force majure) until more favorable conditions present. | KRAYN-WKO-NDX-20120302 | 1
KRAYN-WKO-NDX-20120302-02 | FM124 / Gear OilFilt Alarm(replace Fi) | 2012-03-02 | 2012-03-02 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced | KRAYN-NDX-PRT-0325 | 1 | 1.2333 | Highland 1 | Arrived at turbine in response to FM 124. Ascended tower in order to perform gear oil filter swap. Metal shavings were discovered and collected. Pictures to come…Do not consume filter. | KRAYN-WKO-NDX-20120302 | 1
KRAYN-WKO-NDX-20120303-01 | FM1209 / MI class C (Service!) Fault | 2012-03-03 | 2012-03-03 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 42.25 | Forced | KRAYN-NDX-PRT-0960 | 1 | 40.3167 | Highland 1 | Pulled many triggers, phone support and contact with Sean Illig and SEG, Told us to change LSC side Igbt, changed LSC igbt, did not fix, changed fit, changed HUR, jumped out IGBTs again pulled triggers, changed MSC IGBT, would not start, ran 1/2 power all night. (note following morning swapped back HUR and Fit so do not consume) following morning found fibers in wrong spot when changed fit back and started. | KRAYN-WKO-NDX-20120303 | 1
KRAYN-WKO-NDX-20120303-02 | FM1209 / MI class C (Service!) Fault | 2012-03-03 | 2012-03-03 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 40.3167 | Highland 1 | Looked at triggers from yesterday at the shop and gathered some possible parts for the repair includeing a FIT board and SUR. Traveled to the site and began by looking over everything done the night before. Looked over the IGBT's which where changed the night before with no defects noted. Moved to the HUR and checked all of the wire landings and fiber terminations with no defects noted but noted the SUR error light was on. Moved to the SUR and inspected its connections finding no defects to note. From there we inspected the FIT board which was suspect the night before. It was changed the night before so we began to change the FIT board back to the original. During this process it was found that two of the fibers where swapped 19 AND 20. After finding this we continuesd installing the orginal and correcting the fiber issue. The LED on the FIT went amber and then after reset it returned to green. After this we buttoned up the cabinets and started the turbine with no defects noted. | KRAYN-WKO-NDX-20120303 | 1
KRAYN-WKO-NDX-20120303-03 | FM332 / LV Griderror 660V Alarm | 2012-03-03 | 2012-03-03 | KRAYN-WTG22 | General Maintenance | Nordex USA OandM | 7.5 | Forced | KRAYN-NDX-PRT-0042,KRAYN-NDX-PRT-0090 | 2,1 | 17.2167 | Highland 1 | Arrived at turbine in response to FM 332. Also presented with FM 300 and 700. Found that Q10P would not reset manually. Troubleshot convertor and service sides of Q10P associated circuits and discovered voltage present on diode X33. The 24 volts was preventing Q10P from resetting. After traveling back to the shop the diode was replaced and the turbine was started via NC2. All is well. | KRAYN-WKO-NDX-20120303 | 1
KRAYN-WKO-NDX-20120305-01 | FM124 / Gear OilFilt Alarm(replace Fi) | 2012-03-05 | 2012-03-05 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced | KRAYN-NDX-PRT-0325 | 1 | 2.65 | Highland 1 | Gathered parts and PPE to load up truck. Drove to Turbine. Climbed turbine. Took filter and tools up turbine. Shut off 400V to pump. Took out old filter and replaced with new. Reconected all valves and replaced lid. Tried to cycle but turbine would not exit out of local mode. sent everythign down tower. Found switch on hatch from yaw deck not working properly. Corrected switch. Contacted other tech to reset due to MI class B fault needing 400 level access. All faults cleared. Climbed down tower. Reset any remaining faults. Restarted turbine. Drove back to O&M building. unloaded truck and completeed service order. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-02 | No work order description provided by contractor | 2012-03-05 |  | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 6.9 | Highland 1 | Door latch for turbine was replaced. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-03 | No work order description provided by contractor | 2012-03-05 |  | KRAYN-WTG20 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 1.2 | Highland 1 | Door latch for turbine was replaced which required a Lowes run to secure proper hardware and a titanium bit.2 | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-04 | No work order description provided by contractor | 2012-03-05 |  | KRAYN-WTG21 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 3.5333 | Highland 1 | Door latch for turbine was replaced. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-05 | No work order description provided by contractor | 2012-03-05 |  | KRAYN-WTG23 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 7.7 | Highland 1 | Door latch for turbine was replaced. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-06 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-05 |  | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 4.2833 | Highland 1 | Reviewed NC II logs which pointed to a broken yaw stack. Traveled to site and climbed the turbine. Manually yawed the turbine with no defects noted. Removed the top hats from the yaw drive motors and jumped the motor brakes to release them. Turned the motors and stacks by hand to find the hinged side to only turn 3 revolutions and the open side to turn forever. With this it was confirmed that the open side stack was broken. Connected the computer to the ABB drive via drive windows and checked the data loggers and faults. We save this information and emailed it to engineering. Climbed back down tower and left the turbine in a manual stop and took the switch rights. With that done we returned to the shop. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120305-07 | No work order description provided by contractor | 2012-03-05 |  | KRAYN-WTG25 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 2.9167 | Highland 1 | Door latch for turbine was replaced. | KRAYN-WKO-NDX-20120305 | 1
KRAYN-WKO-NDX-20120306-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-06 | 2012-03-07 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0959 | 2 | 193.4333 | Highland 1 | Performed and safety tailgate meeting with Nordex and WTS techs. Traveled to site and climbed the tower. Assembiled the onboard crain and began the yaw drive swap. Removed the higned side first with no problems but had to wait for proper rigging to bring the new one up so we removed the open side drive and sent it down tower also. The rigging arrived and we lifted the new drive and installed it in the hinged side with no issues then we lifted the last new drive and installed it on the open side. Torqued the drive bases and installed the yaw motors with wiring while WTS lowered the crane to the ground. Finished the install by attaching the steps around the yaw stacks. Gathered tools and sent them down on the crain hoist after the crane was down. Climbed down tower and Started hte turbine. | KRAYN-WKO-NDX-20120306 | 1
KRAYN-WKO-NDX-20120306-02 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-06 |  | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 15.5 | Forced |  |  | 3.0167 | Highland 1 | Loaded truck with prep tools and PPE. Drove to turbine. Climbd turbine. Switched off the 400V breaker to the yaw motors. Switched off the 110AF3(230V) breaker to the yaw motors. Switched off the 104F3 breaker (24V) to the yaw motor). All power was off to the motors so we disconnected wires. Disconnected the grease fittings in the belly of the nacelle to the yaw drives. Unbolted and disconnected motors from the yaw drive. Used Hytorque to break loose the yaw stack bolts. Lifted parts and crane peices for yaw drive replacement. Once all pieces were up turbine reset chaing hoiste and roof. Climbed down turbine. Drove back to O&M building. | KRAYN-WKO-NDX-20120306 | 1
KRAYN-WKO-NDX-20120306-03 | FM400 / Wind DirSlanting Stop(due YP50) | 2012-03-06 |  | KRAYN-WTG24 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 3.0167 | Highland 1 | Found that the 124K1 relay was not previously changed. Changed out relay. Continued to work on yaw stacks. | KRAYN-WKO-NDX-20120306 | 1
KRAYN-WKO-NDX-20120308-01 | FM1208 / MI class B Fault | 2012-03-08 |  | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 6.9 | Highland 1 | Pulled trigger files and sent them to S.E.G. in response to MI Class B and pick up fault. Turbine was not shut down. | KRAYN-WKO-NDX-20120308 | 1
KRAYN-WKO-NDX-20120309-01 | FM50 / SafetyChain Activated | 2012-03-09 | 2012-03-10 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.05 | Highland 1 | Drove to turbine. Logged on to NC2. Reset RFC. Checked schematics. Switched off breakers 34F2 and 34F3 to kill 24v power to Pepperl & Fuchs modules. Safety chain faults cleared. MI class B fault was reset and cleared. Turbine was in "OK" status. Restarted turbine. Drove back to O&M building. | KRAYN-WKO-NDX-20120309 | 1
KRAYN-WKO-NDX-20120309-02 | FM1208 / MI class B Fault | 2012-03-09 | 2012-03-09 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 0.8 | Highland 1 | Travel to site and reviewed the SEG faults which showed a DC voltage issue. The faults cleared and the turbine reset and ran. Pulled the event logger, trigger files, and created a live trigger all of which where saved to send to engineering. Monitored the turbine for 10 minutes with no defects noted and returned to the shop. | KRAYN-WKO-NDX-20120309 | 1
KRAYN-WKO-NDX-20120310-01 | FM50 / SafetyChain Activated | 2012-03-10 | 2012-03-10 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced |  |  | 11.3833 | Highland 1 | Spent some time in the shop prepareing for Pepperl and fuchs modual work by trying to load moduals in shop with PACTware. Traveled to site and climbed up tower. Troubleshot the safety chain system with extra focus on the Pepperl and Fuchs system since the safety chain wouldn't reset from down tower. Reset the safety chain and reset the turbine, removed wire from interbus pin 48 105A4 to simulate a 24 VDC failure which reproduced some of the same faults plus many more. Relanded the wire on 48 and cleared the saefty chain and reset teh turbine. Continued this process of trying to reproduce the same faults and found that the only way to to this was to removed the 24 VDC from 142K2 which is the Pepperl and Fuchs way of throwing the saefty chain anyway. So it was determined that the Pepperl and Fuchs system was working properly. With that the CSO East Master tech Sean Illig was contacted and he informed us that a similar problem was seen on a different turbine a while ago which was resolved with a reset of the HUR and re-comissioning of the converter. With this info we returned down tower and did just that. We tried to pull triggers but the HUR would not allow the triggers to be saved. So we reset the HUR and began the comissioning but the winds where very low and had to wait sometime to get the machine into the speed window for comissioning of the converter. After getting the comissioning done the turbine was stoped and returneed to a normal fault free state and started again. | KRAYN-WKO-NDX-20120310 | 1
KRAYN-WKO-NDX-20120310-02 | FM50 / SafetyChain Activated | 2012-03-10 | 2012-03-10 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 0.25 | Forced |  |  | 11.3833 | Highland 1 | While troubleshooting FM50, found that the 124K1 relay was not previously changed. Changed out relay. | KRAYN-WKO-NDX-20120310 | 1
KRAYN-WKO-NDX-20120311-01 | FM261 / RotBrk Brakepressure Fault | 2012-03-11 | 2012-03-11 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced |  |  | 6.1667 | Highland 1 | Spend so time on NCII troubleshooting faults to determine what we may have needed to take along. After doing this we decided to take the accum service kit and N2 along with tools to adjust the verious pressures throughout the hyd station. Travele to site and disabled the FM 261 and started the turbine this resulted in a FM 262 which we then disabled and the turbine passed its rotor brake test and begain to run. With this we thought there was an adjustment problem with the 740.2 or 810.2 positions on the hyd station. So with that we climbed up with tools to adjust the pressures but after arring up tower it was dretermined that the problem was actually the 110 BAR accum which was flat flat flat. Sent Mike Huss back down the tower and lowered the chain hoist to raise up the serviceing kit and tank. Seviced all accum's and cleared the turbine to a fault free condition. Started the turbine and it passed its rotor brake test and remained fault free. Packed and lower all tools and equipment then lowered it all down with teh chain hoist. After running the chain hoist back up it was lowered into its proper position and the nacelle hatch was closed and latched. I returned down tower via the ladder and started the turbine. | KRAYN-WKO-NDX-20120311 | 1
KRAYN-WKO-NDX-20120312-01 | FM727 / Wind Speed Left-hand CableCut | 2012-03-12 | 2012-03-12 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 7.25 | Forced | KRAYN-NDX-PRT-0603 | 1 | 6.5 | Highland 1 | Technicians briefly assessed the function of the ultrasonic anemometer, determined it needed to be changed. Removed old ultrasonic, installed new ultrasonic, routed cables, alligned the component. Developed a problem with the anemometer and wind vane due to moisture in nacelle during the intial troubleshooting. Blew fuse 160F2 (different Service Order). | KRAYN-WKO-NDX-20120312 | 1
KRAYN-WKO-NDX-20120312-02 | FM6 / WTG Manual Stop | 2012-03-12 | 2012-03-12 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 9.8667 | Highland 1 | Loaded parts and tools into the truck. Drove to turbine. Climbed up turbine. Lifted tools and parts up tower. Hooked up ITH to the bolt stretcher. Applied 1300 bar to bolt to tension bolt per specification. Adjusted bolt height to specification. reapplied bolt caps. Unhooked hydraulic pump and cleaned up tools. | KRAYN-WKO-NDX-20120312 | 1
KRAYN-WKO-NDX-20120312-03 | FM420 / Yaw HydBrk not open | 2012-03-12 | 2012-03-12 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0547 | 1 | 1.2 | Highland 1 | Arrived at turbine in response to FM420 with the intention of swapping a throttle valve ( 123.23 ) on the hydraulic station. After several resets and attempts and yawing manually a few other throttle valves were used. Parameter P16.17 was then changed from 4 to 4.35. All faults cleared and the turbine restarted without incident. | KRAYN-WKO-NDX-20120312 | 1
KRAYN-WKO-NDX-20120313-01 | FM6 / WTG Manual Stop | 2012-03-13 | 2012-03-13 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced |  |  | 3.4167 | Highland 1 | Loaded parts and tools into the truck. Drove to turbine. Climbed up turbine. Lifted tools and parts up tower. Hooked up ITH to the bolt stretcher. Applied 1300 bar to bolt to tension bolt per specification. Adjusted bolt height to specification. reapplied bolt caps. Unhooked hydraulic pump and cleaned up tools. Dropped all tools to ground. Climbed down. Restarted tubine. Drove Back to O&M building. Unloaded tools and filed paperwork. | KRAYN-WKO-NDX-20120313 | 1
KRAYN-WKO-NDX-20120316-01 | FM254 / Hyd OilPmpRuntime long | 2012-03-16 | 2012-03-16 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 18 | Forced |  |  | 9.2 | Highland 1 | Ran through schematics and piping diagrams for the hydro system. Drove out to site and climbed the tower. First check was to clean the position 500 and 210 valves. This produced no fix or change in operation. Replaced the position 500 valve with a new valve and electromaginet with the results haveing no fix or change. The CSO EAST mastertech joined the fun and suggested some adjusting of a few valves which made no affect on the hyd pump run time long events. After this we adjusted some accumilator related valves with only minor effects noticed it was then determined to try the 130 BAR accumilator. After a short wait for the part the hyd station was de-energized and the 130 BAR accummilator was de-pressurized. We installed a new accummilator and serviced it to 130 BAR afterwhich we re-energized the hyd station and allowed the pump to pressurize the system. A yaw test showed no change to the situation. With this we placed the hyd station back into a operable condition and returned down tower, started the turbine and returned to the shop. | KRAYN-WKO-NDX-20120316 | 1
KRAYN-WKO-NDX-20120316-02 | FM6 / WTG Manual Stop | 2012-03-16 | 2012-03-16 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 13.25 | Planned | KRAYN-NDX-PRT-0966 | 4.0L | 9.2 | Highland 1 | Completed Maintenance III stage two(including tower torque, Yaw motor brake adjustment, Coolant samples bottom and top, and tightened shaft nut). Ping test in Hub was also completed. | KRAYN-WKO-NDX-20120316 | 1
KRAYN-WKO-NDX-20120318-01 | FM120 / Gen CWPress L Stop | 2012-03-18 | 2012-03-19 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.0167 | Highland 1 | Accended tower, lowered hoist for coolant and pump. Lifted coolant and pump, filled coolant station to 2.2 bar (5gal) then lowered pump and empty coolant container. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120318 | 1
KRAYN-WKO-NDX-20120319-01 | FM1208 / MI class B Fault | 2012-03-19 | 2012-03-19 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.8667 | Highland 1 | Evaluated faults which looked like a SEG comissioning issue. Traveled to WTG 1 and found the SEG screen showing an M5 comissioning missing. Manually ran turbine to 1100 RPM and re-comisioned the SEG. Returned the turbine ro auto and started the machine with no defects noted at this time. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-02 | FM254 / Hyd OilPmpRuntime long | 2012-03-19 | 2012-03-19 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0320,KRAYN-NDX-PRT-0025,KRAYN-NDX-PRT-0024,KRAYN-NDX-PRT-0015 | 1,1,1,1 | 4.8167 | Highland 1 | Lots of prework including yawing of numerious turbine s as comparisons to WTG 12. Changed parameters 22.01, 22.02, and 22.03 to see the affects of those changes on the turbine which made no change. Traveled out to the turbine and climbed up tower. Sent the chain hoist down and chained up tools and parts. Began by trying a new pump in the hydro station which involved droping the 400 VAC on the hyd motor and verifying no voltage. With this we removed the wires and the removed the pressure from the system. Then removed the rigid line from the pump base and then removed the motor and pump assembily. Once removed we seperated the pump from the motor. The "LOVE JOY" connection was slightly damaged so all three pieces of it were replaced and the new pump installed. Witht he new pump and love joys in the motor was lined up to the pump and installed together. With that complete the assembily was installed back into the hyd station and the line was installed along with the wires. 400 VAC was returned to the motor and the turbine was reset. Hyd station functions work good with no defects noted. Compared run times to turbine 11 with no real differences noted. Returned down tower and started the turbine. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-03 | FM110 / GenTot RpmDiff H Stop | 2012-03-19 | 2012-03-19 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced | KRAYN-NDX-PRT-0325 | 1 | 10.6 | Highland 1 | Ater troublshooting the RotorRPM fault, continued to change filter on generator oil pump. Killed the power to the oil motor pump. Drained pressure. Took out old filter. Putin new filter. Closed up cap. Returned voltage to motor. Ran pump. All checked out fine. Lowered tools. Climbed down tower. Restarted turbine. Drove to turbine #12 for troubleshooting support. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-04 | FM110 / GenTot RpmDiff H Stop | 2012-03-19 | 2012-03-19 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 10.6 | Highland 1 | Preped tools and materials. Drove to turbine. Climbed tower. Checked sensors on rotor side with shake test. Adjusted sensors. Checked trends. All signals looked good. Continued working on filter. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-05 | No work order description provided by contractor | 2012-03-19 |  | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 3.9 | Highland 1 | Apprached turbine and found it to be I a running state. OPC fault, Reset and run subserver. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-06 | FM6 / WTG Manual Stop | 2012-03-19 | 2012-03-19 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.8333 | Highland 1 | Ascended tower to pull yaw triggers and perform checks according to engineering | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120319-07 | FM6 / WTG Manual Stop | 2012-03-19 | 2012-03-19 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.78333 | Highland 1 | Ascended tower to pull yaw triggers and perform checks according to engineering. Mission was aborted when no communication could be established with the yaw drive. | KRAYN-WKO-NDX-20120319 | 1
KRAYN-WKO-NDX-20120320-01 | FM110 / GenTot RpmDiff H Stop | 2012-03-20 | 2012-03-20 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced | KRAYN-NDX-PRT-0683 | 1 | 18.25 | Highland 1 | Approached down turbine, checked converter and took triggers. Exchanged fit adapt and started turbine. Turbine fauulted and took new triggers. Called Sean Illig and pointed me towards the Gen encoder, fast logged the fault and found defective Gen encoder. Climbed tower and changed gen encoder and desended tower. Balanced encoder and started turbine | KRAYN-WKO-NDX-20120320 | 1
KRAYN-WKO-NDX-20120320-02 | FM110 / GenTot RpmDiff H Stop | 2012-03-20 | 2012-03-21 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0045,KRAYN-NDX-PRT-0729 | 1,1 | 7.7 | Highland 1 | Ascended turbine in response to FM 110. After determining the problem sensor (right hand side when facing the back of the nacelle) the plug was replaced. The wires in the old plug were found to be rather long so they were cut back prior to plug replacement. This initiated an FM 253 so, the original fault was temporarily ignored. Various attempts to get the rotor brake to release were unsuccessful. It was discovered that module 105A13 pin two was not recieving power....when jumped the rotor brake released. ST 268 was then disabled while the pin was jumped and the turbine started up. Turbine was allowed to run for several minutes and no FM 110, 100, or 50 occured. Because further action would require 1-2 hours of additional prep/drive time because of the hour and because one tech involved had to attend climb safety training the next day the turbine was called good and the tower was decsended. The turbine passed the rotor brake test and started up via NC2 downtower. | KRAYN-WKO-NDX-20120320 | 1
KRAYN-WKO-NDX-20120320-03 | FM110 / GenTot RpmDiff H Stop | 2012-03-20 | 2012-03-20 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 13.7833 | Highland 1 | Accended tower and adjusted sensor arm and exchanged sensors, reset and ran turbine for fifteen mins to check for faults, turbine was fault free, ran turbine. | KRAYN-WKO-NDX-20120320 | 1
KRAYN-WKO-NDX-20120320-04 | FM110 / GenTot RpmDiff H Stop | 2012-03-20 | 2012-03-20 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 13.7833 | Highland 1 | Ascended tower to pull yaw triggers and perform checks according to engineering. | KRAYN-WKO-NDX-20120320 | 1
KRAYN-WKO-NDX-20120321-01 | FM110 / GenTot RpmDiff H Stop | 2012-03-21 | 2012-03-21 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced | KRAYN-NDX-PRT-0568 | 1 | 11.45 | Highland 1 | Accended tower, replaced pepper&fuchs module SAP ID 23513 and exchanged interbus modules 105A5 for 105A6. Cleared FM110, FM 419 and FM 253. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120321 | 1
KRAYN-WKO-NDX-20120322-01 | FM729 / Wind Speed Right-hand CableCut | 2012-03-22 | 2012-03-22 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced | KRAYN-NDX-PRT-0625 | 2 | 0.75 | Highland 1 | Nordex Technicians replaced 160F2 which blew during the replacement of an ultrasonic anemometer. Param 26.17 returned to 3. Everything good. Travel time incorporated in a different SO. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-02 | FM866 / Air Temp CtrlCab H Stop | 2012-03-22 | 2012-03-22 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 2.05 | Highland 1 | Nordex technicians turned fans in top box cabinet back on that were inadvertantly left off. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-03 | FM0 / WTG System ok | 2012-03-22 |  | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.4833 | Highland 1 | Removed old door bracket and exchanged for new bracket which was too big for door to shut. We then removed spacers and replaced old door bracket which seemed to work. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-04 | FM503 / Wind SpeedDiff H Warn | 2012-03-22 | 2012-03-22 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0603 | 1 | 2.7833 | Highland 1 | Accended tower, kill power to 160F2 & interbus modules 105A5&105A6 via 104F2&104F3. Checked fuse from 160F2 and switched interbus moduls 105A5&105A6 but fault persisted. We then removed the ultrasonic, killed 104F2 and terminating all wires in X8 and replaced ultrasonic. Fault cleared and turbine runs. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-05 | FM6 / WTG Manual Stop | 2012-03-22 | 2012-03-22 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.6333 | Highland 1 | Ascended tower to pull yaw triggers and perform checks according to engineering. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-06 | FM866 / Air Temp CtrlCab H Stop | 2012-03-22 | 2012-03-22 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 1.9333 | Highland 1 | Approached down turbine, assended tower and found one ac unit faulted and and the other ac unit set to 55 degrees c. Reset and adjusted ac units to 33 degrees c. reset and started turbine | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-07 | FM6 / WTG Manual Stop | 2012-03-22 | 2012-03-22 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 2.8833 | Highland 1 | Arrived at turbine in response to FM 307 warning. After disengaging the LV Switch and ascending the turbine, all gen brushes were checked and found to be adequatly long. Troubleshooting (in order to find the faulty switch) revealed a loose wire (Sp 16) in the generator box (173 S1). This did not fix the fault. Further troubleshooting revealed that the switch in question was the hindge side on the high speed shaft. Because there is no brush at this point the switch was removed from the circuit and a jumper was installed (at 173 S1) in its place. The turbine was cleared of all faults via NC2 and started up without incident after climbing down and reengaging the LV switch. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120322-08 | FM6 / WTG Manual Stop | 2012-03-22 |  | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.78333 | Highland 1 | Arrived at turbine in response to a No Comm. Fault. The NC2 Subserver was reset and the fault cleared and remained clear for the durration of our stay. Turbine was not shut down. | KRAYN-WKO-NDX-20120322 | 1
KRAYN-WKO-NDX-20120324-01 | FM1156 / Pitchangle 1 Diff.Act-RedAct | 2012-03-24 | 2012-03-24 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced |  |  | 9.5333 | Highland 1 | Arrived at turbine in response to FM 1156. Upon hub entry a broken blade bolt (see Q-Notice) was discovered that had bumped the Red. Encoder on pitch 1. The encoder was adjusted from 86.8 to 87.2 degrees and all faults cleared. The turbine started up without incident. | KRAYN-WKO-NDX-20120324 | 1
KRAYN-WKO-NDX-20120326-01 | FM493 / Yaw SensTrack 1(90&deg | 2012-03-26 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 1.3667 | Highland 1 | Called from HINO with a Yaw SensTrack 1 error. Drove to turbine. Climbed up turbine. Took covers off. Jumped out yaw motor brake. Found on break to spiin while other stayed stationary. Determined that the stationary motor's corresponding stack is broken. Made plans for yaw stack prep. Climbed down turbine. Put turbine in to manual yaw with switch rights disabled. Drove back to HINO. | KRAYN-WKO-NDX-20120326 | 1
KRAYN-WKO-NDX-20120327-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-27 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 0.46667 | Highland 1 | Went up tower. Found broken bolt. Replaced bolt with good hardware. Found small hole in bottom of bag. Lowered almost all of the chain out of the bag. Patched hole. Brought chain back up for use until bag can be replaced. Climbed back down turbine. | KRAYN-WKO-NDX-20120327 | 1
KRAYN-WKO-NDX-20120327-02 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-27 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 10.5 | Forced |  |  | 0.46667 | Highland 1 | Loaded truck with tools. Drove to Turbine. Climbed up turbine with minor tools. Unbolted floor panels. Turned off 24v and 400v to motors on yaw stacks. Un wired motors. Unbolted motors. Lifted motors and secured away from stack. Used Hytorc to intially loosen stack bolts and then impact drill to take out. Left two bolts in for security. Gathered tools. sent down turbine. Cleaned area as well as possible. Climbed down down. Returned to shop. | KRAYN-WKO-NDX-20120327 | 1
KRAYN-WKO-NDX-20120327-03 | FM0 / WTG System ok | 2012-03-27 |  | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 6.1667 | Highland 1 | Apon customer request we traveled to WTG 21 to check the shaft nut. Once arriving at the turbine the winds had picked up to 7-9 m/s. This situation had been seen before which was evedent from a loud clunck from the nacelle. With the wind at 8 ish m/s we listened to the operation of the machine. No cluncking, thudding, or any other noises where noted from the machine. From inside of the tower there was no noticable difference in sound from any other running turbine. With no noticable defects from the ground and descent wind and the lateness of the hour it was deturmined to allow the turbine to run and plan a more suitable time to shut it down and physically check the shaft nut. We left the site and returned to the shop. | KRAYN-WKO-NDX-20120327 | 1
KRAYN-WKO-NDX-20120328-01 | FM358 / LV UPSBatteryChange | 2012-03-28 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 6.4 | Highland 1 | Loaded battery pack and UPS into truck with PPE. Drove to Turbine. Checked to see if the UPS would reset. The UPS did reset. Set up a secondary UPS in the bottom of turbine #6 as a charging station to charge one rack of batteries. Closed doors and left Turbine. Drove over to Hghland North for support. | KRAYN-WKO-NDX-20120328 | 1
KRAYN-WKO-NDX-20120328-02 | FM750 / IBS Pitch CommFlt | 2012-03-28 | 2012-03-28 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 9.25 | Forced | KRAYN-NDX-PRT-0725 | 1 | 7.3167 | Highland 1 | Traveled to turbine and found that someone had reset and that the FM 750 had cleared. It was also found that the hyd station motor was commanded on but was not running. Climbed the tower and found 104F5 24VDC breaker tripper in the top cabinet. This is different than the usual situation with a FM 750. Reset the breaker and the hyd station ran. The faults all cleared for a moment then the breaker 104F5 tripped again. Continued checking top cabinet items related to the 104F5 breaker eliminating all items. Locked out the hub and climbed out to check the slip ring. Removed the cover from the slip ring and found that there was an large amount of "dust" in the housing. Called the shop and had a tech run out a cleaned and lubed unit from the shop. Lowered the chain hoist down with the arrival of the slip ring and hoisted it up. Removed and replaced the slip ring and returned to the nacelle. Returned power to the hub from the change out, unpinned the hub, and reset the turbine. All faults cleared and operated correctly. Started the turbine and allowed it to run through its rotor test and pitch test with no defects noted. Placed the turbine in manual stop and lowered the old slip ring down then returned the hoist unit to the stowed position. Closed up the nacelle and climbed down tower. Started the turbine and left. | KRAYN-WKO-NDX-20120328 | 1
KRAYN-WKO-NDX-20120328-03 | FM300 / LV MainSwitch OFF | 2012-03-28 | 2012-03-29 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 17.75 | Forced | KRAYN-NDX-PRT-0090,KRAYN-NDX-PRT-0644 | 4,3 | 11.5333 | Highland 1 | Drove to Turbine #15. Noticed that the transformer doors were blown open. Waited for EP to inspect transformer and reclose the doors. Went into turbine for intial inspection. Foundthe Q10P was tripped. Looked through the schematics for the circuit. Found the diode on X8 33 was blown. turned off power to diode block via 153F7. Replaced the diode. Tried to reset the Q10P. The Q10P would reset until the breaker was turned back on. Further inspection of circuit brought us to the line fuses. Saw that the micro switchs were open on all three fuses. Contacted EP. Waited for EP to switch off transformer to change fuses. The EP personnel did not havce the correct grounding cables. Waited for EP to get correct cables. Once the transformer was turned off checked voltage in the cabinet before working. Changed out line fuses. Inspected the rest of the cabinet for any damage. Closed up cabinet. Had EP switch the transformer back on. Recheck diodes. Diodes were blown again. Revisited circuit. All paths pointed to the X8 pin #33 suppression diode. Decided to check for voltage on the customer/transformer side. Found 24V signal coming from the transformer side. Contacted EP for schematic support. The wire was not normally supposed to have signal unless the transformer was overheating (yet the transformer was cool). Decided that the extra current was coming from the Transformer blowing the diodes. Waited for EP to send Email confirmation that the wire should be pulled, the turbine restarted, and that they would take full liability for this decision. The Email was recieved and confirmed. The turbine was cleaned up of all parts, tools, and materials. All doors were closed. The turbine was restarted untill morning. Drove back to O&M building. Unloaded truck and complete paperwork. | KRAYN-WKO-NDX-20120328 | 1
KRAYN-WKO-NDX-20120328-04 | FM300 / LV MainSwitch OFF | 2012-03-28 | 2012-03-29 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 22 | Forced | KRAYN-NDX-PRT-0090 | 9 | 11.45 | Highland 1 | Arrived at turbine in response to FM300 (post lightning storm). It was found that t Q10p would not reset. Troubleshooting commenced (trigger files were pulled)…several suppression diodes were found bad and replaced. These were at locations X8.2 diode #2, X8.1 diode #47, X8 diodes #1, #9, #10, #31 through #35. After all replacements were installed and rewired the Q10p was thrown and still would not reset. Further troubleshooting isolated the problem to X8 #33. Everpower was contacted and it was discovered that this connection is for the temp. sensor inside the pad mount transformer. With Everpower's blessing the wire at X8 #33 was disconnected, the Q10p was reset, faults through NC2 were cleared and the turbine was started up. Everpower will be addressing the temp. sensor on 3/29/2012. | KRAYN-WKO-NDX-20120328 | 1
KRAYN-WKO-NDX-20120328-05 | FM332 / LV Griderror 660V Alarm | 2012-03-28 | 2012-03-28 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 5.75 | Forced | KRAYN-NDX-PRT-0090 | 5 | 7.3667 | Highland 1 | Nordex technicians approached tower and discovered that the Q10P would not remain closed. Troubleshot various components across cabinets 1S1-1S6 and was informed of blown supression diodes. Diodes changed. PLC reset. | KRAYN-WKO-NDX-20120328 | 1
KRAYN-WKO-NDX-20120329-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-03-29 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.46667 | Highland 1 | Went to turbine. Climbed up. Unwrapped groups of wires from drives and rewrapped individually. Did the same process for both drives. Went to cabinet and restored all breakers except for the 400v azimuth breaker. Reset safety cahnge and PLC. Cleared faults down tower. Made sure that the turbine was able to "pin wheel". Climbed down turbine. Returned to O&M building. Unloaded trucks and completed service orders. | KRAYN-WKO-NDX-20120329 | 1
KRAYN-WKO-NDX-20120329-02 | FM347 / LV InsulatMonitor 660V Warn | 2012-03-29 |  | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 8.5 | Forced | KRAYN-NDX-PRT-0090 | 3 | 0.96667 | Highland 1 | Started today by reviewing the schematics and eliminating possible problems that had been addresses the day before. Gathered a few related parts and traveled to site. Started by looking into the transformer signal wires which land on X8. It was found last night that by removing the blue wire from pin 33 on X8 the turbine would run. Apon investigation 3 more suppression diodes where failed in the 9 and 10 positions on X8 with are both from the transformer outside and on pin 1. Replaced these 3 diodes and started the turbine with no change but it was noticed that the warning appeared with the cut action of the convertor. Before diving directly into the convertor we checked the 660 VAC insolation monitor for correct operation and corispondance with the interbus warning signal which all checked good. Everpower tech arrived and together we began to troubleshoot the convertor side of things with focus on the grid side to the main transformer. With this a very through visual inspection was preformed through the SEG cabinet. With no defects noted we moved out of the turbine and Everpower opened the switch gear and grounded the transformer. We returned inside and verified no voltage and continued with the visual inspection. After finishing the inspection with no defects found we moved to the pad mount transformer. A quick visual inspection reveal numious arc marks on the 660 VAC side. With a closer look BRAD FOY found that the bushing on the far RIGHT had expanded a little and was creating a white powder on the open area. He then decided to leave the turbine down until a thorough Transformer inspection can be proper performed with the appropriate tools and personel. Clean up the tools there and placed everthing back to normal and secured the cabinets and then tower door. | KRAYN-WKO-NDX-20120329 | 1
KRAYN-WKO-NDX-20120330-01 | FM6 / WTG Manual Stop | 2012-03-30 | 2012-03-30 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 7 | Forced |  |  | 5.8333 | Highland 1 | Gather tools. Drove Half way to site. Received call that yaw parameters needed updated. Drove back to O&M buildign for optical cable set. Drove to turbine #21 from O&M building then. Climbed turbine. Hoisted tools up. Unbolted diamond step plates. Found that shaft nut bolt was already loose ( able to be spun with fingers). Continued to loosen nut for easier turning and tightening. Applied bolts to nut for better leverage when tightening. once shaft nut turned as much as possible the main shaft was spun for access to the tensioning bolt. Due to low winds the main shaft had to be coaxed manually. Once the tensioning nut was in a position where it could be tightened, the nut was torqued to 925 NM per the lastes maintenance document. The shaft was marked to show future slippage. The step plates were put back on. | KRAYN-WKO-NDX-20120330 | 1
KRAYN-WKO-NDX-20120330-02 | FM6 / WTG Manual Stop | 2012-03-30 | 2012-03-28 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 7.3667 | Highland 1 | Nordex technicians change ABB Yaw vari drive parameters. | KRAYN-WKO-NDX-20120330 | 1
KRAYN-WKO-NDX-20120330-03 | No work order description provided by contractor | 2012-03-30 |  | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 3.4167 | Highland 1 | Took handle to turbine #24. Screwed in handle. Check locking mechanism. Everything worked correctly. Left turbine for O&M building. Completed service orders. | KRAYN-WKO-NDX-20120330 | 1
KRAYN-WKO-NDX-20120331-01 | FM50 / SafetyChain Activated | 2012-03-31 | 2012-03-31 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 11.35 | Highland 1 | While in shop fast logged faults on NC2. Gathered potential parts and PPE to load truck. Drove out to turbine. Reset breakers down towere to reset the interbus module. This allowed for the safety chain to be reset down tower. Reset all faults via NC2. All faults cleared. Restarted turbine to do a real time trend. the Rotor, Gen Rotor, and Gen MI all looked clean and fluid. Stayed to pull triggers. Issues with software prevented triggers from being pulled. Both programs were not responding as they should be. Turbine continued to run with no faults. Triggers will be pulled in the future. Cleaned up all tools and equipment. Drove back to O&M building. Unloaded truck and completed service orders. | KRAYN-WKO-NDX-20120331 | 1
KRAYN-WKO-NDX-20120402-01 | FM347 / LV InsulatMonitor 660V Warn | 2012-04-02 | 2012-04-02 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 11.25 | Forced |  |  | 102.45 | Highland 1 | Traveled to site to prepare for grid disconnect of circuit 1. Arrived at WTG 1 and began stoping turbines on circuit 1 and preparing them for grid disconnect using VNC Viewer. Once prepared we went into the sub-station and verified all personel clear of park. Everpower then dropped the circuit and grounded it out. With this the statin was locked out by Nordex and Everpower and both companys Traveled to WTG 15. Apon arrive Everpower techs verified no voltage and began disconnecting the pad mount transformer. Once the transformer was disconnected and the cables isolated we meggered each of then to verify that there was no cable damage during the transformer failure. All cables checked good and where reconneccted and torqued to 30 NM in the cabinet. We then aided Everpower techs as they set the new transformer and landed their connections. After Everpowers work was completed both sides inspected each others work and relocated to the sub-station. Once at the sub station the lockes where removed by Everpower and Nordex and the grounds removed by Everpower then the knife switchs closed. Moved back into the sub station and the circuit was brought back online. We then went to WTG 1 to begin starting the turbines on circuit 1. During this WTG 1 showed and safety chain which cleared and allowed the turbine to Start, WTG 2 should a bad pitch battery but also showed contradicting commands on NCII so the pitch master for that blade (2) was reset from down tower which allowed the turbine to Start. After this we traveled to WTG 15 and closed down tower breakers that where left of to eliminate any surge from the new transformer. Once reset the turbine Started with no defects noted. Traveled back to shop. | KRAYN-WKO-NDX-20120402 | 1
KRAYN-WKO-NDX-20120403-01 | FM493 / Yaw SensTrack 1(90&deg | 2012-04-03 |  | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 1.3667 | Highland 1 | Gathered all of the appropriate tools and equipment for a yaw drives replacement and traveled out to site. Once there it was found that the crane was not completely built yet. Tooling and equipmetn was unloaded and preped to be taken up tower with the crane. The new yaw stacks where on site but needed the new motors removed form them so the crates where opened and the base bolts on the motors removed. With that the motors where ready to be lifted off with the crane. Checked back in with the crane crew to get an estimated on their readiness and they had ran into some problems. At 17:00 we called the job to wait for the mechanic of the crane to come fix it in the morning. Departed site and traveled to the shop. | KRAYN-WKO-NDX-20120403 | 1
KRAYN-WKO-NDX-20120404-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-04-04 | 2012-04-04 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 11.5 | Forced | KRAYN-NDX-PRT-0781,KRAYN-NDX-PRT-0781 | 1,1 | 221.8167 | Highland 1 | Nordex Technicians arrived at tower 13 at appx. 08:00. Remained on hold for appx. 3.5 hours while the crane crew worked out the fault with their equipment. By appx. 11:45, nordex techs began climbing ladder, replacing yaw drives, torquing yaw drives, installing motors, cleaning up. | KRAYN-WKO-NDX-20120404 | 1
KRAYN-WKO-NDX-20120409-01 | FM6 / WTG Manual Stop | 2012-04-09 | 2012-04-09 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 6 | Forced |  |  | 2.65 | Highland 1 | Prework involved finding and preparing ground wire for installation from the FAA light to a proper ground. Traveled to turbine and placed it into a manual stop then climbed tower. By using a multi meter we determined that a vertical support behind the oil cooler was a good ground. Placed new ground wire from the base of the FAA light to the vertical support. FAA light base omhed good to chassis ground. Climbed back down tower and traveled back to the shop. | KRAYN-WKO-NDX-20120409 | 1
KRAYN-WKO-NDX-20120409-02 | FM50 / SafetyChain Activated | 2012-04-09 | 2012-04-10 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 0.93333 | Highland 1 | On call. Approach down turbine, reset safety chain and reset and start turbine. | KRAYN-WKO-NDX-20120409 | 1
KRAYN-WKO-NDX-20120409-03 | FM311 / LP (LightnProt) Gen | 2012-04-09 | 2012-04-10 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0044 | 1 | 1.6 | Highland 1 | On call. Approach down turbine, Checked top box inter bus popcorn fuses and found 105A2 fuse burnt out. Replaced and checked all other fuses. Reset and started turbine | KRAYN-WKO-NDX-20120409 | 1
KRAYN-WKO-NDX-20120411-01 | FM6 / WTG Manual Stop | 2012-04-11 | 2012-04-11 | KRAYN-WTG05 | General Maintenance | Nordex USA OandM | 8 | Forced |  |  | 5.8667 | Highland 1 | CSC 3 converter training with Dave from Woodward. During the first class with Everpower and Charles Martin, Daniel, Jennings, and Sean assended tower to tighten the shaft nut, install yaw parameters, and grounding wire on the FAA light. We desended the tower and completed our training for the converter and went back to the CSO for test and the compliation of the training. | KRAYN-WKO-NDX-20120411 | 1
KRAYN-WKO-NDX-20120411-02 | FM6 / WTG Manual Stop | 2012-04-11 | 2012-04-11 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.8667 | Highland 1 | Installed ground for the FAA light per Sean Illigs request to reduce static electricity during a lightning storm and blowing our popcorn fuses. | KRAYN-WKO-NDX-20120411 | 1
KRAYN-WKO-NDX-20120411-03 | FM6 / WTG Manual Stop | 2012-04-11 | 2012-04-11 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 5.8667 | Highland 1 | Tightened shaft nut. Moved 2 inches tighter and was marked and dated on the rotor. | KRAYN-WKO-NDX-20120411 | 1
KRAYN-WKO-NDX-20120411-04 | FM6 / WTG Manual Stop | 2012-04-11 | 2012-04-11 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 5.8667 | Highland 1 | Installed reduced torque parameters for the yaw converter per enginering request. | KRAYN-WKO-NDX-20120411 | 1
KRAYN-WKO-NDX-20120412-01 | No work order description provided by contractor | 2012-04-12 | 2012-04-12 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 3.25 | Forced |  |  | 0.73333 | Highland 1 | swapped out a UPS from the shop as requested by the customer. We did this as a test to see if it will help with the amps they see on the grounding ring. This part was put back into stock because it did not change anything. | KRAYN-WKO-NDX-20120412 | 1
KRAYN-WKO-NDX-20120412-02 | FM492 / Yaw SensTrack 2(0&deg | 2012-04-12 |  | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 11.25 | Forced |  |  | 3.9 | Highland 1 | Gathered up all of the correct tooling and traveled to site. Climbed tower and used the chain hoist to raise two loads of tools up to the nacelle. Began prepareing the yaw drives by removing the surrounding deck plates. Once the plates are removed then breakers 104f3, 124K2, 111AF3, and 120S1 are turned OFF. Then the covers removed on the yaw motors and lack of voltage was verified. With that the wires can be lifted, covered and move out of the way. Then the motors removed via four 19mm bolts and placed infront of the gen out of the way. Then we set up the hytorc and MXT 1 head with a 36mm socket. Using that we loosened and removed all of the attaching bolts from the base of the drives except one on each base which will get removed when the crane is ready to pick. With this complete we closed up the nacelle and climbed down tower and traveled back to the shop. | KRAYN-WKO-NDX-20120412 | 1
KRAYN-WKO-NDX-20120412-03 | FM490 / Yaw SensRuntimeToothToTooth TimeOut | 2012-04-12 |  | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 9.6833 | Highland 1 | Turbine faulted at 19:07 and tried to call my on call partner Charles Martin, 1 call to his work phone and 3 calls to his personal phone and no answer or call back. Called Willy Finch and headed to turbine. Assended turbine and checked yaw stacks for propper backlash, found hinge side yaw stack broken, and siezed, no movement when braked open.. Informed Jennings Lynch and Everpower | KRAYN-WKO-NDX-20120412 | 1
KRAYN-WKO-NDX-20120413-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-04-13 | 2012-04-13 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 14 | Forced | KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0959 | 1,1 | 48.3333 | Highland 1 | Met with the contractors from WTG at the shop and then traveled out to site. Apon arrival we dicussed the hazards of the days job and planned our lift with that in mind. We then unloaded the trucks and two of the WTS contractors climbed up tower. They lowered the chain hoist and we began hoisting up the rest of the equipment for the up tower cranes. With most of the tooling and equipmetn organized and ready to pick two Nordex techs climbed up tower. We finished the equipment picks and the up tower team began assembilling the up tower cranes. Once built we removed the hinge side yaw drive and sent it down tower. Then hoisted the new drive up tower and installed. With the drive in and the base bolts snugged the crane left the hinge side drive and hooked to the open side drive. Pulled the opened side drive and lowered it to the ground and into one of the new drives boxs. Then the other new drive got rigged and hoisted up to the nacelle. After arriving up tower the drive was set down into place. With this complete the crane was dismanteled and the yaw drives torqued down with the MXT 1 and hytorc pump. After that the decking was installed around the drives then the motors set down on the drives and wired. After the completion of the wiring the breakers were switch back on from the previous day by removing LOTO and returning 104F3, 111AF3, 124K2, and120S1 to ON. The original parameters where restored to the yaw convertor with the original torque setting. With that the turbine was reset and manually yawed. Packed up the remaining tooling and equipment and sent it down with the chain hoist. From down tower NC II was checked and found no faults or warnings. All personnel climbed down tower and Started the turbine with no defects noted at this time. | KRAYN-WKO-NDX-20120413 | 1
KRAYN-WKO-NDX-20120416-01 | Pitch 3 DC overcurrent | 2012-04-16 | 2012-04-16 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 6.0833 | Highland 1 | Got a hub slip ring after reviewing the logs. Traveled to site and entered the turbine. Pin wheeled turbine and heard a thud in the hub. Climbed the turbine and locked out the rotor. Moved out to the hub and entered the hub. Once there a broken blade bolt was found along with a nut and washer. removed all of the pieces and inspected fro damage. With no defects noted we left the hub and returned to the nacelle where we unlocked the rotor and reset the turbine. Everything looked good and we returned down tower via the ladder. Started the turbine and returned to the shop. | KRAYN-WKO-NDX-20120416 | 1
KRAYN-WKO-NDX-20120417-01 | FM6 / WTG Manual Stop | 2012-04-17 | 2012-04-17 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 10.75 | Planned |  |  | 7.5 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120417 | 1
KRAYN-WKO-NDX-20120417-02 | FM6 / WTG Manual Stop | 2012-04-17 | 2012-04-17 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 1 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 7.5 | Highland 1 | Arived on site, replaced bottom box filters. Accended tower, yaw ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather. | KRAYN-WKO-NDX-20120417 | 1
KRAYN-WKO-NDX-20120417-03 | MI Class B fault. | 2012-04-17 | 2012-04-17 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 10.25 | Forced | KRAYN-NDX-PRT-0683,0 | 1, | 7.3333 | Highland 1 | Saw turbine go down on NCII from shop. Drove to turbine. Checked logs for gen rotor and gen rotor MI to compare signals. The gen MI showed a low spike just before the fault occurred. Traveled back to the O&M for a replacement gen rpm encoder. Drove back to turbine. Climbed up turbine. Unbolted the encoder and unwired the old one. Replaced encoder and rewired new one. Cleaned up all parts and tools. Climbed back down turbine. Restarted turbine and trended the gen speeds again. Let turbine runa dn continued to watch for a period of time to make sure the fault did not reoccure. The turbine continued to run. Packed up truck and drove back to O&m building. Unloaded truck and completed service order. | KRAYN-WKO-NDX-20120417 | 1
KRAYN-WKO-NDX-20120417-04 | MI Class B fault. | 2012-04-17 | 2012-04-17 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 10.25 | Forced | KRAYN-NDX-PRT-0683 | 1 | 7.3333 | Highland 1 | Saw turbine go down on NCII from shop. Drove to turbine. Checked logs for gen rotor and gen rotor MI to compare signals. The gen MI showed a low spike just before the fault occurred. Traveled back to the O&M for a replacement gen rpm encoder. Drove back to turbine. Climbed up turbine. Unbolted the encoder and unwired the old one. Replaced encoder and rewired new one. Cleaned up all parts and tools. Climbed back down turbine. Restarted turbine and trended the gen speeds again. Let turbine runa dn continued to watch for a period of time to make sure the fault did not reoccure. The turbine continued to run. Packed up truck and drove back to O&m building. Unloaded truck and completed service order. | KRAYN-WKO-NDX-20120417 | 1
KRAYN-WKO-NDX-20120418-01 | FM6 / WTG Manual Stop | 2012-04-18 | 2012-04-18 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned |  |  | 6.9833 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120418-02 | No work order description provided by contractor | 2012-04-18 | 2012-04-18 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 1.5833 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,1kg | 6.9833 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120418-03 | No work order description provided by contractor | 2012-04-18 | 2012-04-19 | KRAYN-WTG07 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 12.45 | Highland 1 | Installed rear nacelle fan cover. | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120418-04 | No work order description provided by contractor | 2012-04-18 | 2012-04-19 | KRAYN-WTG07 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 12.45 | Highland 1 | Jib crane positioning nut was installed. | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120418-05 | No work order description provided by contractor | 2012-04-18 | 2012-04-19 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 12.45 | Highland 1 | Shaft cover retro was completed. One cover section for the HSS was craned uptower. | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120418-06 | Wind turbine manual stop | 2012-04-18 | 2012-04-19 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 14.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0697 | 10,2.5,6 | 12.45 | Highland 1 | Completed Maintenance III stage one and two (with the exception of tower torque, shaft nut, and bottom coolant sample, main shaft and rotor torque, tower torque and turbine final cleaning). | KRAYN-WKO-NDX-20120418 | 1
KRAYN-WKO-NDX-20120419-01 | FM6 / WTG Manual Stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 5.3 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120419-02 | FM6 / WTG Manual Stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 5.3 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120419-03 | FM6 / WTG Manual Stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 5 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120419-04 | FM6 / WTG Manual Stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0009,KRAYN-NDX-PRT-0364 | 1,1,1,1,2,3.2kg | 5 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120419-05 | Wind turbine manual stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.9667 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120419-06 | Wind turbine manual stop | 2012-04-19 | 2012-04-19 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned |  |  | 5.9667 | Highland 1 | Completed Maintenance III stage one and two (tower torque, shaft nut, bottom coolant sample, main shaft rotor torque, tower torque, and turbine final cleaning). | KRAYN-WKO-NDX-20120419 | 1
KRAYN-WKO-NDX-20120420-01 | FM6 / WTG Manual Stop | 2012-04-20 | 2012-04-20 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 5.1 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120420 | 1
KRAYN-WKO-NDX-20120420-02 | FM6 / WTG Manual Stop | 2012-04-20 | 2012-04-20 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 5.1 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120420 | 1
KRAYN-WKO-NDX-20120420-03 | FM6 / WTG Manual Stop | 2012-04-20 | 2012-04-20 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 4.5833 | Planned |  |  | 5.2 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120420 | 1
KRAYN-WKO-NDX-20120420-04 | FM6 / WTG Manual Stop | 2012-04-20 | 2012-04-20 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 5.2 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120420 | 1
KRAYN-WKO-NDX-20120424-01 | No work order description provided by contractor | 2012-04-24 | 2012-04-25 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 10.65 | Highland 1 | Fire extinguishers were swapped. The charged one from downtower was cranned up while the old one was brought down. | KRAYN-WKO-NDX-20120424 | 1
KRAYN-WKO-NDX-20120424-02 | No work order description provided by contractor | 2012-04-24 | 2012-04-25 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0320 | 1 | 10.65 | Highland 1 | Hydac pump was replaced. | KRAYN-WKO-NDX-20120424 | 1
KRAYN-WKO-NDX-20120424-03 | No work order description provided by contractor | 2012-04-24 | 2012-04-25 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 10.65 | Highland 1 | Shaft cover retro was completed. Four cover sections were craned uptower….for the gearbox. | KRAYN-WKO-NDX-20120424 | 1
KRAYN-WKO-NDX-20120425-01 | No work order description provided by contractor | 2012-04-25 | 2012-04-25 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 10.65 | Highland 1 | Performed gen alignment. All points were within tolerance. | KRAYN-WKO-NDX-20120425 | 1
KRAYN-WKO-NDX-20120425-02 | No work order description provided by contractor | 2012-04-25 | 2012-04-25 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0013 | 1 | 10.65 | Highland 1 | Hydac sight glass was replaced. | KRAYN-WKO-NDX-20120425 | 1
KRAYN-WKO-NDX-20120425-03 | No work order description provided by contractor | 2012-04-25 | 2012-04-25 | KRAYN-WTG05 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 10.65 | Highland 1 | Yaw parameters were updated | KRAYN-WKO-NDX-20120425 | 1
KRAYN-WKO-NDX-20120426-01 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 9.9333 | Highland 1 | Installed all shaft covers for the rotor and high speed shaft. | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120426-02 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 2.5 | Planned |  |  | 9.9333 | Highland 1 | Moved new certified fire extinguisher up tower and moved old one to first deck for recertification. | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120426-03 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.4667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120426-04 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 6.4667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120426-05 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 8 | Planned |  |  | 6.4667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120426-06 | FM6 / WTG Manual Stop | 2012-04-26 | 2012-04-26 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 6.4667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120426 | 1
KRAYN-WKO-NDX-20120427-01 | FM6 / WTG Manual Stop | 2012-04-27 | 2012-04-27 | KRAYN-WTG05 | Preventive Maintenance | Nordex USA OandM | 7.25 | Planned |  |  | 5.75 | Highland 1 | Performed the Safety functions test, as well as yaw limit switch test. | KRAYN-WKO-NDX-20120427 | 1
KRAYN-WKO-NDX-20120427-02 | FM6 / WTG Manual Stop | 2012-04-27 | 2012-04-27 | KRAYN-WTG07 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 4.4 | Highland 1 | Main 3 stage 3 ( Function Test ) | KRAYN-WKO-NDX-20120427 | 1
KRAYN-WKO-NDX-20120427-03 | FM6 / WTG Manual Stop | 2012-04-27 | 2012-04-27 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 4.4 | Highland 1 | Install new yaw torque parameters per engineering | KRAYN-WKO-NDX-20120427 | 1
KRAYN-WKO-NDX-20120428-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-04-28 |  | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 7.25 | Forced |  |  | 0.93333 | Highland 1 | Prep yaw stacks for removal. | KRAYN-WKO-NDX-20120428 | 1
KRAYN-WKO-NDX-20120428-02 | FM6 / WTG Manual Stop | 2012-04-28 | 2012-04-28 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 8.65 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120428 | 1
KRAYN-WKO-NDX-20120428-03 | FM6 / WTG Manual Stop | 2012-04-28 | 2012-04-28 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,1 kg | 8.65 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120428 | 1
KRAYN-WKO-NDX-20120501-01 | FM492 / Yaw SensTrack 2(0&deg | 2012-05-01 | 2012-05-02 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 44.75 | Forced | KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0959 | 1,1 | 108.1833 | Highland 1 | Most WTS equipment was already prepped for Yaw stack change out. Got all equipment up tower. Changed out first yaw stack. Changed out second yaw stack. Sent down all parts and equipment. Packed up trucks. Reset faults. Turbine was in ok status, but in an FM1002 with winds too low to start. Drove back to O&M building. Unloaded truck. Completed service order. | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120501-02 | FM6 / WTG Manual Stop | 2012-05-01 | 2012-05-01 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 5 | Planned |  |  | 6.25 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120501-03 | FM6 / WTG Manual Stop | 2012-05-01 | 2012-05-01 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364 | 1,1,1,2 | 6.25 | Highland 1 | In conjunction with gear box oil change, changed air filters on the bottom box, the main gear oil filter, the bypass filter, the hyd station filter, the generator air filter mats, and filled the yaw ALU. | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120501-04 | FM6 / WTG Manual Stop | 2012-05-01 | 2012-05-02 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 6.5 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120501-05 | FM6 / WTG Manual Stop | 2012-05-01 | 2012-05-02 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 2 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017 | 1,1,1 | 6.5 | Highland 1 | In conjunction with gear box oil change, changed the main gear oil filter, the bypass filter, the hyd station filter, the generator air filter mats. | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120501-06 | FM1211 / MI GridDiscon DespiteReleaseForOp. | 2012-05-01 | 2012-05-01 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 5.3167 | Highland 1 | Drove to turbine #25 on the way to turbine #1. Found door pryed open with cable broken. There was a rock wedged in the bottom of the door. Found the key on the SEG cabinet turned to service. Reset key to auto. Found odd program ( MS notebook) open on monitor. Closed program. Opened NCII. Restarted turbine. Notified supervision of possible vandalism. Continued to turbine #1. | KRAYN-WKO-NDX-20120501 | 1
KRAYN-WKO-NDX-20120502-01 | FM419 / Yaw HydBrk not closed | 2012-05-02 | 2012-05-02 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 1.6667 | Forced |  |  | 4.6667 | Highland 1 | Nordex technicians attended tower 2 to correct a yaw hyd brake not open fault. Installed the black relay provided by engineering. Problem seems to be corrected. Will continue to monitor. | KRAYN-WKO-NDX-20120502 | 1
KRAYN-WKO-NDX-20120502-02 | FM6 / WTG Manual Stop | 2012-05-02 | 2012-05-02 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 4.5 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120502 | 1
KRAYN-WKO-NDX-20120502-03 | FM6 / WTG Manual Stop | 2012-05-02 | 2012-05-02 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1.6667 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0350 | 1,1,1,2,1 | 4.5 | Highland 1 | In conjunction with gear box oil change, changed the main gear oil filter, the bypass filter, the hyd station filter, the generator air filter mats. | KRAYN-WKO-NDX-20120502 | 1
KRAYN-WKO-NDX-20120503-01 | FM618 / WFM CommunicationFault Warn | 2012-05-03 | 2012-05-03 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 7.5 | Forced | KRAYN-NDX-PRT-0043,KRAYN-NDX-PRT-0090 | 2,3 | 9.9833 | Highland 1 | Opened Bottom Box, Nordex side and 153F7 was triped. We then checked terminal strip X8,X8.1 and X8.2 for blown suppression diode's. On strip X8, diode's 9,10,33 and 34 was blown. On strip X8.1, diode's 45 and 53 where blown. On strip X8.2, diode 2 was blown. We replaced all blown diode's Eever Power is responsable for diode's 9,10,33 and 34 on strip X8 and we where responsable for the remaining diode's. We also replaced a 2A 250V fuse from interbus module 151A3. We then accended tower, replaced 2A 250V fuse from interbus module 105A2 in TopBox and installed gounding cable for FAA light. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120503 | 1
KRAYN-WKO-NDX-20120505-01 | FM6 / WTG Manual Stop | 2012-05-05 | 2012-05-05 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned |  |  | 4.7833 | Highland 1 | Gearbox oil change | KRAYN-WKO-NDX-20120505 | 1
KRAYN-WKO-NDX-20120505-02 | FM6 / WTG Manual Stop | 2012-05-05 | 2012-05-05 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 1.75 | Planned | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364 | 1,1,1,1,1 | 4.7833 | Highland 1 | Changed main oil filter, offline filter, hydraulic filter, filled yaw alu, replaced main converter air filters, replaced generator air filter, left gearbox air filter on gearbox. | KRAYN-WKO-NDX-20120505 | 1
KRAYN-WKO-NDX-20120505-03 | FM6 / WTG Manual Stop | 2012-05-05 | 2012-05-05 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 4.75 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120505 | 1
KRAYN-WKO-NDX-20120505-04 | FM6 / WTG Manual Stop | 2012-05-05 | 2012-05-05 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 1.75 | Planned | KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0364 | 1,1,1,1,1 | 4.75 | Highland 1 | Changed gearbox air filter, main oil filter, offline oil filter, hydraulic filter, filled yaw alu. | KRAYN-WKO-NDX-20120505 | 1
KRAYN-WKO-NDX-20120505-05 | FM1172 / Pitch PowerVolt. Fault | 2012-05-05 | 2012-05-05 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 10.3 | Highland 1 | Approached doen turbine and assended tower. Inside the hub found a broken blade bolt in blade 2 position 32. recovered blade bolt and washer. Broken blade bolt damaged 400 volt power plug in pitch motor 1. Fixed briken plug. Reset and checked for propper pitch function and desended tower. Started turbine. | KRAYN-WKO-NDX-20120505 | 1
KRAYN-WKO-NDX-20120506-01 | Yaw Brake Not Open | 2012-05-06 | 2012-05-07 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 5.6167 | Highland 1 | Arrived at turbine in respoce to FM420. The jumping of 121K1 saw no movement from the yaw brakes but pins 13 and 14 associated did receive power indicating the the relay was functioning properly. Power was then confirmed to be present in Box 6. Next, pressure was drained from the hyd station and valve 210 was removed, cleaned and physically acctuated. Valve 210 was then replaced and the fault cleared via NC2. The turbine was yawed in manual several times without incident. | KRAYN-WKO-NDX-20120506 | 1
KRAYN-WKO-NDX-20120507-01 | Wind turbine manual stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 6.4 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-02 | Wind turbine manual stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 8.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058 | 8,4 | 6.4 | Highland 1 | Completed maintenance ( Shaft nut, ALU were filled, Generator slip ring was cleaned, Fluid samples were taken, and visual inspections) | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-03 | FM6 / WTG Manual Stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 4.7667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-04 | FM6 / WTG Manual Stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 4.7667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-05 | manual stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0322 | 5,1 | 6.2333 | Highland 1 | Maint 3 partially complete (due to lightning). Completed hub work is as follows; slip ring inspected and lubbed, all blades greased, zeroed, and aligned. Nacelle work as followes; wind sensors tested and aligned, gen slip ring inspected and measured, hyd station maint., various visual inspections. | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-06 | FM6 / WTG Manual Stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 6.3333 | Highland 1 | Installed FAA ground as per Sean Illig for static electricity discharge. | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120507-07 | FM6 / WTG Manual Stop | 2012-05-07 | 2012-05-07 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0320 | 1 | 6.3333 | Highland 1 | Install new Hyde pump inside hyde station. Work included dismantaling Hyde motor and getting to the pump inside the station, dismantaling pump from motor and reassembling all parts. | KRAYN-WKO-NDX-20120507 | 1
KRAYN-WKO-NDX-20120508-01 | FM307 / Gen brushWear Warn | 2012-05-08 | 2012-05-08 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 4.6833 | Highland 1 | Installed 100% torque yaw parameters per engineering request for tubines with new yaw drives. | KRAYN-WKO-NDX-20120508 | 1
KRAYN-WKO-NDX-20120508-02 | FM307 / Gen brushWear Warn | 2012-05-08 | 2012-05-08 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 4.6833 | Highland 1 | Approached turbine and L.O.T.O the Q10p. Assended tower and troubleshoot the gen slip rings gen brush limit switches. Found switch on brush L4 dirty and spring needed to be cleaned and adjusted.Reassembled and unlocked Q10p and reset turbine. | KRAYN-WKO-NDX-20120508 | 1
KRAYN-WKO-NDX-20120508-03 | FM307 / Gen brushWear Warn | 2012-05-08 | 2012-05-08 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 3 | Planned |  |  | 4.6833 | Highland 1 | Maintenance 3 stage 3. Function test | KRAYN-WKO-NDX-20120508 | 1
KRAYN-WKO-NDX-20120508-04 | FM6 / WTG Manual Stop | 2012-05-08 | 2012-05-08 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 4.8667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120508 | 1
KRAYN-WKO-NDX-20120508-05 | FM6 / WTG Manual Stop | 2012-05-08 | 2012-05-08 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 4.8667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120508 | 1
KRAYN-WKO-NDX-20120509-01 | FM6 / WTG Manual Stop | 2012-05-09 | 2012-05-10 | KRAYN-WTG02 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 10.8833 | Highland 1 | Loaded 100% torque parameters. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-02 | manual stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0062 | 2 | 9.85 | Highland 1 | Maint. 3 was completed. All screw checks, function tests, cleaning and inspections were completed. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-03 | manual stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 1.75 | Forced |  |  | 9.85 | Highland 1 | Yaw parameters were updated. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-04 | FM6 / WTG Manual Stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 4.15 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-05 | FM6 / WTG Manual Stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 3.9833 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-06 | FM6 / WTG Manual Stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 3.9833 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-07 | FM6 / WTG Manual Stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 4.15 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-08 | Wind turbine manual stop | 2012-05-09 | 2012-05-10 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 17.25 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0962,KRAYN-NDX-PRT-0363 | 6,1,20 | 10.8833 | Highland 1 | Completed Maintenance III stage one: ( blade grease and torque, slip ring cleaning, function test, collection bottle change, final cleaning) Stage two:(tower torque, bottom coolant sample, main shaft rotor torque, Gen align, Hyd station, yaw deck and turbine final cleaning). | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-09 | manual stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 9.85 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120509-10 | manual stop | 2012-05-09 | 2012-05-09 | KRAYN-WTG03 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 9.85 | Highland 1 | Generator was aligned. Was off both 1mil. vertically and .3 mils horizontally. This was corrected. | KRAYN-WKO-NDX-20120509 | 1
KRAYN-WKO-NDX-20120510-01 | FM1209 / MI class C (Service!) Fault | 2012-05-10 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 11.5 | Forced |  |  | 6.4 | Highland 1 | Drove to turbine. Turbine faulted with MI class B and C. Isolated IGBT's on both line and machine side. individually to check for proper function. Found fault on line side and machine side of converter through the SEG information screen. Went to get an IGBT and other tooling to have on-site if needed. Turbine would run for about 5-10 min and fault again. Looked at event recorder from CSC3 program. Found that on the faults occurring today that the L2 and L3 windings showed abnormal (choppy or rigid) values and L1 was smooth until the fault. Switched the rotor cables to see if the values moved or if the readings were inaccurate. The readings did carry over to the L1 winding. Went back to shop to get a Megger. Took readings of the rotor cables down in the bottom box. The L2 and L3 cables showed a very low resistance of 1.88 K ohms. Went up tower to verify that the short was in the Generator. Checked the K, M, and L slip ring for resistance. Again the K and L showed a short directly on the slip ring, where the K/M and L/M showed high resistance (normal reading). It was then determined that there is a short in the Generator. Pack up all tools and went down tower. Made sure that all tools and parts were cleaned up. Closed all doors. Blocked the switch right to the turbine. Left for the O&M building. | KRAYN-WKO-NDX-20120510 | 1
KRAYN-WKO-NDX-20120514-01 | FM6 / WTG Manual Stop | 2012-05-14 | 2012-05-14 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned |  |  | 2.6833 | Highland 1 | Function Tests | KRAYN-WKO-NDX-20120514 | 1
KRAYN-WKO-NDX-20120514-02 | FM6 / WTG Manual Stop | 2012-05-14 | 2012-05-14 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned |  |  | 2.6833 | Highland 1 | Function Tests | KRAYN-WKO-NDX-20120514 | 1
KRAYN-WKO-NDX-20120514-03 | FM6 / WTG Manual Stop | 2012-05-14 | 2012-05-14 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 4.9 | Highland 1 | Maintenance type 3 stage 3. Function test. | KRAYN-WKO-NDX-20120514 | 1
KRAYN-WKO-NDX-20120514-04 | FM6 / WTG Manual Stop | 2012-05-14 | 2012-05-14 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3.75 | Planned | KRAYN-NDX-PRT-0632 | 1 | 4.9 | Highland 1 | Installed new SUR in SEG cabinet.The old SUR would not take triggers. Did not verify new SUR due to yaw cable rewind from stage 3 function test. | KRAYN-WKO-NDX-20120514 | 1
KRAYN-WKO-NDX-20120514-05 | FM6 / WTG Manual Stop | 2012-05-14 | 2012-05-14 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 2.25 | Forced |  |  | 4.9 | Highland 1 | Install reduced yaw parameters per engineering request for older yaw stacks | KRAYN-WKO-NDX-20120514 | 1
KRAYN-WKO-NDX-20120515-01 | FM6 / WTG Manual Stop | 2012-05-15 |  | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0058 | 8,12,6,3kg | 0 | Highland 1 | Type 3 maintenance stage one and stage two. | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-02 | Wind turbine manual stop | 2012-05-15 | 2012-05-16 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 14.25 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0697 | 3,8,14,3 | 12.3833 | Highland 1 | Completed Maintenance III stage one and two(with the exception of nacelle cleaning). | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-03 | FM1209 / MI class C (Service!) Fault | 2012-05-15 |  | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 24.2333 | Highland 1 | Install 75% yaw torque parameters per engineering request on old yaw drive stacks. | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-04 | FM1209 / MI class C (Service!) Fault | 2012-05-15 |  | KRAYN-WTG06 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 24.2333 | Highland 1 | Install grounding wire from FAA light to ground per Sean Illig request to help with static discharge from lightning storms. | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-05 | FM1209 / MI class C (Service!) Fault | 2012-05-15 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced |  |  | 24.2333 | Highland 1 | Megger check of the rotor and stator windings. Phase to Phase and Phase to ground for engineering including documentation and pictures. Prep gen for work to be done on Thursday. | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-06 | FM6 / WTG Manual Stop | 2012-05-15 | 2012-05-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 7.1667 | Planned |  |  | 5.3167 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-07 | FM6 / WTG Manual Stop | 2012-05-15 | 2012-05-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 5.4833 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120515-08 | FM6 / WTG Manual Stop | 2012-05-15 | 2012-05-15 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 5.8333 | Planned |  |  | 3.1667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120515 | 1
KRAYN-WKO-NDX-20120516-01 | manual stop | 2012-05-16 | 2012-05-16 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 6.8667 | Highland 1 | Completed function tests as part of Maint. 3 | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-02 | manual stop | 2012-05-16 | 2012-05-16 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 5 | Forced |  |  | 6.8667 | Highland 1 | Performed visual inspection (pictures will follow) of the generator rotor wires. This required removal of the encoder which, in turn, required re-commissioning. | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-03 | Wind turbine manual stop | 2012-05-16 | 2012-05-17 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 11.0333 | Highland 1 | Replaced shaft covers on high speed side. speed shaft. | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-04 | Wind turbine manual stop | 2012-05-16 | 2012-05-17 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13.5 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0697,KRAYN-NDX-PRT-0963 | 3,8,16,3,3 | 11.0333 | Highland 1 | Completed Maintenance III stage one and two(with the exception of nacelle cleaning). | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-05 | Wind turbine manual stop | 2012-05-16 | 2012-05-17 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 11.0333 | Highland 1 | Replaced shaft covers on high speed side. speed shaft. | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-06 | Wind turbine manual stop | 2012-05-16 | 2012-05-17 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 13.5 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0697,KRAYN-NDX-PRT-0963 | 3,8,16,3,3 | 11.0333 | Highland 1 | Completed Maintenance III stage one and two(with the exception of nacelle cleaning). | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-07 | FM6 / WTG Manual Stop | 2012-05-16 | 2012-05-16 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 3.7833 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120516-08 | FM6 / WTG Manual Stop | 2012-05-16 | 2012-05-16 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 3.7833 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120516 | 1
KRAYN-WKO-NDX-20120517-01 | FM6 / WTG Manual Stop | 2012-05-17 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 12.5 | Forced |  |  | 0 | Highland 1 | Assended turbine. Hoisted up parts and tooling to start dissembling the generator. Started by pulling the housing off from around the generator slip ring. Had to diconnect the leads from the junction box at the back of the generator. Removed the bridge that the gen brushes sit in. Applied a puller mechanism to the back of the slip ring to begin removing it. Used a enerpac hydraulic ram to pull the slip ring off the rotor shaft. Began removing the grounding ring from the rotor shaft. Prepped for Fridays work. Came down tower. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-02 | Yaw Motor Break Not Open | 2012-05-17 | 2012-05-17 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0961 | 1 | 4.9667 | Highland 1 | Replace 124A1 yaw motor timer relay, Troubleshot gen brush wear warning, jump out phase side to see if fault returned. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-03 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 11.4333 | Highland 1 | Grounding wire was installed on FAA light. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-04 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 11.4333 | Highland 1 | Gearbox was inspected. Photos to follow. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-05 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 11.4333 | Highland 1 | Generator was aligned. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-06 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0322,KRAYN-NDX-PRT-0062 | 100 grams,1,8 | 11.0667 | Highland 1 | Maint. 3 | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-07 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 11.0667 | Highland 1 | Installed repaired shaft covers. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-08 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 11.4333 | Highland 1 | Grounding wire was installed on FAA light. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-09 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 11.4333 | Highland 1 | Gearbox was inspected. Photos to follow. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-10 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 1 | Forced |  |  | 11.4333 | Highland 1 | Generator was aligned. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-11 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0964,KRAYN-NDX-PRT-0322,KRAYN-NDX-PRT-0062 | 100 grams,1,8 | 11.0667 | Highland 1 | Maint. 3 | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-12 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 11.0667 | Highland 1 | Installed repaired shaft covers. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-13 | manual stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 11.0667 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-14 | FM6 / WTG Manual Stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 4.75 | Planned |  |  | 4.4 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-15 | FM6 / WTG Manual Stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 4.4 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-16 | FM6 / WTG Manual Stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 5.25 | Planned |  |  | 3.2667 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120517-17 | FM6 / WTG Manual Stop | 2012-05-17 | 2012-05-17 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 3.2667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120517 | 1
KRAYN-WKO-NDX-20120518-01 | FM6 / WTG Manual Stop | 2012-05-18 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 16 | Forced |  |  | 0 | Highland 1 | Ascended Turbine. Locked out rotor. Lowered hoist for additional parts. Started by removing the dust cover from the back of the generator. After removing the dust cover we used all thread to pull the grease slinger off of the shaft. Once the grease slinger was removed that allowed us to access the rear generator bearing housing. Removed the rear generator bearing from the shaft. Applied heat with a torch to the rear generator bearing inner race to remove it from the shaft.began prepping the rear bell housing for removal. We attached a chain hoist to the lifting eye and ran 2 pieces of all the 180 degrees apart through the bolt holes into the generator. We removed all the bolts from the bell housing and begain sliding the bell housing off while using the all thread and chain hoist as a guide. Once the bell housing was removed that exposed the rotor of the generator. We then removed the cover of the rotor and started to cut and pull the wires out of the shaft. Ran a Motor Circut Evaluation test on the rotor and stator. Organized and prepped turbine for work tomorrow. Hoisted tooling and bad parts down tower. Descended tower. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-02 | FM1143 / Pitchangle 3 Diff.Set-RedAct | 2012-05-18 | 2012-05-18 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 7.3333 | Forced | KRAYN-NDX-PRT-0264 | 1 | 6.3333 | Highland 1 | Nordex technicians attended tower 9 to repair damage in hub caused by loose pitch box cover. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-03 | FM1143 / Pitchangle 3 Diff.Set-RedAct | 2012-05-18 | 2012-05-18 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 7.3333 | Forced | KRAYN-NDX-PRT-0264 | 1 | 6.3333 | Highland 1 | Nordex technicians attended tower 9 to repair damage in hub caused by loose pitch box cover. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-04 | MI Class B | 2012-05-18 | 2012-05-18 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 0.96667 | Highland 1 | MI class B, reset and pulled triggers | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-05 | FM6 / WTG Manual Stop | 2012-05-18 | 2012-05-18 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 3.7667 | Highland 1 | Oil Change. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-06 | FM5 / WTG ManualControlTurbine | 2012-05-18 | 2012-05-18 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 3.7667 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-07 | FM6 / WTG Manual Stop | 2012-05-18 | 2012-05-18 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 4.5 | Planned |  |  | 3 | Highland 1 | Gear Box Oil Change | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120518-08 | FM6 / WTG Manual Stop | 2012-05-18 |  | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned | KRAYN-NDX-PRT-0325,KRAYN-NDX-PRT-0356,KRAYN-NDX-PRT-0017,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0364 | 1,1,1,1,3.2kg | 3 | Highland 1 | Arived on site, replaced bottom box filters, filled coolant station down tower. Accended tower, filled gen ALU, yaw ALU and main bearing ALU. Killed 400, changed gearbox oil filter, by-pass filter and hyd station filter and gearbox filter breather and checked accumulator pressure. Light cleaning in Nacelle. | KRAYN-WKO-NDX-20120518 | 1
KRAYN-WKO-NDX-20120519-01 | Top Box Cabinet Temp Stop | 2012-05-19 | 2012-05-19 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 3.4333 | Highland 1 | Top Box Cabinet Doors open | KRAYN-WKO-NDX-20120519 | 1
KRAYN-WKO-NDX-20120519-02 | No work order description provided by contractor | 2012-05-19 | 2012-05-19 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.9 | Highland 1 | Changed Slip Ring | KRAYN-WKO-NDX-20120519 | 1
KRAYN-WKO-NDX-20120521-01 | FM6 / WTG Manual Stop | 2012-05-21 |  | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 14 | Forced |  |  | 0 | Highland 1 | Ascended turbine. Used the hoist to lift up tooling and parts for todays work. Began by cleaning the filler out of the generator shaft. Had to out of the holes in the shaft that the leads run through from the rotor. There is a very thick layer of varnish that coats the leads from the rotor which we had to remove with a chisel, hammer, and drill. We cleaned and prepped the gen. parts for reinstallation. After all the parts we cleaned we started to run the new leads through the shaft and bolted them to the rotor. Filled the shaft with a filler compound. We put the rotor cover on. Prepped for work on Tuesday. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-02 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 5.8167 | Highland 1 | Turbine had been running with an intermitent FM 307 gen brush wear warning. Climbed the tower and began to isolate each section of brushes and found that the front grounding brush mirco switch was causeing the warning. Since these have been removed earlier in the turbines life they are no longer needed to be monitored so we jumped out that section and the warning went away. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-03 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 6.5 | Planned |  |  | 5.8167 | Highland 1 | Was up tower from other work and once finished begain the final cleaning for the TYPE III. CLEANED, CLEANED, CLEANED nacelle then CLEANED the yaw deck then picked up loose zip ties on decks on the way down. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-04 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.8167 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-05 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 2.25 | Planned |  |  | 4.9833 | Highland 1 | Realign the generator for Main 3 | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-06 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG04 | Preventive Maintenance | Nordex USA OandM | 5.75 | Planned |  |  | 4.9833 | Highland 1 | Main. 3 stage 3 ( function test) | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-07 | Wind turbine manual stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 3.0667 | Highland 1 | Drove to turbine. Climbed tower. Replaced shaft covers on slow speed side. Readjusted sensors. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-08 | Wind turbine manual stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 3.0667 | Highland 1 | Finished cleaning nacelle for maintenance type III. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-09 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 4.0833 | Planned |  |  | 3.1333 | Highland 1 | Cleaned nacelle, conducted bottom box maintenance. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-10 | Wind turbine manual stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG08 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 3.0667 | Highland 1 | Drove to turbine. Climbed tower. Replaced shaft covers on slow speed side. Readjusted sensors. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-11 | Wind turbine manual stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG08 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 3.0667 | Highland 1 | Finished cleaning nacelle for maintenance type III. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120521-12 | FM6 / WTG Manual Stop | 2012-05-21 | 2012-05-21 | KRAYN-WTG09 | Preventive Maintenance | Nordex USA OandM | 4.0833 | Planned |  |  | 3.1333 | Highland 1 | Cleaned nacelle, conducted bottom box maintenance. | KRAYN-WKO-NDX-20120521 | 1
KRAYN-WKO-NDX-20120522-01 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced |  |  | 7.8333 | Highland 1 | Installed grounding cable to FAA light. | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-02 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 7.8333 | Highland 1 | Completed funtions test and gearbox inspection ( with the exception of overspeed test due to lack of wind). | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-03 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 7.8333 | Highland 1 | Installed Yaw parameters to 100% torque as per instructed. | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-04 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 10 | Planned |  |  | 6.4667 | Highland 1 | Function Tests. Type 3 mx | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-05 | Wind turbine manual stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 7 | Planned |  |  | 6 | Highland 1 | Nordex Technician did safety functions tests, as well as various nacelle an bottom box checks. | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-06 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG25 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 5.1167 | Highland 1 | Installed grounding wire from FAA light to frame of the naccelle per Sean Illig request for static discharge during a lightning storm. | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-07 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 5.1167 | Highland 1 | Maintenance type 3 stage 3 Function test and gear box inspection. | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120522-08 | FM6 / WTG Manual Stop | 2012-05-22 | 2012-05-22 | KRAYN-WTG25 | Retrofit | Nordex USA OandM | 2.5 | Forced |  |  | 5.1167 | Highland 1 | Installed 75 % torque yaw parameters as per engineering request for all old yaw stacks | KRAYN-WKO-NDX-20120522 | 1
KRAYN-WKO-NDX-20120523-01 | FM6 / WTG Manual Stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 13.5 | Forced |  |  | 300.4333 | Highland 1 | Ascended turbine.Installed the bridge that the slip ring brushes sit in to the back of the generator. With a chain fall hoisted the rear bell housing up and slid it over the slipring and mounted it to the back of the generator.Mounted the little junction box onto the side of the end bell housing next to the top cabinet. Hooked up the leads from the junction box to the slip ring bridge. Bolted the leads in the junction box to the bus bars.Started mounting the slip ring fan and ducting to the back of the slip ring. Performed a Motor Circuit Evaluation on the generator. Cleaned nacelle and organized tooling. Sent tools down on chain hoist. Descended turbine. Started turbine. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-02 | FM6 / WTG Manual Stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 9.1833 | Highland 1 | Realign Generator | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-03 | FM6 / WTG Manual Stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 9.1833 | Highland 1 | Install new positioning nut for chain hoist. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-04 | FM6 / WTG Manual Stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 8.5 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0058 | 8,2,6,3 kg | 9.1833 | Highland 1 | Maintenance 3 stage 1 and 2 | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-05 | FM6 / WTG Manual Stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG22 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 9.1833 | Highland 1 | Verified seviced fire ext was up and ext in need of service was down. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-06 | Wind turbine manual stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 9.8833 | Highland 1 | Switched out old fire extinquishers for newly inspected ones. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-07 | Wind turbine manual stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 9.8833 | Highland 1 | Completed alignment of generator. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120523-08 | Wind turbine manual stop | 2012-05-23 | 2012-05-23 | KRAYN-WTG23 | Preventive Maintenance | Nordex USA OandM | 28.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0322 | 8,3,14,1 | 9.8833 | Highland 1 | Completed maintenance type III stages 1 and 2. | KRAYN-WKO-NDX-20120523 | 1
KRAYN-WKO-NDX-20120524-01 | FM1157 / Pitchangle 2 Diff.Act-RedAct | 2012-05-24 | 2012-05-25 | KRAYN-WTG13 | General Maintenance | Nordex USA OandM | 14.5 | Forced | KRAYN-NDX-PRT-0959 | 1 | 15.7667 | Highland 1 | Performed bolt extraction per Jeremy Zorns request. Blade 2 position 31. After trouble shooting fault we called Willie Finch to bring all tools necessary for bolt extraction. After moving tools into the hub we started the extraction by drilling and stepping up sizes 5 times for the eazy out. Extracted bolt and inspected bolt hole, documented and bora scoped hole. Installed new blade bolt, moved all tools out of the hub. Desended down the tower and reset and started the turbine. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-02 | FM1157 / Pitchangle 2 Diff.Act-RedAct | 2012-05-24 | 2012-05-25 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced |  |  | 15.7667 | Highland 1 | Approached down turbine with maintenance crew. Upon entry of the hub found signs of a broken blade bolt. After searching the hub found broken blade bolt from blade 2 position 31. During operation of the turbine the bolt damaged the encoder. Replaced encoder, checkd NC2 for function af the pitch and reset the turbine. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-03 | FM1157 / Pitchangle 2 Diff.Act-RedAct | 2012-05-24 | 2012-05-25 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0467 | 1 | 15.7667 | Highland 1 | Approached down turbine with maintenance crew. Upon entry of the hub found signs of a broken blade bolt. After searching the hub found broken blade bolt from blade 2 position 31. During operation of the turbine the bolt damaged the encoder. Replaced encoder, checkd NC2 for function af the pitch and reset the turbine. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-04 | FM1157 / Pitchangle 2 Diff.Act-RedAct | 2012-05-24 | 2012-05-25 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 15.7667 | Highland 1 | Installed new positioning nut for the chain hoist. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-05 | FM1157 / Pitchangle 2 Diff.Act-RedAct | 2012-05-24 | 2012-05-25 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 5 | Planned | KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0009 | 3 kg,2,2,1 | 15.7667 | Highland 1 | Preformed Main. 3 stage 2. Did not complete Bottom box | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-06 | Wind turbine manual stop | 2012-05-24 | 2012-05-24 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 9.4667 | Highland 1 | Replaced fire extinguisher with newly inspected one. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120524-07 | Wind turbine manual stop | 2012-05-24 | 2012-05-24 | KRAYN-WTG24 | Preventive Maintenance | Nordex USA OandM | 30.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0290,KRAYN-NDX-PRT-0029 | 8,3,10,70,4 | 9.4667 | Highland 1 | Completed maintenance type III stages 1 and 2. | KRAYN-WKO-NDX-20120524 | 1
KRAYN-WKO-NDX-20120525-01 | FM6 / WTG Manual Stop | 2012-05-25 | 2012-05-25 | KRAYN-WTG06 | Preventive Maintenance | Nordex USA OandM | 6.75 | Planned |  |  | 4.5167 | Highland 1 | Completed type III stage 3(function tests) maintenance. | KRAYN-WKO-NDX-20120525 | 1
KRAYN-WKO-NDX-20120526-01 | FM332 / LV Griderror 660V Alarm | 2012-05-26 | 2012-05-27 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 0.75 | Forced |  |  | 4.0833 | Highland 1 | Nordex technicians attended tower 12 to reset a fault caused by a grid error. | KRAYN-WKO-NDX-20120526 | 1
KRAYN-WKO-NDX-20120526-02 | FM1208 / MI class B Fault | 2012-05-26 | 2012-05-27 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 4.1333 | Highland 1 | Lightning stand down from 18:00 till 20:00. Talked to BJ and meet at tower to check pad mount for damage, checked converter for faults and found Q10 was tripped. Reset Q10 and reset and started turbine. Will take triggers at a later date to determan root cause of fault, had to attend to other down turbines from the lightning storm. | KRAYN-WKO-NDX-20120526 | 1
KRAYN-WKO-NDX-20120527-01 | FM4 / WTG Maintenance | 2012-05-27 | 2012-05-28 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 1 | Forced |  |  | 15.0667 | Highland 1 | Could not respond do to lighting until early morning. Went there directly after another turbine and climbed tower to find 104f3 tripped. Reset breaker and rotor brake would not release. Cycled power to the inter bus an rotor brake released and operated normally. Climbed down and started turbine. | KRAYN-WKO-NDX-20120527 | 1
KRAYN-WKO-NDX-20120527-02 | FM866 / Air Temp CtrlCab H Stop | 2012-05-27 | 2012-05-27 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.65 | Highland 1 | Approached down turbine and acsended tower. Checked cooling unit breakers and were on. Checked both AC units and found both units needed to be reset. Let units cool off and reset, decsended tower. Reset and started turbine. Drove back to shop and monitionred temp on NC2. | KRAYN-WKO-NDX-20120527 | 1
KRAYN-WKO-NDX-20120527-03 | FM420 / Yaw HydBrk not open | 2012-05-27 | 2012-05-28 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 14.3167 | Highland 1 | Could not get to turbine after it faulting do to a major lighting storm until early in the mornig. Traveled to site and climbed tower. Removed valve on hyd station and found a teflon back up ring misaligned. Installed the ring properly and installed the valve. Reset the turbine and yawed. No other defects noted. Climbed down tower and started the turbine. | KRAYN-WKO-NDX-20120527 | 1
KRAYN-WKO-NDX-20120529-01 | FM6 / WTG Manual Stop | 2012-05-29 | 2012-05-29 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 5.75 | Planned | KRAYN-NDX-PRT-0716 | 0.25 | 4.25 | Highland 1 | Nordex technicians performed various checks for type III maintenance. | KRAYN-WKO-NDX-20120529 | 1
KRAYN-WKO-NDX-20120530-01 | No work order description provided by contractor | 2012-05-30 | 2012-05-30 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 12.25 | Forced | KRAYN-NDX-PRT-0029 | 10 L | 10.6 | Highland 1 | Yaw sliding retro with Renew as per Everpower request. | KRAYN-WKO-NDX-20120530 | 1
KRAYN-WKO-NDX-20120530-02 | FM6 / WTG Manual Stop | 2012-05-30 | 2012-05-30 | KRAYN-WTG18 | Preventive Maintenance | Nordex USA OandM | 17.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0979,KRAYN-NDX-PRT-0350,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0963,KRAYN-NDX-PRT-0963 | 8,1gram,1,15,4,2 | 9.6833 | Highland 1 | Completed type III maintenance stages 1 and 2. Also completed overspeed test for stage 3. | KRAYN-WKO-NDX-20120530 | 1
KRAYN-WKO-NDX-20120530-03 | FM6 / WTG Manual Stop | 2012-05-30 | 2012-05-30 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 9.6833 | Highland 1 | Exchanged fire extinguishers. | KRAYN-WKO-NDX-20120530 | 1
KRAYN-WKO-NDX-20120531-01 | No work order description provided by contractor | 2012-05-31 | 2012-05-31 | KRAYN-WTG03 | Corrective Maintenance | Nordex USA OandM | 11 | Forced | KRAYN-NDX-PRT-0029 | 10 L | 7.5 | Highland 1 | Yaw sliding retro with Renew as per Everpower request. | KRAYN-WKO-NDX-20120531 | 1
KRAYN-WKO-NDX-20120531-02 | FM6 / WTG Manual Stop | 2012-05-31 | 2012-05-31 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 7.6 | Highland 1 | Moved the fire extinguisher from down tower to up tower since it was already inspected. Then moved the up tower unit to the base where it can be easily inspected later. | KRAYN-WKO-NDX-20120531 | 1
KRAYN-WKO-NDX-20120531-03 | FM6 / WTG Manual Stop | 2012-05-31 | 2012-05-31 | KRAYN-WTG13 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062 | 16,6 | 7.5158 | Highland 1 | Arrived at turbine wtg 13. Ascended turbine. Completed stage 1 and 3 maintenance. Descended turbine. | KRAYN-WKO-NDX-20120531 | 1
KRAYN-WKO-NDX-20120531-04 | FM6 / WTG Manual Stop | 2012-05-31 | 2012-05-31 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 9.7333 | Highland 1 | Exchanged Fire Extinguishers. | KRAYN-WKO-NDX-20120531 | 1
KRAYN-WKO-NDX-20120531-05 | Wind turbine manual stop | 2012-05-31 | 2012-05-31 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 1 | Planned | KRAYN-NDX-PRT-0449 | 1 | 9.7333 | Highland 1 | Nordex technician changed the top box cooler, right hand side of cabinet. A/C not in SAP inventory. | KRAYN-WKO-NDX-20120531 | 1
KRAYN-WKO-NDX-20120601-01 | safety chain | 2012-06-01 | 2012-06-01 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.9 | Highland 1 | Arrived at turbine in response to a safety chain fault. Fast logs taken by Jennings Lynch indicated a pepper&fuchs issue. This was reset via 34F2 and 34F3. All faults cleared and turbine restarted without incident. | KRAYN-WKO-NDX-20120601 | 1
KRAYN-WKO-NDX-20120601-02 | safety chain | 2012-06-01 | 2012-06-01 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.9 | Highland 1 | Arrived at turbine in response to a safety chain fault. Fast logs taken by Jennings Lynch indicated a pepper&fuchs issue. This was reset via 34F2 and 34F3. All faults cleared and turbine restarted without incident. | KRAYN-WKO-NDX-20120601 | 1
KRAYN-WKO-NDX-20120603-01 | FM700 / IBS Interbus Stop | 2012-06-03 | 2012-06-03 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 4.75 | Forced | KRAYN-NDX-PRT-0725 | 1 | 3.9333 | Highland 1 | Remotely reset turbine, turbine repeated problem, called Willie and met at shop, proceeded to turbine with parts because of suspect slipring failure, assended turbine and preceeded to change out slipring. Double checked cabinet covers and work, buttoned up hub and decended tower. Started and drove to shop. | KRAYN-WKO-NDX-20120603 | 1
KRAYN-WKO-NDX-20120604-01 | FM1167 / Pitch2 battery defect | 2012-06-04 | 2012-06-05 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 4.25 | Forced | KRAYN-NDX-PRT-0138 | 2 | 3.95 | Highland 1 | Approached down turbine and tried reseting the hub. That failed and acsended tower. Entered the hub and began troubleshooting pitch two batteries.Found two batteries with low voltage, ( one in upper back rack and one in the middle back rack.) Replaced batteries and checked the turbine to pass its pitch test. Once pass we decsended tower reset and started turbine. | KRAYN-WKO-NDX-20120604 | 1
KRAYN-WKO-NDX-20120604-02 | No work order description provided by contractor | 2012-06-04 | 2012-06-04 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 11 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0009,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0292,KRAYN-NDX-PRT-0681 | 7,10,1,3 kg,1 l,8 | 8.2667 | Highland 1 | Maintenance 3 stage 1,2 | KRAYN-WKO-NDX-20120604 | 1
KRAYN-WKO-NDX-20120604-03 | No work order description provided by contractor | 2012-06-04 | 2012-06-04 | KRAYN-WTG19 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 8.2667 | Highland 1 | Install 75% yaw torque parameter per engineering request. | KRAYN-WKO-NDX-20120604 | 1
KRAYN-WKO-NDX-20120605-01 | No work order description provided by contractor | 2012-06-05 | 2012-06-05 | KRAYN-WTG19 | Preventive Maintenance | Nordex USA OandM | 9.5 | Planned |  |  | 4.6 | Highland 1 | Arrived at tower. Stopped tower. Ascended tower. Began to perform a function test on wtg 19. Desended tower. Started tower. | KRAYN-WKO-NDX-20120605 | 1
KRAYN-WKO-NDX-20120605-02 | FM6 / WTG Manual Stop | 2012-06-05 | 2012-06-05 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 9.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0322,KRAYN-NDX-PRT-0058 | 8,8,1,3 kg | 7.25 | Highland 1 | Maintenance 3 stage 1,2 | KRAYN-WKO-NDX-20120605 | 1
KRAYN-WKO-NDX-20120606-01 | FM6 / WTG Manual Stop | 2012-06-06 | 2012-06-06 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 10.3 | Highland 1 | Nordex technicians installed grounding wire from FAA light to nacelle | KRAYN-WKO-NDX-20120606 | 1
KRAYN-WKO-NDX-20120606-02 | manual stop | 2012-06-06 | 2012-06-06 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 12.25 | Planned | KRAYN-NDX-PRT-0364,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0979 | 3.2,8,1 gram | 10.3 | Highland 1 | Maint. 3 | KRAYN-WKO-NDX-20120606 | 1
KRAYN-WKO-NDX-20120606-03 | manual stop | 2012-06-06 | 2012-06-06 | KRAYN-WTG21 | Retrofit | Nordex USA OandM | 3.25 | Forced |  |  | 10.3 | Highland 1 | Installed repaired shaft covers. | KRAYN-WKO-NDX-20120606 | 1
KRAYN-WKO-NDX-20120607-01 | manual stop | 2012-06-07 | 2012-06-07 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 6 | Planned |  |  | 3.4167 | Highland 1 | Arrived at turbine and proceeded to perform "Safety Test of the Safety Devices" Also completed gearbox inspection. | KRAYN-WKO-NDX-20120607 | 1
KRAYN-WKO-NDX-20120607-02 | FM6 / WTG Manual Stop | 2012-06-07 | 2012-06-07 | KRAYN-WTG20 | Preventive Maintenance | Nordex USA OandM | 4 | Planned |  |  | 4.25 | Highland 1 | Type III functions test completed. | KRAYN-WKO-NDX-20120607 | 1
KRAYN-WKO-NDX-20120607-03 | FM6 / WTG Manual Stop | 2012-06-07 | 2012-06-07 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 5.75 | Planned |  |  | 3.5333 | Highland 1 | Maintenance 3 stage 3 | KRAYN-WKO-NDX-20120607 | 1
KRAYN-WKO-NDX-20120610-01 | FM866 / Air Temp CtrlCab H Stop | 2012-06-10 | 2012-06-10 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 3.7333 | Highland 1 | Arrived at turbine, proceeded up tower to find that the AC breakers were left off. Let cabinet air out, turned on AC let cool down till reset and decinded turbine, started and left. | KRAYN-WKO-NDX-20120610 | 1
KRAYN-WKO-NDX-20120611-01 | Wind turbine manual stop | 2012-06-11 | 2012-06-11 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 8.25 | Highland 1 | Nordex technicians applied a grounding wire to FAA light. Grounding wire was scrap. 2 circle terminals applied. | KRAYN-WKO-NDX-20120611 | 1
KRAYN-WKO-NDX-20120611-02 | Wind turbine manual stop | 2012-06-11 | 2012-06-11 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.25 | Highland 1 | Made sure that the inspected fire ext wasup tower and the non inspected was down tower and ready to receive its inspection. | KRAYN-WKO-NDX-20120611 | 1
KRAYN-WKO-NDX-20120611-03 | Wind turbine manual stop | 2012-06-11 | 2012-06-11 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 8.75 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0058,KRAYN-NDX-PRT-0322 | 8,3,1 | 8.25 | Highland 1 | Completed maintenance type III stages 1 and 2. | KRAYN-WKO-NDX-20120611 | 1
KRAYN-WKO-NDX-20120611-04 | Wind turbine manual stop | 2012-06-11 | 2012-06-11 | KRAYN-WTG14 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 8.25 | Highland 1 | Nordex technicians changed yaw parameters to 75% torque on the ABB VFD. | KRAYN-WKO-NDX-20120611 | 1
KRAYN-WKO-NDX-20120611-05 | FM6 / WTG Manual Stop | 2012-06-11 | 2012-06-11 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 9 | Planned |  |  | 7.3833 | Highland 1 | Arrived at turbine, proceeded up tower to perform type 3 stage 3 function tests. and decinded turbine, started and left.After climbing and swinging out hoist it was discovered that it was inoperable. Lowered tag line and lifted up computer bag with that. Proceeded to fix loose wire in chain hoist. Then with function tests. Decended turbine and started. Went over to 14 unloaded two loads and continued to shop. | KRAYN-WKO-NDX-20120611 | 1
KRAYN-WKO-NDX-20120612-01 | manual stop | 2012-06-12 | 2012-06-13 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 2.5333 | Highland 1 | Arrived at turbine in response to FM 50. Manually reset the MFR and the LV switch. All faults cleared and the turbine restarted without incident. | KRAYN-WKO-NDX-20120612 | 1
KRAYN-WKO-NDX-20120612-02 | FM1208 / MI class B Fault | 2012-06-12 | 2012-06-12 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 0.66667 | Highland 1 | Arrived at turbine, proceeded to pull triggers for our master tech. He called back and said that it was a pickup fault and needed to clean the encoder to see if that helped. Went back to shop picked up materials. Proceeded back to site to wtg18 and acended tower. removed encoder and cleaned thourghly with rag and blew out with a can of compressed air. Due to low winds unable to start turbine to test, left turbine in unfaulted state. Should start, if faoult again will need to replace the encoder. | KRAYN-WKO-NDX-20120612 | 1
KRAYN-WKO-NDX-20120612-03 | FM6 / WTG Manual Stop | 2012-06-12 | 2012-06-12 | KRAYN-WTG02 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 0.46667 | Highland 1 | True North WTG2 | KRAYN-WKO-NDX-20120612 | 1
KRAYN-WKO-NDX-20120613-01 | manual stop | 2012-06-13 | 2012-06-13 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 20.75 | Planned |  |  | 9.8167 | Highland 1 | Type 3, Satge 3 and various stage 2 | KRAYN-WKO-NDX-20120613 | 1
KRAYN-WKO-NDX-20120613-02 | FM100 / GenRot RpmSensor CollFault | 2012-06-13 | 2012-06-14 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 1.05 | Highland 1 | Arrived at turbine in response to Fm 100. Reset interbus from downtower via breakers 34F3, 34F4. | KRAYN-WKO-NDX-20120613 | 1
KRAYN-WKO-NDX-20120613-03 | manual stop | 2012-06-13 | 2012-06-13 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0322 | 7,8,1 | 10.35 | Highland 1 | Maint. 3, stages 1 and 2 | KRAYN-WKO-NDX-20120613 | 1
KRAYN-WKO-NDX-20120613-04 | FM6 / WTG Manual Stop | 2012-06-13 | 2012-06-13 | KRAYN-WTG15 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 10.35 | Highland 1 | Fire Extinguisher | KRAYN-WKO-NDX-20120613 | 1
KRAYN-WKO-NDX-20120613-05 | FM6 / WTG Manual Stop | 2012-06-13 | 2012-06-13 | KRAYN-WTG15 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 10.35 | Highland 1 | Shaft Covers | KRAYN-WKO-NDX-20120613 | 1
KRAYN-WKO-NDX-20120614-01 | Manual Stop | 2012-06-14 | 2012-06-14 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 3.05 | Highland 1 | Did they yaw cam switch test for the stage 3 part of the type to maint. This involves the tubine going clockwise and counter clockwise 990 degrees. | KRAYN-WKO-NDX-20120614 | 1
KRAYN-WKO-NDX-20120614-02 | FM50 / SafetyChain Activated | 2012-06-14 | 2012-06-14 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 20.1667 | Highland 1 | Installed ground to FAA light base. Per nordex engineering. | KRAYN-WKO-NDX-20120614 | 1
KRAYN-WKO-NDX-20120614-03 | FM50 / SafetyChain Activated | 2012-06-14 | 2012-06-14 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 20.1667 | Highland 1 | Swapped the fire ext. from up tower to down tower. | KRAYN-WKO-NDX-20120614 | 1
KRAYN-WKO-NDX-20120614-04 | manual stop | 2012-06-14 | 2012-06-14 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 12 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0009,KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0682 | 7,8,1,12,2 | 20.1667 | Highland 1 | Maint. 3, stages 1 and 2 | KRAYN-WKO-NDX-20120614 | 1
KRAYN-WKO-NDX-20120615-01 | FM6 / WTG Manual Stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG02 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.1167 | Highland 1 | Accended tower adjusted yaw pressure to 70. Yawed turbine untill sound subsided. Everpower showed up to confirm. Turbine just made a little noise in some areas. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-02 | manual stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 11.5 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0322 | 9,8,1 | 8.7833 | Highland 1 | Maint. 3, stages 1 and part of 2 | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-03 | manual stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG10 | Retrofit | Nordex USA OandM | 0.5 | Forced |  |  | 8.7833 | Highland 1 | Jib Crane snap hook was replaced. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-04 | Wind turbine manual stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 0.25 | Forced |  |  | 8.8 | Highland 1 | Nordex Technician replaced broken hardware on Taucha Krane StarLift Kit. Travel time on maintenance Service Report. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-05 | Wind turbine manual stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.8 | Highland 1 | Nordex Technician installed 75% torque parameters on ABB yaw VFD. Travel time on maintenance Service Report. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-06 | FM120 / Gen CWPress L Stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 12.5 | Highland 1 | Accended tower found sensor wire on coolant station pulled out. Crimped connector to attach better. Decended tower. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120615-07 | manual stop | 2012-06-15 | 2012-06-15 | KRAYN-WTG10 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 8.7833 | Highland 1 | Fire extinguisher swap. | KRAYN-WKO-NDX-20120615 | 1
KRAYN-WKO-NDX-20120616-01 | No work order description provided by contractor | 2012-06-16 | 2012-06-16 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 6.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 7.4 | Highland 1 |  | KRAYN-WKO-NDX-20120616 | 1
KRAYN-WKO-NDX-20120618-01 | FM55 / GenRot RpmMonitor Stop | 2012-06-18 | 2012-06-18 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 10.0833 | Highland 1 | Approached down turbine and fast logged faulted turbine. Found rotor side speed difference, reset from down tower and reset and started turbine. Trended gen and rotor speed sensors for 15 min and saw nothing out of the ordinary. Left turbine for a maintenance. | KRAYN-WKO-NDX-20120618 | 1
KRAYN-WKO-NDX-20120618-02 | manual stop | 2012-06-18 | 2012-06-18 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 6.3167 | Highland 1 | Fire Extinguishers were swapped. | KRAYN-WKO-NDX-20120618 | 1
KRAYN-WKO-NDX-20120618-03 | manual stop | 2012-06-18 | 2012-06-18 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 9.25 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062 | 2,6 | 6.3167 | Highland 1 | Maint. 3, stages 1 and part of 2. | KRAYN-WKO-NDX-20120618 | 1
KRAYN-WKO-NDX-20120618-04 | FM55 / GenRot RpmMonitor Stop | 2012-06-18 | 2012-06-18 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced |  |  | 6.4333 | Highland 1 | Installed grounding wire on the FAA light per Sean Illigs request for the static discharge during a lightning storm. | KRAYN-WKO-NDX-20120618 | 1
KRAYN-WKO-NDX-20120618-05 | FM55 / GenRot RpmMonitor Stop | 2012-06-18 | 2012-06-18 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 7 | Planned | KRAYN-NDX-PRT-0058 | 3 kg | 6.4333 | Highland 1 | Maintence 3 stage 2 and 3. ( every thing for stage 2 but the tower and the yaw) | KRAYN-WKO-NDX-20120618 | 1
KRAYN-WKO-NDX-20120619-01 | No work order description provided by contractor | 2012-06-19 |  | KRAYN-WTG | Corrective Maintenance | Nordex USA OandM | 6 | Forced |  |  | 24.25 | Highland 1 | Approached each turbine and opened louvers for summer fresh air and removed all 25 fire extinguishers. | KRAYN-WKO-NDX-20120619 | 1
KRAYN-WKO-NDX-20120620-01 | manual stop | 2012-06-20 | 2012-06-20 | KRAYN-WTG16 | Preventive Maintenance | Nordex USA OandM | 10 | Planned | KRAYN-NDX-PRT-0960,KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0322 | 6,8,1 | 7 | Highland 1 | Maint. 3, stages 1 and part of 2 | KRAYN-WKO-NDX-20120620 | 1
KRAYN-WKO-NDX-20120620-02 | FM6 / WTG Manual Stop | 2012-06-20 | 2012-06-20 | KRAYN-WTG16 | Retrofit | Nordex USA OandM | 1.5 | Forced |  |  | 7.0833 | Highland 1 | Shaft Covers | KRAYN-WKO-NDX-20120620 | 1
KRAYN-WKO-NDX-20120620-03 | FM6 / WTG Manual Stop | 2012-06-20 | 2012-06-20 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.9167 | Highland 1 | Installed ground on base of FAA light to machine frame ground per nordex engineering. | KRAYN-WKO-NDX-20120620 | 1
KRAYN-WKO-NDX-20120620-04 | FM6 / WTG Manual Stop | 2012-06-20 | 2012-06-20 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 0.5 | Planned |  |  | 5.9167 | Highland 1 | Swapped fire ext. from down to up tower. | KRAYN-WKO-NDX-20120620 | 1
KRAYN-WKO-NDX-20120620-05 | manual stop | 2012-06-20 | 2012-06-20 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 18 | Planned | KRAYN-NDX-PRT-0681,KRAYN-NDX-PRT-0978,KRAYN-NDX-PRT-0058 | 5,2,3 | 5.9167 | Highland 1 | Type 3, Satge 3 and various stage 2 | KRAYN-WKO-NDX-20120620 | 1
KRAYN-WKO-NDX-20120621-01 | No work order description provided by contractor | 2012-06-21 | 2012-06-21 | KRAYN-WTG12 | Preventive Maintenance | Nordex USA OandM | 12.5 | Planned | KRAYN-NDX-PRT-0090 | 2 | 7.35 | Highland 1 | Performed cleaning, tower torquing and function tests. | KRAYN-WKO-NDX-20120621 | 1
KRAYN-WKO-NDX-20120621-02 | FM6 / WTG Manual Stop | 2012-06-21 | 2012-06-21 | KRAYN-WTG17 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 7.0333 | Highland 1 | Applied all shaft covers to rotor and high speed shaft. | KRAYN-WKO-NDX-20120621 | 1
KRAYN-WKO-NDX-20120621-03 | FM6 / WTG Manual Stop | 2012-06-21 | 2012-06-21 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 7.0333 | Highland 1 | Applied all shaft covers to rotor and high speed shaft. | KRAYN-WKO-NDX-20120621 | 1
KRAYN-WKO-NDX-20120621-04 | FM6 / WTG Manual Stop | 2012-06-21 | 2012-06-21 | KRAYN-WTG17 | Preventive Maintenance | Nordex USA OandM | 15 | Planned | KRAYN-NDX-PRT-0062,KRAYN-NDX-PRT-0960 | 8,17 | 7.0333 | Highland 1 | Completed type III maintenance stages 1; as well as the Yaw and tower torque of stage 2. | KRAYN-WKO-NDX-20120621 | 1
KRAYN-WKO-NDX-20120621-05 | Manual stop | 2012-06-21 | 2012-06-21 | KRAYN-WTG25 | Preventive Maintenance | Nordex USA OandM | 3.25 | Planned |  |  | 1.4333 | Highland 1 | Performed the function run up tes of the type 3 Maint. | KRAYN-WKO-NDX-20120621 | 1
KRAYN-WKO-NDX-20120622-01 | No work order description provided by contractor | 2012-06-22 |  | KRAYN-WTG | Preventive Maintenance | Nordex USA OandM | 2 | Planned |  |  | 24.25 | Highland 1 | Nordex techs drove to site to replace the downtower fire extinguishers. No turbines were shut down. | KRAYN-WKO-NDX-20120622 | 1
KRAYN-WKO-NDX-20120625-01 | FM750 / IBS Pitch CommFlt | 2012-06-25 | 2012-06-25 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced |  |  | 14.75 | Highland 1 | Turbine down for pitch faults. Discovered broken blade bolt (Blade 1 position 30) had damaged pitch communication plug. Technicians made minor repairs to existing parts / equipment. No material was used. Machine running without further difficulty. Will continue to monitor. | KRAYN-WKO-NDX-20120625 | 1
KRAYN-WKO-NDX-20120626-01 | FM1205 / MI Griderror | 2012-06-26 | 2012-06-26 | KRAYN-WTG04 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 11.6333 | Highland 1 | Approached down turbine and checked NC2 and found grid error event, checked converter and had to reset IGBT overload line side. Reset turbine, started and monitior turbine. Took triggers but SUR had to be reformated and could not retrieve triggers. Turbine connected on small contactor and at 9:15 connected on big contactor. | KRAYN-WKO-NDX-20120626 | 1
KRAYN-WKO-NDX-20120628-01 | FM750 / IBS Pitch CommFlt | 2012-06-28 | 2012-06-28 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 6 | Forced | KRAYN-NDX-PRT-0725 | 1 | 6 | Highland 1 | Nordex technicians responded to an FM 750. Replaced a slip ring. This SR installation produced pitch emergency run active alarm. Called Geistown to bring another SR. Installed it. This one worked. | KRAYN-WKO-NDX-20120628 | 1
KRAYN-WKO-NDX-20120628-02 | FM262 / RotBrk HoldPressure Fault | 2012-06-28 | 2012-06-28 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 2.8333 | Forced |  |  | 1.8333 | Highland 1 | Nordex Technicians ascended tower, checked accumulators. Discovered 70 bar accumulator had 30 bar of pressure and 13 bar accumulator was empty. Accumulators charged and monitored. In event of further FM 262, technicians will change out the 70 and 13 Bar accumulators. Will continue to monitor. | KRAYN-WKO-NDX-20120628 | 1
KRAYN-WKO-NDX-20120630-01 | FM700 / IBS Interbus Stop | 2012-06-30 | 2012-06-30 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 5.5 | Forced | KRAYN-NDX-PRT-0725 | 1 | 20.9833 | Highland 1 | Drove to turbine, droped off chris, once materials were up tower drove to wtg 07, chris performed slip ring swap. Decended tower and drove to shop. | KRAYN-WKO-NDX-20120630 | 1
KRAYN-WKO-NDX-20120630-02 | FM50 / SafetyChain Activated | 2012-06-30 | 2012-06-30 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 11.05 | Highland 1 | Dropped off Chris to wtg 6 while I proceeded to wtg 07 to reset and pull triggers from FM50, waiting on report from master tech on cause of disturbance. | KRAYN-WKO-NDX-20120630 | 1
KRAYN-WKO-NDX-20120703-01 | FM6 / WTG Manual Stop | 2012-07-03 | 2012-07-03 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.7167 | Highland 1 | Gen Inspection. | KRAYN-WKO-NDX-20120703 | 1
KRAYN-WKO-NDX-20120706-01 | FM414 / Yaw MotBrake not open | 2012-07-06 | 2012-07-06 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 3 | Forced |  |  | 3.1667 | Highland 1 | 112 K2 wire 18 was discovered loose after responding to an FM 414. This was ammended and all faults cleared. | KRAYN-WKO-NDX-20120706 | 1
KRAYN-WKO-NDX-20120706-02 | FM6 / WTG Manual Stop | 2012-07-06 | 2012-07-06 | KRAYN-WTG22 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 68.65 | Highland 1 | We arrived in order to clear an FM 1208 MI Class B and reset the LV Switch. The switch was not reseting and it was deduced that the turbine must have been struck by lightning while it was offline. The suppression diode at position 33 on X8 was confirmed to be bad and was replaced. The LV switch reset and all faults cleared. Suppression diode replaced by Everpower. | KRAYN-WKO-NDX-20120706 | 1
KRAYN-WKO-NDX-20120710-02 | FM6 / WTG Manual Stop | 2012-07-10 | 2012-07-10 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 9 | Forced |  |  | 6.35 | Highland 1 | Arrived at WTG 08. Stopped turbine and prepped parts and tools to be lifted up tower. Applied LOTO on the Q10P. Ascended the turbine. Removed the panels off of the slip ring cover on the back of the generator. Pulled the vent housing and tube off of the Rear of the generator. Removed the carbon brushes from the slip ring. Unbolted the leads from the back of the slip ring. Mounted a puller to remove the slip ring. With a torch heated the grounding ring to get it to loosen up from the shaft. Once the grounding ring is removed the rotor shaft on the generator we then cleaned. With a bearing heater we heated the new grounding ring and placed it on the shaft. Slid the slip ring back on to the shaft. Replaced the vent ducting back on the rear of the generator. Installed the carbon brushes. Put the panels back on the slip ring cover. Pack up tools and old parts and sent them down tower. Descended tower. Calibrated generator encoder. Started turbine. | KRAYN-WKO-NDX-20120710 | 1
KRAYN-WKO-NDX-20120710-09 | FM6 / WTG Manual Stop | 2012-07-10 | 2012-07-10 | KRAYN-WTG08 | Retrofit | Nordex USA OandM | 9 | Forced |  |  | 6.35 | Highland 1 | Arrived at WTG 08. Stopped turbine and prepped parts and tools to be lifted up tower. Applied LOTO on the Q10P. Ascended the turbine. Removed the panels off of the slip ring cover on the back of the generator. Pulled the vent housing and tube off of the Rear of the generator. Removed the carbon brushes from the slip ring. Unbolted the leads from the back of the slip ring. Mounted a puller to remove the slip ring. With a torch heated the grounding ring to get it to loosen up from the shaft. Once the grounding ring is removed the rotor shaft on the generator we then cleaned. With a bearing heater we heated the new grounding ring and placed it on the shaft. Slid the slip ring back on to the shaft. Replaced the vent ducting back on the rear of the generator. Installed the carbon brushes. Put the panels back on the slip ring cover. Pack up tools and old parts and sent them down tower. Descended tower. Calibrated generator encoder. Started turbine. | KRAYN-WKO-NDX-20120710 | 1
KRAYN-WKO-NDX-20120711-01 | FM6 / WTG Manual Stop | 2012-07-11 | 2012-07-11 | KRAYN-WTG09 | Retrofit | Nordex USA OandM | 20.75 | Forced |  |  | 8.8333 | Highland 1 | Arrived at WTG 09. Stopped turbine and prepped parts and tools to be lifted up tower. Applied LOTO on the Q10P. Ascended the turbine. Removed the panels off of the slip ring cover on the back of the generator. Pulled the vent housing and tube off of the Rear of the generator. Removed the carbon brushes from the slip ring. Unbolted the leads from the back of the slip ring. Mounted a puller to remove the slip ring. With a torch heated the grounding ring to get it to loosen up from the shaft. Once the grounding ring is removed the rotor shaft on the generator we then cleaned. With a bearing heater we heated the new grounding ring and placed it on the shaft. Slid the slip ring back on to the shaft. Replaced the vent ducting back on the rear of the generator. Installed the carbon brushes. Put the panels back on the slip ring cover. Pack up tools and old parts and sent them down tower. Descended tower. Calibrated generator encoder. Started turbine. | KRAYN-WKO-NDX-20120711 | 1
KRAYN-WKO-NDX-20120711-02 | FM6 / WTG Manual Stop | 2012-07-11 | 2012-07-11 | KRAYN-WTG09 | General Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0959 | 2 | 8.8333 | Highland 1 | Entered hub with all tools and procedures nessesary for blade bolt extraction and replace in blade 3. While extracting bolt position 38 noticed that bolt position 36 was also broken. They both were broken in the same manner, broken off right at the washer. After extracting both bolts we proceded to flip bolts position 35,37,39. Exited hub and climbed down tower. After generator grounding ring replace we needed to rebalance the generator encoder. Rebalanced encoder, reset and started turbine. | KRAYN-WKO-NDX-20120711 | 1
KRAYN-WKO-NDX-20120711-03 | FM6 / WTG Manual Stop | 2012-07-11 | 2012-07-11 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 1.75 | Forced |  |  | 1.2333 | Highland 1 | Nordex technicians investigated why the Q10P circuit breaker was not functioning upon activation of an E-stop. | KRAYN-WKO-NDX-20120711 | 1
KRAYN-WKO-NDX-20120711-04 | FM6 / WTG Manual Stop | 2012-07-11 | 2012-07-11 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced | KRAYN-NDX-PRT-0172 | 1 | 0.91667 | Highland 1 | Nordex techncians investigated a customer complaint with the DMT vibration sensor. Sensor was replaced, wires relanded, reading on NCII was zeroed. FM 403 also investigated and corrected at this time. | KRAYN-WKO-NDX-20120711 | 1
KRAYN-WKO-NDX-20120712-01 | FM6 / WTG Manual Stop | 2012-07-12 | 2012-07-12 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 8.75 | Forced |  |  | 7.1667 | Highland 1 | Arrived at WTG 10. Stopped turbine and prepped parts and tools to be lifted up tower. Applied LOTO on the Q10P. Ascended the turbine. Removed the panels off of the slip ring cover on the back of the generator. Pulled the vent housing and tube off of the Rear of the generator. Removed the carbon brushes from the slip ring. Unbolted the leads from the back of the slip ring. Mounted a puller to remove the slip ring. With a torch heated the grounding ring to get it to loosen up from the shaft. Once the grounding ring is removed the rotor shaft on the generator we then cleaned. With a bearing heater we heated the new grounding ring and placed it on the shaft. Slid the slip ring back on to the shaft. Replaced the vent ducting back on the rear of the generator. Installed the carbon brushes. Put the panels back on the slip ring cover. Pack up tools and old parts and sent them down tower. Descended tower. Calibrated generator encoder. Started turbine. | KRAYN-WKO-NDX-20120712 | 1
KRAYN-WKO-NDX-20120712-02 | FM6 / WTG Manual Stop | 2012-07-12 | 2012-07-12 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 10.25 | Forced | KRAYN-NDX-PRT-0959 | 1 | 7.1667 | Highland 1 | Entered hub with all tool and procedures nessesary for blade bolt extraction and replace in blade 2. Drilled into bolt. Extracted remaining bolt end. Secured new bolt with Hytorc. Tightened bolts at position 36 and 38. Cleaned all tools and parts. Exited hub and climbed down tower. After generator grounding ring replace we needed to rebalance the generator encoder. Rebalanced encoder, reset and started turbine. | KRAYN-WKO-NDX-20120712 | 1
KRAYN-WKO-NDX-20120716-01 | FM419 / Yaw HydBrk not closed | 2012-07-16 | 2012-07-17 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.8333 | Highland 1 | Accended tower, 124K1 relay seemed to be sticking so we replaced 125K1 relay w/ retro relay, fault cleared. We then got an gearbox oil sample. Decended tower and turbine runs. | KRAYN-WKO-NDX-20120716 | 1
KRAYN-WKO-NDX-20120717-01 | FM6 / WTG Manual Stop | 2012-07-17 | 2012-07-17 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 11.5 | Forced | KRAYN-NDX-PRT-0959 | 1 | 9.35 | Highland 1 | After locking out the hub with blade 3 in the down position, the hub was entered and the broken bolt in blade 3 at position 33 was drilled and removed. A new bolt was installed and torqued to 357 bar. | KRAYN-WKO-NDX-20120717 | 1
KRAYN-WKO-NDX-20120717-02 | FM6 / WTG Manual Stop | 2012-07-17 | 2012-07-17 | KRAYN-WTG03 | Retrofit | Nordex USA OandM | 6.25 | Forced |  |  | 9.3333 | Highland 1 | Arrived at WTG 3. Stopped turbine and prepped parts and tools to be lifted up tower. Applied LOTO on the Q10P. Ascended the turbine. Removed the panels off of the slip ring cover on the back of the generator. Pulled the vent housing and tube off of the Rear of the generator. Removed the carbon brushes from the slip ring. Unbolted the leads from the back of the slip ring. Mounted a puller to remove the slip ring. With a torch heated the grounding ring to get it to loosen up from the shaft. Once the grounding ring is removed the rotor shaft on the generator we then cleaned. With a bearing heater we heated the new grounding ring and placed it on the shaft. Slid the slip ring back on to the shaft. Replaced the vent ducting back on the rear of the generator. Installed the carbon brushes. Put the panels back on the slip ring cover. Pack up tools and old parts and sent them down tower. Descended tower. Calibrated generator encoder. Started turbine. | KRAYN-WKO-NDX-20120717 | 1
KRAYN-WKO-NDX-20120718-01 | FM358 / LV UPSBatteryChange | 2012-07-18 | 2012-07-18 | KRAYN-WTG23 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0138 | 4 | 0.15 | Highland 1 | Turbine stopped, turned off UPS, and changed UPS battery tray. Fault cleared and turbine running. | KRAYN-WKO-NDX-20120718 | 1
KRAYN-WKO-NDX-20120718-02 | FM300 / LV MainSwitch OFF | 2012-07-18 | 2012-07-18 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 2 | Forced |  |  | 1.8 | Highland 1 | Arrived at turbine in response to FM 300 and 700. An attempt to reset the LV switch manually was unsuccessful. Exploration of the suppression diodes on X8 in the bottom box resulted in the discovery of a bad diode at position 33. This was replaced and the turbine reset and restarted without incident. Also, triggers were pulled and stored. | KRAYN-WKO-NDX-20120718 | 1
KRAYN-WKO-NDX-20120721-01 | FM700 / IBS Interbus Stop | 2012-07-21 | 2012-07-21 | KRAYN-WTG06 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 6.4 | Highland 1 | Arrived at turbine. Lifted slip ring and tools is basket. Ascend the tower and locked out rotor for hub entry. Entered hub with tools and slip ring. Proceeded to disassemble old slip ring and install new slip ring. Check the hub for tools, parts, and secured hub door. Went back out to the nacelle. Reset turbine mechanics to run state. Went down tower. Reset all faults. All faults cleared. Started turbine. | KRAYN-WKO-NDX-20120721 | 1
KRAYN-WKO-NDX-20120723-01 | No work order description provided by contractor | 2012-07-23 | 2012-07-23 | KRAYN-WTG01 | Preventive Maintenance | Nordex USA OandM | 3.5 | Planned |  |  | 1.4917 | Highland 1 | Arrived at WTG 01. Stopped Turbine. Ascended turbine with WTS to instruct them on the rigging of the scaffold and use of the turbine. Descended turbine. Started turbine. | KRAYN-WKO-NDX-20120723 | 1
KRAYN-WKO-NDX-20120724-01 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-24 |  | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 4 | Forced |  |  | 1.4917 | Highland 1 | Arrived at turbine. Ascended turbine. Started by disconnecting the lines from the gen. bearing ALU. We then forced it high to ensure that the ALU is pumping grease into Grease junction box. After we verified that the grease was flowing properly from the ALU. we then checked all fittings leading out of the junction box to the Drive end bearing and non-drive end bearing. We found that there was a dry piece of grease in one of the fittings, cleaned them out and reinstalled the fittings. We forced the ALU high to ensure that it wasn’t clogged any more. the grease was now flowing out of the fitting that run into the drive end bearing. Left the ALU forced high for approx. 20 mins. descended the turbine. started the turbine. both bearing temps were less than 65 degrees Celsius and within a hour it faulted out at 90 degrees Celsius.Consulted Jennings and Sean and they said it was best to leave the turbine down over night. | KRAYN-WKO-NDX-20120724 | 1
KRAYN-WKO-NDX-20120724-02 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-24 |  | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 3 | Forced |  |  | 1.4917 | Highland 1 | Recommissioned and balanced gen encoder after gen grounding ring installation. Wind was low so had to wait for the speed window to complete. | KRAYN-WKO-NDX-20120724 | 1
KRAYN-WKO-NDX-20120724-03 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-24 |  | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 1.4333 | Highland 1 | Stopped turbine from WTG 01 while troubleshooting same fault. Approached down turbine and started to troubleshoot Gen ALU. Checked all grease tubes, flow, grease junction box, and grease flow out the ends of the tubes to the bearing, and function of the ALU itself. All seemed in order so continued to check NC2 parameters and called Sean Illig for assistance because the bearing on WTG01 was heating up again. Changed parameters for gen Alu to run constance and started turbine. Once the turbine was running monitored temp of both bearings. Within 15 min the temp rose 10 degrees and the ALU was running. While turbine was running we heard and felt vibrations coming from the drive end of the Gen. Consulted Jennings and Sean we felt it was best to leave the turbine down till the morning for further troubleshooting. | KRAYN-WKO-NDX-20120724 | 1
KRAYN-WKO-NDX-20120725-01 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-25 | 2012-07-26 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 7 | Forced | KRAYN-NDX-PRT-0587 | 3 | 22.6333 | Highland 1 | Manually pumped kluberplex into zerk fittings in front and back of generator | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-02 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-25 | 2012-07-26 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 4.5 | Forced |  |  | 22.6333 | Highland 1 | Locked out Q10P, ascended tower. Hoisted tooling and grounding ring. Heated up grounding ring to 570 degrease for smooth installation. Disassembled gen encoder, gen slip ring shrouding, gen slip ring via slip ring cylinder extractor/retractor & enerpac and grounding ring w/ oxygen/cetaylne torch. Grounding ring slid on gen shaft smoothly due to pre heating. Re-assembled gen slip ring via slip ring cylinder extractor/retractor & enerpac. Continued to re-assemble slip ring shrouding and gen encoder. | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-03 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-25 | 2012-07-26 | KRAYN-WTG01 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 22.6333 | Highland 1 | Shaft Covers | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-04 | FM6 / WTG Manual Stop | 2012-07-25 | 2012-07-26 | KRAYN-WTG18 | Corrective Maintenance | Nordex USA OandM | 16 | Forced | KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0968,KRAYN-NDX-PRT-0969 | 1,1,1 | 13.5397 | Highland 1 | Entered hub with all tools and procedures necessary for blade bolt extraction and replace in blade 2 position 64. We had to remove the redundant encoder from the blade. We then Pitched the blade so we could access the broken bolt. Extracted the bolt and replaced it with a new one. We removed all unnecessary tooling and parts from the hub. We then began reinstalling the encoder. This was excessively complicated but, was eventually successful. | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-05 | FM6 / WTG Manual Stop | 2012-07-25 | 2012-07-26 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 9.2167 | Highland 1 | Went to turbine. Helped LMS with rigging and prepping turbine mechanically for blade repair. Assisted as work was being done. Once all work was completed for the day, sent all equipment down turbine. Reset turbine to start status up tower. Due to an adhesive that needed to set, the turbine was started remotely at a later time. | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-06 | FM0 / WTG System ok | 2012-07-25 |  | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 9.2167 | Highland 1 | Went to turbine to allow access for LMS blade repair crew. Once the crew arrived it was determined that the winds were too high (with a prospect of increasing) and an approaching storm would prevent any blade work from being done. Turbine was not shut down during the process. | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120725-07 | FM824 / Gen BearTemp (AS) H Stop | 2012-07-25 | 2012-07-25 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 12 | Forced | KRAYN-NDX-PRT-0587 | 3 | 24.25 | Highland 1 | Approached down turbine with Sean Illig to troubleshoot bearing temp. Force gen alu high and monitored gen bearings for grease to extrude from bearing to tell it was full. During that time we did run up the turbine to check bearing temp. Also we did a gen alignment and found it to be within tolerance. Once the bearing would not cool off we decided to send Jennings to Roth Rock for Kluberplex grease. Decended tower to help with WTG 18. Once we had the kluberpex Travis and I Ascended tower to grease drive end of the gen Per Sean iIlligs instructions. We greased the bearing until extruded from bearing and started turbine. Monitored bearing temp for 1/2 hr and documented results. Cleaned bearings and descended tower. Reset and started turbine. Monitored turbine bearing temp. | KRAYN-WKO-NDX-20120725 | 1
KRAYN-WKO-NDX-20120726-01 | FM50 / SafetyChain Activated | 2012-07-26 | 2012-07-26 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 3.2833 | Highland 1 | Approached down turbine and reset pepperl and fuchs modules from down tower and reset and started turbine. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120726-02 | FM710 / Gen CWTemp GenInlt CableCut | 2012-07-26 | 2012-07-26 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 8 | Forced |  |  | 7.8 | Highland 1 | Ascended tower, flipped breaker 102F1, checked fuse in 105A12 module and all fuses from 105A7-105A12. Switched 105A11 and w/ 105A12 to see if fault followed. Then found rotor break temperature PT100 was damaged due to dog bone chafing shielding. We then followed W707 to the gen cooling temp PT100 which was also had no continuity. We switched PT100 gen cooling temp w/ nacelle PT100 temporarily. Fault cleared turbine runs. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120726-03 | FM300 / LV MainSwitch OFF | 2012-07-26 | 2012-07-26 | KRAYN-WTG19 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0090 | 1 | 4.05 | Highland 1 | Arrived at tower to troubleshoot FM300. Replaced diode 33 at x8 terminal strip. Returned tower to service. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120726-04 | FM300 / LV MainSwitch OFF | 2012-07-26 | 2012-07-26 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 0.5 | Forced | KRAYN-NDX-PRT-0090 | 1 | 4.5667 | Highland 1 | Arrived at tower to troubleshoot FM300. Replaced diode 33 at x8 terminal strip. Returned tower to service. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120726-05 | FM6 / WTG Manual Stop | 2012-07-26 | 2012-07-26 | KRAYN-WTG24 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced | KRAYN-NDX-PRT-0587 | 3 | 3.0167 | Highland 1 | Went to turbine. Shut off Q10P. Went up turbine. Took off top high speed shaft cover on the generator side. Took of access covers for the generator slip ring. Checked for voltage. No voltage was present. Took of rotor break to allow pin wheeling. Greased both drive and non-drive side generator bearing. Reapplied covers and access panels. cleaned up all excess grease. Cleaned up tools. went down turbine. Reset Q10P. Restarted turbine. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120726-06 | FM614 / TimeSynchronisation failed(P26.04) | 2012-07-26 | 2012-07-26 | KRAYN-WTG25 | Corrective Maintenance | Nordex USA OandM | 5.25 | Forced | KRAYN-NDX-PRT-0090,KRAYN-NDX-PRT-0044 | 9,2 | 9.2833 | Highland 1 | Arrived at tower to troubleshoot FM614. Replaced diodes 1, 10, 32, 33, 34 at x8 terminal strip and diode 2 at x8.2 terminal strip. Had to return to shop and get button fuses for interbus, replaced and turned on breakers and new fuse failed. Found diodes at 41, 52, and 53 at x8.1 terminal strip had also failed. Replaced diodes and button fuse, reset alarms and returned tower to service. | KRAYN-WKO-NDX-20120726 | 1
KRAYN-WKO-NDX-20120727-01 | FM1208 / MI class B Fault | 2012-07-27 | 2012-07-27 | KRAYN-WTG07 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 14.55 | Highland 1 | Prepare new micro logics for Q10 and traveled to Everpower to get some one to open the pad mount transformer. After arriving on site we prepared the turbine for grid disconnect and waited on Everpower to show up. Once they arrived they opened the pad mount transformer's breaker. We entered the turbine and verified no voltage and R&R micro logics on the Q10. After completion of that we call Everpower back and waited for their arrival. Once there they closed the pad mounts breaker and energized the turbine. We then started the turbine and returned to the shop. | KRAYN-WKO-NDX-20120727 | 1
KRAYN-WKO-NDX-20120727-02 | FM6 / WTG Manual Stop | 2012-07-27 | 2012-07-27 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 10.75 | Forced |  |  | 8.8667 | Highland 1 | Went to turbine. Helped LMS with rigging and prepping turbine mechanically for blade repair. Assisted as work was being done. Once all work was completed for the day, sent all equipment down turbine. Reset turbine to start status up tower. Due to an adhesive that needed to set, the turbine was started remotely at a later time. | KRAYN-WKO-NDX-20120727 | 1
KRAYN-WKO-NDX-20120728-01 | FM6 / WTG Manual Stop | 2012-07-28 | 2012-07-28 | KRAYN-WTG21 | Warranty Repair | Nordex USA OandM | 9 | Forced |  |  | 7.8031 | Highland 1 | Assisted Rope Works with WTG 21. Rope Works recommended that we leave the turbine down for an additional 2 hours to let the glue fully cured. Monitored turbine untill 3:30 then started it. | KRAYN-WKO-NDX-20120728 | 1
KRAYN-WKO-NDX-20120730-01 | FM6 / WTG Manual Stop | 2012-07-30 | 2012-07-30 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0587 | 2 | 2.9667 | Highland 1 | Drove to site, went up tower and greased gen bearings. | KRAYN-WKO-NDX-20120730 | 1
KRAYN-WKO-NDX-20120730-02 | FM6 / WTG Manual Stop | 2012-07-30 | 2012-07-30 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 3.5 | Forced |  |  | 2.9667 | Highland 1 | Addressed multiple FM262s. Upon checking accumulator pressure on the hydac station 3 were found to be out of spec. The 110 bar accumulator was found to be at 170 bar, the 70 bar accumulator was found to be at 40 bar and the 13 bar accumulator was found to be at 22 bar. All were corrected. The turbine started without incident. | KRAYN-WKO-NDX-20120730 | 1
KRAYN-WKO-NDX-20120730-03 | FM6 / WTG Manual Stop | 2012-07-30 | 2012-07-30 | KRAYN-WTG14 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced |  |  | 2.9667 | Highland 1 | Arrived at turbine. We had to check suppression diodes for engineering. | KRAYN-WKO-NDX-20120730 | 1
KRAYN-WKO-NDX-20120730-04 | FM705 / RotBrk Temp CableCut | 2012-07-30 | 2012-07-30 | KRAYN-WTG17 | Retrofit | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0587 | 2 | 3.1833 | Highland 1 | Cleaned off generator bearing (both drive and non-drive side) of excess grease. Used automatic grease gun. Added one tube of Kluberplex to drive side of generator bearing and one tube to the non-drive side of the generator bearing. Applied the shaft covers to high speed shaft. Cleaned up all tools and materials. Sent everything down tower. Climbed down tower. started turbine. | KRAYN-WKO-NDX-20120730 | 1
KRAYN-WKO-NDX-20120730-05 | FM705 / RotBrk Temp CableCut | 2012-07-30 | 2012-07-30 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 3 | Forced | KRAYN-NDX-PRT-0540 | 1 | 3.1833 | Highland 1 | Went to turbine. Hoisted tools and materials up turbine. Took off both high speed shaft covers on the generator side and the bottom high speed shaft cover on the gearbox side. Took PT sensor off of the rotor break. Put new sensor on brake caliber. Continued working other issues. | KRAYN-WKO-NDX-20120730 | 1
KRAYN-WKO-NDX-20120731-01 | FM6 / WTG Manual Stop | 2012-07-31 | 2012-07-31 | KRAYN-WTG15 | Corrective Maintenance | Nordex USA OandM | 2.75 | Forced | KRAYN-NDX-PRT-0587 | 2 | 0.99361 | Highland 1 | Stopped turbine. Ascended turbine. Manually pumped kluberplex into the gen bearings to reduce running temp. Descended Turbine and started it. | KRAYN-WKO-NDX-20120731 | 1
KRAYN-WKO-NDX-20120731-02 | FM825 / Gen BearTemp (AS) H Warn | 2012-07-31 | 2012-07-31 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 1.25 | Forced |  |  | 1.5833 | Highland 1 | Drilled a hole into the broken bolt. Tapped in the easy out. extracted broken bolt. Applied new bolt. Cleaned up materials. Hoisted tools and materials down tower. Went down tower. Started turbine. | KRAYN-WKO-NDX-20120731 | 1
KRAYN-WKO-NDX-20120731-03 | FM825 / Gen BearTemp (AS) H Warn | 2012-07-31 | 2012-07-31 | KRAYN-WTG16 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0587 | 3 | 1.5833 | Highland 1 | went up tower. Cleaned off generator bearing (both drive and non-drive side) of excess grease. Used automatic grease gun. Added 1.5 tube of Kluberplex to drive side of generator bearing and 1.5 tube to the non-drive side of the generator bearing. Applied the shaft covers to high speed shaft. Attended to other issues. | KRAYN-WKO-NDX-20120731 | 1
KRAYN-WKO-NDX-20120731-04 | No work order description provided by contractor | 2012-07-31 |  | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 8 | Forced | KRAYN-NDX-PRT-0293 | 1 | 2.1167 | Highland 1 | Waited for the all clear for lightning. Went to turbine. Found the 33F1 breaker tripped. Proceeded to turn breaker back on. Once power was reapplied the UPS started to short and make noises from within its case. Went to turbine #1 for an extra UPS that has been stored there. Went back to turbine #20. Checked schematics and circuits for any overvoltage as to not damage the good UPS. All voltages looked good. Plugged in UPS and applied power. All power was restored. There was then a RFC error 10.0. Trouble shot the module for the RFC error. Reset the RFC and did a Hard reset on the turbine. No change in the error. 151A8 was associated with the error. Went back to the shop to retrieve the corresponding module. went back to the turbine. Installed new module. The error stayed consistent. Went up tower. Checked all breakers and fuses associated with the interbus. No faults were found physically in the interbus up tower. Came back down tower. Contacted Lead tech and Master technician. Logged onto Diag+. Disabled the 0.0 error on the interbus. 23.0 became red. Reset RFC. The 10.0 error reappeared. It was determined at this point that it may be a SEG error. The turbine was left down until SEG qualified technicians could assess the problem. | KRAYN-WKO-NDX-20120731 | 1
KRAYN-WKO-NDX-20120801-01 | FM1172 / Pitch PowerVolt. Fault | 2012-08-01 | 2012-08-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced | KRAYN-NDX-PRT-0587 | 3 | 20.0833 | Highland 1 | went up tower. Cleaned off generator bearing (both drive and non-drive side) of excess grease. Used automatic grease gun. Added 1.5 tube of Kluberplex to drive side of generator bearing and 1.5 tube to the non-drive side of the generator bearing. Cleaned up materials. Went back down tower. Loaded truck and left for fire extinguisher recovery at Highland North. | KRAYN-WKO-NDX-20120801 | 1
KRAYN-WKO-NDX-20120801-02 | No work order description provided by contractor | 2012-08-01 | 2012-08-01 | KRAYN-WTG20 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0634 | 1 | 19 | Highland 1 | Arrived at turbine in order to continue previous night's work.151A9 was swapped with a new module to no avail. The original module was put back in and the replacement was returned to inventory. Next, the HUR was swapped. This cleared the RFC faults and restored communication with NC2. All faults cleared via NC2. we are now waiting on wind in order to recommission the convertor and start the turbine. | KRAYN-WKO-NDX-20120801 | 1
KRAYN-WKO-NDX-20120801-03 | FM6 / WTG Manual Stop | 2012-08-01 | 2012-08-01 | KRAYN-WTG21 | Preventive Maintenance | Nordex USA OandM | 1.25 | Planned |  |  | 1.5667 | Highland 1 | Removed gearbox inspection plate, cut length of tubing and began pumping to extract oil sample from gear box. Secured inspection plate, put away hoist and buttoned up nacelle lid and descended turbine. | KRAYN-WKO-NDX-20120801 | 1
KRAYN-WKO-NDX-20120801-04 | FM6 / WTG Manual Stop | 2012-08-01 | 2012-08-01 | KRAYN-WTG21 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced | KRAYN-NDX-PRT-0587 | 3 | 1.5667 | Highland 1 | Drove to site, climbed up, greased gen bearings and wiped off excess grease. | KRAYN-WKO-NDX-20120801 | 1
KRAYN-WKO-NDX-20120802-01 | FM6 / WTG Manual Stop | 2012-08-02 | 2012-08-02 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0587 | 3 | 3.7167 | Highland 1 | Climbed up and pumped grease into gen bearings. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-02 | FM700 / IBS Interbus Stop | 2012-08-02 | 2012-08-02 | KRAYN-WTG09 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced |  |  | 3.7167 | Highland 1 | Locked out rotor, entered hub, cleaned slip ring, drove back to shop. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-03 | FM100 / GenRot RpmSensor CollFault | 2012-08-02 | 2012-08-02 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 4.5 | Forced | KRAYN-NDX-PRT-0568,KRAYN-NDX-PRT-0567,KRAYN-NDX-PRT-0569 | 1,1,1 | 4.6333 | Highland 1 | Arrived at turbine in response to FM 55 and 100. After programming the module while downtower the tower was ascended and the following modules were given replacements: 142A6, 142A7 and 142A9. After a test run the tower was deemed fixed and has been running ever since. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-04 | FM6 / WTG Manual Stop | 2012-08-02 | 2012-08-02 | KRAYN-WTG11 | Preventive Maintenance | Nordex USA OandM | 1.5 | Planned |  |  | 4.6333 | Highland 1 | Gearbox oil sample taken. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-05 | FM6 / WTG Manual Stop | 2012-08-02 | 2012-08-02 | KRAYN-WTG11 | Corrective Maintenance | Nordex USA OandM | 1 | Forced | KRAYN-NDX-PRT-0587 | 3 | 4.6333 | Highland 1 | Injected Kluberplex into generator bearing. 1.5 tubes in front and 1.5 tubes in back. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-06 | FM6 / WTG Manual Stop | 2012-08-02 | 2012-08-02 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 9.5 | Forced | KRAYN-NDX-PRT-0959,KRAYN-NDX-PRT-0968,KRAYN-NDX-PRT-0969 | 1,1,1 | 6.8167 | Highland 1 | Arrived at WTG 13. Stopped turbine. Ascended the turbine. We moved all of our tools and parts needed to extract a blade bolt into the hub. Removed and replaced 1 blade bolt and retorqued it. Removed all our tooling and defective parts. Descended turbine and started it. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120802-07 | FM744 / IBS Busquality Warning | 2012-08-02 | 2012-08-02 | KRAYN-WTG13 | Corrective Maintenance | Nordex USA OandM | 17.25 | Forced | KRAYN-NDX-PRT-0727 | 1 | 6.8167 | Highland 1 | Ascended tower, killed 102F2 102F3 and 400V to hub. De-terminated wire's in top box & Hub. Lubed and attached snake to De-terminated wires from top box and pulled slip ring cables through hub. Lubed, taped and attached snake to new slip ring cables and pulled through to nacelle, re-roughed and terminated wires in top box, decended tower, FM744 cleared and turbine run's. | KRAYN-WKO-NDX-20120802 | 1
KRAYN-WKO-NDX-20120803-01 | FM6 / WTG Manual Stop | 2012-08-03 | 2012-08-03 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 5 | Forced | KRAYN-NDX-PRT-0587 | 3 | 2.2131 | Highland 1 | Stopped turbine. Ascended turbine. Manually pumped kluberplex into the gen bearings to reduce running temp. Descended Turbine and started it. | KRAYN-WKO-NDX-20120803 | 1
KRAYN-WKO-NDX-20120803-02 | FM6 / WTG Manual Stop | 2012-08-03 | 2012-08-03 | KRAYN-WTG12 | Corrective Maintenance | Nordex USA OandM | 3.75 | Forced | KRAYN-NDX-PRT-0587 | 3 | 1.9167 | Highland 1 | drove to site, went up tower, greased gen bearing, climbed down and drove back to shop. | KRAYN-WKO-NDX-20120803 | 1
KRAYN-WKO-NDX-20120806-01 | FM866 / Air Temp CtrlCab H Stop | 2012-08-06 | 2012-08-06 | KRAYN-WTG10 | Corrective Maintenance | Nordex USA OandM | 2.25 | Forced |  |  | 3.5167 | Highland 1 | Approached down turbine and checked NC 2 for cabinet temp. Temp above 50. Ascended tower to check breakers. Found breakers not tripped so troubleshoot A/C units. Both units need to be reset. Reset units and let cabinet cool down below hystorisis to clear fault. Descended tower and reset and started turbine. | KRAYN-WKO-NDX-20120806 | 1
KRAYN-WKO-NDX-20120806-02 | FM1176 / Pitch1 DC/DC converter defect | 2012-08-06 | 2012-08-06 | KRAYN-WTG18 | Retrofit | Nordex USA OandM | 2 | Forced |  |  | 2.1167 | Highland 1 | Went to turbine. Pitched blades manually. Heard noise in hub. Stopped rotor. Went up tower. Pinned rotor out. Entered hub. Found broken blade bolt in blade #1 Pos #32. Retrieved bolt. Adjusted Pitch encoder #2. Cleared hub out. Unpinned hub. Reset faults. Came back down tower. Restarted faults. Drove to turbine #29. | KRAYN-WKO-NDX-20120806 | 1
KRAYN-WKO-NDX-20120813-01 | FM1127 / Pitch2 Batt.Voltage To Low | 2012-08-13 | 2012-08-14 | KRAYN-WTG05 | Corrective Maintenance | Nordex USA OandM | 4 | Forced | KRAYN-NDX-PRT-0138 | 1 | 5.4667 | Highland 1 | Looked at NC II logs remotely and found that it looked like a bad battery in the hub. Tested batteries in stock and took the best 4 we had. Traveled to turbine and climbed up. Lowered chain hoist and hoisted the parts and tools. Went out into the hub to find one very poor battery in pitch box 2. R&R battery and reset turbine. Allowed the turbine to pitch test with no defects noted at this time. One tech returned down tower and we lowered the tooling then secured the hoist. Final man climbed down and we started the turbine. | KRAYN-WKO-NDX-20120813 | 1
KRAYN-WKO-NDX-20121209-01 | No work order description provided by contractor | 2012-12-09 | 2011-12-09 | KRAYN-WTG01 | Corrective Maintenance | Nordex USA OandM | 1.5 | Forced |  |  | 0.41667 | Highland 1 |  | KRAYN-WKO-NDX-20121209 | 1
KRAYN-WKO-NDX-20140214-01 | FM6 / WTG Manual Stop | 2014-02-14 | 2012-02-14 | KRAYN-WTG17 | Corrective Maintenance | Nordex USA OandM | 2.5 | Forced | KRAYN-NDX-PRT-0302,KRAYN-NDX-PRT-0303 | 2,2 | 0.86667 | Highland 1 | After noticing the top cabinet bushings missing during other work days before we returned to the turbine with new bushings. Stopped the turbine and climbed to the nacelle. Installed both the fwd and aft bushing sets. Double checked the surrounding area and assured no damage from the loose cabinet. No defects noted at this time. Returned down tower and placed the turbine in run. | KRAYN-WKO-NDX-20140214 | 1
Note on A1: Kevin Wigell: Use date of WO in ID#.
Note on B1: Kevin Wigell: Use "Fault Description".
Note on C1: Kevin Wigell: Use "Date".
Note on D1: Kevin Wigell: Use "Start Date/Time (Return to Service)".
Note on E1: Kevin Wigell: Use "WTG". Must match an existing Asset ID in MPulse.
Note on F1: Kevin Wigell: Use "Job Type".
Note on H1: Kevin Wigell: Sum of Tech hours.
Note on I1: Kevin Wigell: To be based on Job Type.
Note on L1: Kevin Wigell: Use "Stoppage Time".
Note on N1: Kevin Wigell: Use "Work Performed".