## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Asset ID | Vendor ID | Actual Hours | Part ID | Part Quantity | Comments | Original ID
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0457 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0459 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0460 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0461 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0462 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0463 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0464 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-04 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 27.9667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 27.9667 | GAMSA-PRT-0465 | 3 |  | 401991109
PATTN-WKO-GAM-20150511-05 | GAM-ALARM 2106 TEMP MEASUREENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/11/2015 | 2.3 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4833 |  |  | 2000541: LOCAL RESET | 401991714
PATTN-WKO-GAM-20150511-06 | GAM-30 Month Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/11/2015 | 5/11/2015 | 5/12/2015 | 25.3333 | Patton | Planned |  | PMI-003 |  | VEN-165 | 25.3333 | GAMSA-PRT-0449 | 20 | 30 month maintance | 500716986
PATTN-WKO-GAM-20150512-04 | GAM- WARNING 404 HIGH GEARBOX TEMP | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 3.0333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.8667 | GAMSA-PRT-0459 | 2 | 2000541: FOUND TWO LOUVERS BURT UP | 401990439
PATTN-WKO-GAM-20150512-05 | GAM- WARNING 114 LOW YAW BRAKE PRESSURE | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 5.3333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 |  |  | 2000541: ADJUSTED THE PRESSURES | 401990443
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0451 | 1 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0452 | 4 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0453 | 4 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0381 | 1 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0454 | 6 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0455 | 6 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-06 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0456 | 2 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150513-02 | GAM-ALARM 403 HIG GEARBOX TEMP | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2015 | 5/13/2015 | 5/13/2015 | 7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.8333 | GAMSA-PRT-0458 | 1 | 2000541: FOUND THE GEARBOX FAN FAILED REPLACED IT | 401991588
PATTN-WKO-GAM-20150514-02 | GAM-30 Month Minor maint. Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2015 | 5/14/2015 | 5/14/2015 | 0 | Patton | Planned |  | PMI-003 |  | VEN-165 | 0 |  |  | GAM-30 Month Minor maint. Patton | 500833127
PATTN-WKO-GAM-20150615-02 | GAM-ALARM 2106 T-MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 6/15/2015 | 6/15/2015 | 6/15/2015 | 7.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.41667 |  |  | 2000541: LOCAL RESET | 402022836
PATTN-WKO-GAM-20150616-03 | REPLACED THE DECK SUPPORT RODS | Closed | Corrective Maintenance | Forced | 02-High | 6/16/2015 | 6/16/2015 | 6/16/2015 | 4.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 | GAMSA-PRT-0466 | 1 |  | 402024751
PATTN-WKO-GAM-20150616-04 | REPLACED THE DECK SUPPORT ROD | Closed | Corrective Maintenance | Forced | 02-High | 6/16/2015 | 6/16/2015 | 6/16/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 | GAMSA-PRT-0466 | 1 |  | 402024772
PATTN-WKO-GAM-20150618-02 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0451 | 1 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-02 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0453 | 4 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-02 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0381 | 1 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-02 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0454 | 6 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-02 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 1.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0455 | 6 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150621-02 | GAM-loal reset | Closed | Corrective Maintenance | Forced | 02-High | 6/21/2015 | 6/21/2015 | 6/21/2015 | 7.1 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.11667 |  |  | 2000541: local reset | 402029646
PATTN-WKO-GAM-20150622-02 | CHECKED THE SLIP RING FOR ARC MARKS | Closed | Corrective Maintenance | Forced | 02-High | 6/22/2015 | 6/22/2015 | 6/22/2015 | 3.3333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.6667 | GAMSA-PRT-0467 | 1 | 2000541: CHECKED THE SLIP RING FOR ARC MARKS | 402029810
HIGHNO-WKO-NDX-20150107-02 | Check In - NDX - 81854 - Troubleshooting | Closed |  |  |  | 1/7/2015 | 1/7/2015 | 1/7/2015 | 6.0167 | Highland North |  |  |  |  | VEN-304 | 7 | NORDX-PRT-0002 | 1 | After calling RMC and checking in put tower into manual stop nd disabled switch rights. tower was down on a fm 700 after getting up tower pinned the hub out and shut off all power to the hub off. shut breakers 102f2 and 102f3 and 101f1 and 300f1. Entered the hub and removed slip ring replaced with new one and made all conections. checked work and back to the nacel to clear tower after tower was clear unpinned the hub and let it pin wheel for 10 min and tower was good. went down tower and started turbine. tower is up and running | 700144684
KRAYN-WKO-NDX-20150106-02 | US-HIGHLAND-WEA80826 | Closed |  |  |  | 1/7/2015 | 1/6/2015 | 1/6/2015 | 1.5 | Highland 1 |  |  |  |  | VEN-304 | 4.25 | NORDX-PRT-0002 | 1 | After shutting tower down and putting into a manual stop went up tower to inspect fm172 breaker was tripped breaker did not trip until tower was back up and runnin, removed yaw skirt pieces that was ttore and hanging down. inspeceted around yaw gear and looked for any more loose skirting. went down tower and tower is running | 700144509
KRAYN-WKO-NDX-20140622-02 | FM1141 - 22WEA80830 FM1141 PitchAngle 1 | Closed |  |  |  | 7/1/2014 | 6/22/2014 | 6/23/2014 | 10.4 | Highland 1 |  |  |  |  | VEN-304 | 4.5 |  |  | Went up tower and locked out the rotor. Entered the hub to find a stud in blade 1 had broken in the #8 position. The stud and nutwere found easily. The washer was found after some searching. The internal of the hub was inspected for damage with only cosmetic damge found including chipped paint, dented cabinet doors, and slung grease. We adjusted the RED encoder in blade 1 since it hadbeen knocked out of adjustment. We then returned to the nacelle and unlocked the rotor. We started the turbien to allow for a pitch test which passed. So we manually stopped the turbien and headed down tower. We then started the turbien with no further defects noted at this time. | 800072675

## Parts
ID | Description | Qty | Vendor | Original ID
GAMSA-PRT-0457 | Reten delantero partido D660-D700x20 GVP | 1 | Gamesa | 107912
GAMSA-PRT-0457 | RV8-10-C-0-50 VALVE | 1 | Gamesa | 109534
GAMSA-PRT-0458 | MOTOR ABB 3480RPM, 1.5KW 1.7A 690V 60HZ | 1 | Gamesa | GP005890
GAMSA-PRT-0459 | ACTUADOR JOVENTA mod.DAS2.S 8Nm | 1 | Gamesa | GP009355
GAMSA-PRT-0460 | 100-115-40 FRICTION BEARING | 2 | Gamesa | GP021965
GAMSA-PRT-0461 | G87GF CYLINDER HOLDER (MACHINING) | 2 | Gamesa | GP022073
GAMSA-PRT-0462 | SILICONE DOW CORNING 7093 WHITE | 1 | Gamesa | GP022119
GAMSA-PRT-0463 | SEAL GAUGE 0.5 MM REAR BEARING | 2 | Gamesa | GP072783
GAMSA-PRT-0464 | SEAL GAUGE 1 MM REAR BEARING | 2 | Gamesa | GP072793
GAMSA-PRT-0465 | Stickers botton section | 3 | Gamesa | GP099957
GAMSA-PRT-0466 | BOLTS PLATFORMS FLANGE | 1 | Gamesa | GP099847
GAMSA-PRT-0467 | ADAPTER INTERFACE FOR WIND VANE SIGNAL | 1 | Gamesa | 9010623
NORDX-PRT-0002 | slip ring unit excl. enc. K08 CCV gamma | 1 | Nordex | 32828
NORDX-PRT-0002 | spindle for Liftket chain hoist | 1 | Nordex | 24298