## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Asset ID | Vendor ID | Actual Hours | Part ID | Part Quantity | Comments | Original ID
PATTN-WKO-GAM-20140115-01 | gam-205 low hyro level | Closed | Corrective Maintenance | Forced | 02-High | 1/15/2014 | 1/15/2014 | 1/15/2014 | 2.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9167 |  |  | 2000856: gam-turbine low on hydro fluid , level was ok, found bad acc, replaced acc checked for leaks all checked good ran turbine | 401529646
PATTN-WKO-GAM-20140117-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532925
PATTN-WKO-GAM-20140117-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.33333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532953
PATTN-WKO-GAM-20140117-03 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.16667 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532981
PATTN-WKO-GAM-20140117-04 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532999
PATTN-WKO-GAM-20140117-05 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533008
PATTN-WKO-GAM-20140117-06 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.2667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533033
PATTN-WKO-GAM-20140117-07 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533048
PATTN-WKO-GAM-20140117-08 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.55 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.23333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533061
PATTN-WKO-GAM-20140118-01 | GAM-700 ALARM PLC/ CONVERTER COMMUNICATI | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 2.7333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMM FAILURE / LOCAL RESET | 401533074
PATTN-WKO-GAM-20140118-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 2.85 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533089
PATTN-WKO-GAM-20140118-03 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 4.6167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533109
PATTN-WKO-GAM-20140123-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/23/2014 | 1/23/2014 | 1/23/2014 | 3.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2000856: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401546597
PATTN-WKO-GAM-20140126-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/26/2014 | 1/26/2014 | 1/26/2014 | 1.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401546599
PATTN-WKO-GAM-20140126-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/26/2014 | 1/26/2014 | 1/26/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / RESET | 401546600
PATTN-WKO-GAM-20140129-01 | gam-107 yaw motor breaker | Closed | Corrective Maintenance | Forced | 02-High | 1/29/2014 | 1/29/2014 | 1/29/2014 | 10.5167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10.5167 |  |  | 2000856: gam-remove motor from yaw drive, removed yaw drive from nacelle | 401548165
PATTN-WKO-GAM-20140130-01 | gam-804 blade error | Closed | Corrective Maintenance | Forced | 02-High | 1/30/2014 | 1/30/2014 | 1/30/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.3167 | GAMSA-PRT-0469 | 1 | 2000856: gam-found elctro valve to be bent, drained pressure back from system and replaced valve | 401549323
PATTN-WKO-GAM-20140131-01 | gam-205 low hydro oil | Closed | Corrective Maintenance | Forced | 02-High | 1/31/2014 | 1/31/2014 | 1/31/2014 | 0.76667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.76667 | GAMSA-PRT-0471 | 1 | 2000856: gam-205 low hyro level found oil level to be ok, found level sensor to be nok changed out sensor alarm cleared ran tower | 401549374
PATTN-WKO-GAM-20140209-01 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 2/9/2014 | 2/9/2014 | 2/9/2014 | 1.6833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.41667 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401554554
PATTN-WKO-GAM-20140210-01 | GAM-2118 ALARM INTERBUS FAILURE / TROU | Closed | Corrective Maintenance | Forced | 02-High | 2/10/2014 | 2/10/2014 | 2/10/2014 | 0.38333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / TROUBLESHOOT / RESET | 401556214
PATTN-WKO-GAM-20140210-02 | GAM-2106 ALARM PREVENTATIVE DESIGN MOD | Closed | Corrective Maintenance | Forced | 02-High | 2/10/2014 | 2/10/2014 | 2/10/2014 | 5.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 |  |  | 2001212: GAM-2106 ALARM PREVENTATIVE DESIGN MOD | 401556232
PATTN-WKO-GAM-20140211-01 | GAM-300 ALARM ANEMOMETER FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 2/11/2014 | 2/11/2014 | 2/11/2014 | 5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 | GAMSA-PRT-0466 | 4 | 2001212: GAM-300 ANEMOMETER FAILURE / REPLACED ANEMOMETER AND WIND VANE, WHICH WERE DAMAGED BY ICE, FOUND GEARBOX PUMP WAS LEAKING AND REPLACED | 401556752
PATTN-WKO-GAM-20140211-02 | GAM-PLANNED INVESTIGATION OF YAW DRIVES | Closed | Corrective Maintenance | Forced | 02-High | 2/11/2014 | 2/11/2014 | 2/11/2014 | 5.3333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.5 |  |  | 2001212: GAM-PLANNED INVESTIGATION OF YAW DRIVES WITH ENGINEERS JUAN REDIN, AND RIGOBERTO MEDENA | 401559219
PATTN-WKO-GAM-20140212-01 | GAM-PLANNED INVESTIGATION OF YAW SYSTEM | Closed | Corrective Maintenance | Forced | 02-High | 2/12/2014 | 2/12/2014 | 2/12/2014 | 2.4833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED INVESTIGATION OF YAW SYSTEM WITH ENGINEERS JUAN REDIN AND RIGOBERTO MEDENA | 401559259
PATTN-WKO-GAM-20140213-01 | GAM-2118 ALARM INTERBUS FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/13/2014 | 0.68333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / INSPECTED FOUND LOOSE CARD | 401559273
PATTN-WKO-GAM-20140218-01 | gam-5237 error on rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/18/2014 | 2/18/2014 | 2/19/2014 | 24.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7667 | GAMSA-PRT-0457 | 9 | 2000856: gam-5237 error on rotor phase S went up tower checked converter all looked good, looked at slip ring found arc marks on all phases of slip ring. removed old slip replaced with new. replaced tape on slip ring knuckles applyed the proper paint to | 401567400
PATTN-WKO-GAM-20140218-01 | gam-5237 error on rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/18/2014 | 2/18/2014 | 2/19/2014 | 24.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7667 | GAMSA-PRT-0464 | 20 | 2000856: gam-5237 error on rotor phase S went up tower checked converter all looked good, looked at slip ring found arc marks on all phases of slip ring. removed old slip replaced with new. replaced tape on slip ring knuckles applyed the proper paint to | 401567400
PATTN-WKO-GAM-20140213-02 | gam-5237 error rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/20/2014 | 35.7167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10 | GAMSA-PRT-0457 | 9 | 2000856: gam-5237-found slip ring bad replaced slip ring | 401567423
PATTN-WKO-GAM-20140213-02 | gam-5237 error rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/20/2014 | 35.7167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10 | GAMSA-PRT-0464 | 20 | 2000856: gam-5237-found slip ring bad replaced slip ring | 401567423
PATTN-WKO-GAM-20140221-01 | gam-5238-error phase t | Closed | Corrective Maintenance | Forced | 02-High | 2/21/2014 | 2/21/2014 | 2/22/2014 | 16.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8667 | GAMSA-PRT-0464 | 20 |  | 401569549
PATTN-WKO-GAM-20140221-01 | gam-5238-error phase t | Closed | Corrective Maintenance | Forced | 02-High | 2/21/2014 | 2/21/2014 | 2/22/2014 | 16.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8667 | GAMSA-PRT-0457 | 9 |  | 401569549
PATTN-WKO-GAM-20140225-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 2/25/2014 | 2/25/2014 | 2/25/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0457 | 9 | 2000856: gam-cleaned out slip ring, inspected slip ring body all checked ok ran turbine | 401571051
PATTN-WKO-GAM-20140225-02 | gam-slip ring inspection cleaning | Closed | Corrective Maintenance | Forced | 02-High | 2/25/2014 | 2/25/2014 | 2/25/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 |  |  | 2000856: gam-cleaning inspection on slip ring, cleaned out slip ring all checked ok ran turbine | 401573326
PATTN-WKO-GAM-20140224-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 2/24/2014 | 2/24/2014 | 2/24/2014 | 3.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5 |  |  | 2000856: gam-inspection of slip ring found to be dirty, cleaned slip ring and replaced brushes | 401573340
PATTN-WKO-GAM-20140303-01 | gam-pitch ram cover dm | Closed | Corrective Maintenance | Forced | 02-High | 3/3/2014 | 3/3/2014 | 3/3/2014 | 0.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.83333 |  |  | 2000856: gam-installed new pitch ram shaft cover | 401576693
PATTN-WKO-GAM-20140306-01 | gam-107 yaw motor circuit breaker | Closed | Corrective Maintenance | Forced | 02-High | 3/6/2014 | 3/6/2014 | 3/6/2014 | 8.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 9.5 |  |  | 2000856: gam-found brokin drive removed yaw replace with new drive checked motor and drive for proper fit all checked ok ran turbine | 401580634
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0469 | 2 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0474 | 1 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0475 | 60 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0476 | 1 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0477 | 10 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0478 | 30 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140304-01 | gam-118 yaw motor error | Closed | Corrective Maintenance | Forced | 02-High | 3/4/2014 | 3/4/2014 | 3/4/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.2167 | GAMSA-PRT-0478 | 30 |  | 401581174
PATTN-WKO-GAM-20140304-01 | gam-118 yaw motor error | Closed | Corrective Maintenance | Forced | 02-High | 3/4/2014 | 3/4/2014 | 3/4/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.2167 | GAMSA-PRT-0477 | 30 |  | 401581174
PATTN-WKO-GAM-20140307-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/7/2014 | 3/7/2014 | 3/7/2014 | 0.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 | GAMSA-PRT-0479 | 1 | 2000677: gam-cleaning slip ring, replace brushes, check for leakes on yaw drive, and cleaning belly | 401582862
PATTN-WKO-GAM-20140310-01 | GAM-404 ALARM HIGH TEMP MAIN BEARING | Closed | Corrective Maintenance | Forced | 02-High | 3/10/2014 | 3/10/2014 | 3/10/2014 | 0.66667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-404 ALARM HIGH TEMP MAINBEARING / CHANGED TEMP CARD | 401583356
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0480 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0481 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0482 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140311-01 | gam-inspection of nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/12/2014 | 25.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.1167 |  |  | 2000856: gam-checked the op of the louvers. reset the cams. ran tower | 401584977
PATTN-WKO-GAM-20140311-02 | gam-check nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 2.1333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1333 |  |  | 2000856: gam-check nacelle louvers for proper op, found they were opening backwards. switched wires reset louver cams and ran tower | 401585000
PATTN-WKO-GAM-20140311-03 | gam-naccelle louver inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.6 |  |  | 2000856: gam-checked nacelle louvers, found opening backwards, reset cams and switch wires around ran turbine | 401585004
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0477 | 60 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0478 | 30 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0493 | 10 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0458 | 2 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140312-01 | gam-2106 temp fail | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2000856: gam-2106 reset top cabinet all temps came back ran turbine | 401585166
PATTN-WKO-GAM-20140312-02 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 2.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9 | GAMSA-PRT-0476 | 1 | 2000856: gam-installed north sensor, cleaned out slip ring and changed brushes | 401585267
PATTN-WKO-GAM-20140312-03 | GAM-MODIFIED ROOF AND INSTALLED NORTH SE | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 1.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.25 | GAMSA-PRT-0476 | 1 | 2001212: GAM-MODIFIED ROOF AND INSTALLED NORTH SENSOR | 401585289
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0500 | 1 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0484 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0466 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140315-01 | GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADE | Closed | Corrective Maintenance | Forced | 02-High | 3/15/2014 | 3/15/2014 | 3/15/2014 | 5.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5167 | GAMSA-PRT-0495 | 1 | 2001212: GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADES VERY HIGH / CHANGED BALLUF CABLE | 401590249
PATTN-WKO-GAM-20140317-01 | GAM-800 ALARM PITCH ACTIVATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/17/2014 | 3/17/2014 | 3/17/2014 | 1.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-800 ALARM PITCH ACTIVATION ERROR / CHANGED PROP VALVE ON BLADE C | 401590643
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0484 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0494 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0488 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0484 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0494 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140319-01 | GAM-GEAR BOX OIL SAMPLE / REPLACED MIS | Closed | Corrective Maintenance | Forced | 02-High | 3/19/2014 | 3/19/2014 | 3/19/2014 | 0.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0488 | 1 | 2001212: GAM-GEARBOX OIL SAMPLE / REPLACED NUTS ON VICKERS VALVES | 401592858
PATTN-WKO-GAM-20140320-01 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 5.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LOCAL RESET | 401593615
PATTN-WKO-GAM-20140320-02 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 1.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LANDED GEARBOX SHIELDING | 401594219
PATTN-WKO-GAM-20140320-03 | GAM-426 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 0.88333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 | GAMSA-PRT-0507 | 1 | 2001212: GAM-426 ALARM OGS / CHANGED SENSOR | 401594279
PATTN-WKO-GAM-20140321-01 | GAM-327 ALARM LTK CONFIRMATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 0.41667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-327 LTK CONFIRMATION ERROR / CHANGED LOUVERS | 401594941
PATTN-WKO-GAM-20140321-02 | GAM-PLANNED ROOF REPAIR / GREASED YAW | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 4.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.5 |  |  | 2001212: GAM-PLANNED ROOF REPAIR / GREASED YAW | 401595371
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0464 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0457 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0484 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0466 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0484 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0499 | 3 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0477 | 34 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0493 | 13 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0458 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0466 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0464 | 20 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0457 | 9 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0479 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0476 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0484 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0466 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0479 | 1 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0484 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0466 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140327-01 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 4 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / PLANNED INSTALLATION OF KBT YAW DRIVE | 401601799
PATTN-WKO-GAM-20140327-02 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 3.85 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLATION OF HG YAW DRIVE | 401601823
PATTN-WKO-GAM-20140328-01 | GAM-PLANNED CORRECTIVE / NOTICED SONIC | Closed | Corrective Maintenance | Forced | 02-High | 3/28/2014 | 3/28/2014 | 3/28/2014 | 0.63333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / ADJUSTED SONIC | 401602119
PATTN-WKO-GAM-20140330-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/30/2014 | 3/30/2014 | 3/30/2014 | 3.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5 | GAMSA-PRT-0487 | 1 | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / CHANGED TRANSFORMER FUSE B | 401603723
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0496 | 5 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0497 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0514 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-02 | GAM-804 ALARM DIFFERENCE BETWEEN BLADES | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 1.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 |  |  | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES VERY HIGH / CHANGED AO CARD IN HUB CABINET | 401605611
PATTN-WKO-GAM-20140401-01 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.5167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0491 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHECKED CONVERTER TEMPS, CHANGED SIGHT GLASS ON GEARBOX | 401606444
PATTN-WKO-GAM-20140401-02 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.0333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / WENT UP TO CHECK DIFFERENCES IN CONVERTER TEMPS AT CUSTOMERS REQUEST | 401607123
PATTN-WKO-GAM-20140401-03 | GAM-PLANNED CORRECTIVE / HAD HIGHER TE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 0.8 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSPECTED CONVERTER AT CUSTOMERS REQUEST | 401607130
PATTN-WKO-GAM-20140401-04 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.3833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401607137
PATTN-WKO-GAM-20140401-05 | GAM-5200 ALARM MAGNETOTHERMIC TRIP OF TH | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-5200 ALARM MAGNETOTHERMIC TRIP OF THE LIINE PROTECTION / TRANSFORMER LOUVER CLOSED OVERHEATING CONVERTER | 401607159
PATTN-WKO-GAM-20140402-01 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/2/2014 | 4/2/2014 | 4/2/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.25 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / CHANGED GATEWAY, AND BLED BOTH YAW BRAKE SYSTEM AND ROTOR BRAKE SYSTEM | 401607546
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7 | GAMSA-PRT-0486 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7 | GAMSA-PRT-0485 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 0.98333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401609844
PATTN-WKO-GAM-20140404-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 1.4833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0494 | 2 | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / FOUND 2 BAD ACTUATORS AND CHANGED THEM | 401610176
PATTN-WKO-GAM-20140404-02 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 | GAMSA-PRT-0506 | 1 | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / TESTED KR330G FOUND BAD RESISTANCE AND CHANGED | 401610307
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.2833 | GAMSA-PRT-0502 | 20 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.2833 | GAMSA-PRT-0494 | 1 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140408-01 | GAM-203 ALARM LOW PRESSURE HG / CHANGE | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/9/2014 | 6.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.4833 |  |  | 2001212: GAM-203 ALARM LOW PRESSURE HG / CHANGED BLADE C PITCH BLOCK | 401620946
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0381 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0508 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140411-01 | GAM-1823 ALARM COOLANT CONFIRMATION FAIL | Closed | Corrective Maintenance | Forced | 02-High | 4/11/2014 | 4/11/2014 | 4/11/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 | GAMSA-PRT-0494 | 1 | 2001212: GAM-1823 ALARM COOLANT CONFIRMATION FAILURE / FOUND BAD LOUVER AND CHANGED | 401620949
PATTN-WKO-GAM-20140415-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/15/2014 | 4/15/2014 | 4/15/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CLEANED RADIATORS | 401620950
PATTN-WKO-GAM-20140413-01 | GAM-410 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 4/13/2014 | 4/13/2014 | 4/13/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 | GAMSA-PRT-0507 | 1 | 2001212: GAM-410 OGS / CHANGED SENSOR | 401620951
PATTN-WKO-GAM-20140416-01 | GAM-2198 ALARM TEMP MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 4/16/2014 | 4/16/2014 | 4/16/2014 | 5.3833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6 | GAMSA-PRT-0494 | 2 | 2001212: GAM-2198 ALARM TEMP MODULE FAILURE / CHANGED TEMP CARD, GREASED YAW AND BLED SYSTEM, CHANGED 2 LOUVERS | 401621045
PATTN-WKO-GAM-20140419-01 | GAM-401 ALARM LOW PRESSURE GEAR BOX / | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 1.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624105
PATTN-WKO-GAM-20140419-02 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.8 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624111
PATTN-WKO-GAM-20140419-03 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624119
PATTN-WKO-GAM-20140420-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/20/2014 | 5.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.5 |  |  | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / LEAK TO GROUND ON YAW MOTOR, CHANGED YAW MOTOR 181A | 401624125
PATTN-WKO-GAM-20140420-02 | GAM-PLANNED CORRECTIVE / INSTALLED YAW | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/21/2014 | 29.2333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 | GAMSA-PRT-0502 | 10 | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED YAW DRIVE | 401624141
PATTN-WKO-GAM-20140421-01 | GAM-114 ALARM YAW BRAKE LOW PRESSURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 0.61667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-114 ALARM YAW BRAKE LOW PRESSURE / BLED YAW BRAKE SYSTEM | 401624153
PATTN-WKO-GAM-20140421-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 2.55 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0515 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CARD, GREASED AND BLED YAW CLAMPS | 401624183
PATTN-WKO-GAM-20140422-01 | GAM-PLANNED CORRECTIVE / BLED BRAKE SY | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/22/2014 | 6.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6 | GAMSA-PRT-0494 | 3 | 2001212: GAM-PLANNED CORRECTIVE / BLED BRAKE SYSTEM, FOUND LOOSE BOLTS ON YAW DRIVES AND TIGHTENED, CLEANED TURBINE | 401625671
PATTN-WKO-GAM-20140423-01 | GAM-5209-coolant circuit falure | Closed | Corrective Maintenance | Forced | 02-High | 4/23/2014 | 4/23/2014 | 4/23/2014 | 0.78333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.78333 |  |  | 2001212: GAM-5219-cooling circuit falure- troubleshoot and tightend wiring | 401626574
PATTN-WKO-GAM-20140422-02 | GAM-107 yaw motor circuit breakers | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/24/2014 | 84.4 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.9 | GAMSA-PRT-0494 | 1 | 2001212: GAM-107 yaw motors circuit breakers - call in removed broken left front yaw assembly could not install new assembly due to high winds - returned 24th installed new assembly with new yaw motor also installed new upper ltk louver motor rtsvc | 401627759
PATTN-WKO-GAM-20140424-01 | GAM-721 wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 4/24/2014 | 4/24/2014 | 4/24/2014 | 1.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.1167 |  |  | 2001212: GAM-721 wind vane falure- troubleshoot wind vane | 401627771
PATTN-WKO-GAM-20140425-01 | GAM-PLANNED CORRECTIVE INSTALLED RETRO O | Closed | Corrective Maintenance | Forced | 02-High | 4/25/2014 | 4/25/2014 | 4/25/2014 | 2.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED RETRO ON LIGHTENING SYSTEM FOR ENGINEERS | 401633211
PATTN-WKO-GAM-20140426-01 | GAM-208 ALARM HG FEEDBACK FAILURE / RE | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.3667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0474 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633212
PATTN-WKO-GAM-20140430-01 | GAM-PLANNED CORRECTIVE / OWNER QC WALK | Closed | Corrective Maintenance | Forced | 02-High | 4/30/2014 | 4/30/2014 | 4/30/2014 | 3 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 |  |  | 2001212: GAM-PLANNED CORRECTIVE / OWNER QC WALKDOWN, FOUND FAULTY WIRING IN TOP CABINET ALL OF X4 BLOCK WAS WIRED NEUTRAL TO LINE | 401633213
PATTN-WKO-GAM-20140428-01 | GAM-PLANNED CORRECTIVE / CHANGED MOUNT | Closed | Corrective Maintenance | Forced | 02-High | 4/28/2014 | 4/28/2014 | 4/28/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.7667 | GAMSA-PRT-0498 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHANGED MOUNTING POST FOR SONIC | 401633214
PATTN-WKO-GAM-20140501-01 | GAM-2509-comm error | Closed | Corrective Maintenance | Forced | 02-High | 5/1/2014 | 5/1/2014 | 5/1/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 | GAMSA-PRT-0506 | 1 | 2001212: GAM-2509-comm error- installed new kr330 relay kit in base cabinet rtsvc | 401633286
PATTN-WKO-GAM-20140426-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.6167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633287
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0494 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0503 | 40 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0502 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-02 | GAM-327 ALARM LTK CONFIRMATION ERROR / C | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CHANGED JOVENTA DURING THIRD PARTY INSPECTION OF GEARBOX | 401638191
PATTN-WKO-GAM-20140505-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 4.15 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.15 |  |  | USI-Borescope EOW Inspections/ Perform EOW Gearbox inspections | 401638556
PATTN-WKO-GAM-20140505-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 3.1333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.1333 |  |  | USI-EOW-Gearbox Borescope Inspections/ Perform EOW Gearbox Inspections | 401638557
PATTN-WKO-GAM-20140502-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.9167 |  |  | USI-EOW Gearbox Inspections/ Perform Gearbox Inspections | 401638558
PATTN-WKO-GAM-20140509-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4667 |  |  | USI-EOW Gearbox Borescope Inspections/ Perform Gearbox Inspections | 401640904
PATTN-WKO-GAM-20140509-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8167 |  |  | USI-EOW-Gearbox Borescope Inspections | 401640905
PATTN-WKO-GAM-20140509-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 3.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.1833 |  |  | USI-EOW Gearbox Borescope inspections/perform gearbox inspections | 401640906
PATTN-WKO-GAM-20140509-04 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.6667 |  |  | USI-EOW Gearbox Inspections/ Perform Borescope inspections | 401640907
PATTN-WKO-GAM-20140512-01 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4167 |  |  |  | 401642558
PATTN-WKO-GAM-20140512-02 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0 |  |  | USI-EOW Borescope Inspections Gearbox | 401642559
PATTN-WKO-GAM-20140513-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 |  |  | USI-EOW-Gearbox Borescope inspections | 401643573
PATTN-WKO-GAM-20140513-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9 |  |  | USI-EOW Gearbox borescope inspections | 401643575
PATTN-WKO-GAM-20140514-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8167 |  |  | USI-EOW Gearbox Borescope Inspections/Perform Borescope Inspections | 401645458
PATTN-WKO-GAM-20140514-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.5833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5833 |  |  | USI-EOW-Gearbox Borescope Inspections/Perform gearbox inspections | 401645460
PATTN-WKO-GAM-20140513-03 | GAM-208-hu feedback error | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 | GAMSA-PRT-0512 | 1 | 2001223: GAM-208-hu pump drive falure- installed new contactor | 401645583
PATTN-WKO-GAM-20140515-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 |  |  | USI-EOW Gearbox Borescope inspections | 401645615
PATTN-WKO-GAM-20140515-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | USI-EOW Borescope inspections Gearbox | 401645616
PATTN-WKO-GAM-20140514-03 | GAM-300-anemometer failure | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/15/2014 | 25.4333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.53333 |  |  | 2001223: GAM-300-anemometer falure- found loose wiring - reconnected rtsvc | 401646567
PATTN-WKO-GAM-20140514-04 | GAM-403-high temp gearbox | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 1.0833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.46667 |  |  | 2001223: GAM-403-gearbox high temp | 401646594
PATTN-WKO-GAM-20140515-03 | GAM-721-wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.65 |  |  | 2001223: GAM-721-wind vane falure- installed new wind vane | 401646689
PATTN-WKO-GAM-20140516-01 | GAM-shim gearbox-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox in accordance with maintenance procedure | 401651187
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 | GAMSA-PRT-0485 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 | GAMSA-PRT-0486 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140519-01 | GAM-shim gear box- pending task resoluti | Closed | Corrective Maintenance | Forced | 02-High | 5/19/2014 | 5/19/2014 | 5/19/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox per procedure | 401652551
PATTN-WKO-GAM-20140523-01 | GAM-SHIM GEARBOX-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/23/2014 | 5/23/2014 | 5/23/2014 | 1.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.9167 |  |  | 2001223: GAM-shimed gearbox per procedure | 401658443
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0496 | 5 |  | 401661282
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0497 | 1 |  | 401661282
PATTN-WKO-GAM-20140508-01 | GAM-18 MONTH Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/9/2014 | 32.4833 | Patton | Planned |  | PMI-003 |  | VEN-165 | 2.5833 | GAMSA-PRT-0478 | 30 | 2001212: GAM-18month minor maint complete per ck list 2001223: 18month maint complete per ck list | 500593590
PATTN-WKO-GAM-20140508-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/16/2014 | 198.7833 | Patton | Planned |  | PMI-003 |  | VEN-165 | 1.6833 | GAMSA-PRT-0478 | 30 | 2001223: GAM-18 month maint complete per ck list | 500593836
PATTN-WKO-GAM-20140523-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/23/2014 | 5/23/2014 | 5/28/2014 | 128 | Patton | Planned |  | PMI-003 |  | VEN-165 | 4.8 | GAMSA-PRT-0492 | 1 | 2001223: 18 month maintenance complete per ck list | 500593839
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 |  | VEN-165 | 3.5167 | GAMSA-PRT-0492 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 |  | VEN-165 | 3.5167 | GAMSA-PRT-0466 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140520-01 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/20/2014 | 5/20/2014 | 5/22/2014 | 55.6667 | Patton | Planned |  | PMI-003 |  | VEN-165 | 4.8667 | GAMSA-PRT-0492 | 1 | 2001223: 18 month maintenance complete per ck list | 500597336

## Parts
ID | Description | Qty | Vendor | Original ID
GAMSA-PRT-0457 | SILICE TAPE SCOTCH 70 | 55 | Gamesa | GP003575
GAMSA-PRT-0458 | LADDER RETAINING SUPPORT | 10 | Gamesa | P340009
GAMSA-PRT-0459 | FA NACELLE ACCESS LADDER G8X | 2 | Gamesa | GP012766
GAMSA-PRT-0460 | Hex.head SCR.ISO 4017 M8x45 8.8 DAC500A | 4 | Gamesa | GP004247
GAMSA-PRT-0461 | ISO 7093 M8 NYLON WAS. | 8 | Gamesa | P650226
GAMSA-PRT-0462 | NUT ISO 10511-M8-04-Zn-Ni-PAS,CHR+S | 4 | Gamesa | P670159
GAMSA-PRT-0463 | SLIP RING UNIT | 0 | Gamesa | GP062214
GAMSA-PRT-0464 | ADHESIVE TAPE 0.18x19 SCOTCH-69 | 101 | Gamesa | 1R1524CRFJJ
GAMSA-PRT-0465 | NRG B302 AND B303 WINDVANE | 0 | Gamesa | 9000602
GAMSA-PRT-0466 | ELASTIC FITTING AMC-SCB 25 | 25 | Gamesa | GP007852
GAMSA-PRT-0467 | NRG B301 ANEMOMETER | 0 | Gamesa | 9000601
GAMSA-PRT-0468 | MOTOPUMP B-P 60HZ 100L/MIN 3KW_PX045#4B | 0 | Gamesa | GP097008
GAMSA-PRT-0469 | ELECTRICALLY OPERATED VALVE 02-176361 | 3 | Gamesa | 50786
GAMSA-PRT-0470 | QUICK CONNECTOR FEMALE 4P+E 16A | 1 | Gamesa | GP101673
GAMSA-PRT-0471 | LEVEL SWITCH HINE LM1FA450NASP-WARNING | 1 | Gamesa | GP069609
GAMSA-PRT-0472 | BONFIGLIOLI YAW GEARBOX G9X C4H | 0 | Gamesa | GP118569
GAMSA-PRT-0473 | ACCU. 24.5L PREFILL PRESS. 73 BAR. (CE-A | 0 | Gamesa | GP043460
GAMSA-PRT-0474 | AUXILIARY CONTACT CA5-01 1NC | 2 | Gamesa | 50013
GAMSA-PRT-0475 | GENE.GEAR.SYNT.OIL(PAO) (ISO VG 320) | 60 | Gamesa | GP061950
GAMSA-PRT-0476 | INDUCTIV SENSOR M18 + SHEILD | 4 | Gamesa | 114941
GAMSA-PRT-0477 | SHELL TELLUS S2 V 32 (old named T32) | 142 | Gamesa | GP012886
GAMSA-PRT-0478 | FLUORESCENT TUBE TLD54 18W | 150 | Gamesa | P393068
GAMSA-PRT-0479 | BRUSH CANT05 | 4 | Gamesa | GP052263
GAMSA-PRT-0480 | FITTING LEE15LROMD-CF | 1 | Gamesa | GP219671
GAMSA-PRT-0481 | H-1SC-8-TLML15-TLML9015-NA-NA-C3-1100 | 1 | Gamesa | GP092845
GAMSA-PRT-0482 | FITTING2353-112-15-NA-NA-NA-L-C3-N | 1 | Gamesa | GP107541
GAMSA-PRT-0483 | IB IL TEMP 2 RTD-PAC | 0 | Gamesa | GP004895
GAMSA-PRT-0484 | SCR.ISO 4017-M10x50-8.8-DAC500B | 28 | Gamesa | GP006520
GAMSA-PRT-0485 | G87GF CYLINDER HOLDER (MACHINING) | 6 | Gamesa | GP022073
GAMSA-PRT-0486 | 100-115-40 FRICTION BEARING | 6 | Gamesa | GP021965
GAMSA-PRT-0487 | FUS.BT G80 Estator BUSSMANN S4 2500A | 1 | Gamesa | P393237
GAMSA-PRT-0488 | PLASTIC BOTTLE FOR GEARBOX OIL SAMPLES ( | 2 | Gamesa | GP007339
GAMSA-PRT-0489 | IB IL AO 2-U-BP-PAC | 0 | Gamesa | GP004898
GAMSA-PRT-0490 | 6 MONTHS MAINTENANCE KIT G97 DTC CANT | 0 | Gamesa | GP263544
GAMSA-PRT-0491 | SEACHER LEVEL GEARBOX HANSEN | 1 | Gamesa | GP027902
GAMSA-PRT-0492 | 1 AUXILIARY CONTACT BLOCK N.O CE5-10 D 0 | 3 | Gamesa | 50879
GAMSA-PRT-0493 | COOLER LIQUID FOR VCS COOLER | 23 | Gamesa | 149391
GAMSA-PRT-0494 | ACTUADOR JOVENTA mod.DAS2.S 8Nm | 14 | Gamesa | GP009355
GAMSA-PRT-0495 | CABLE WS251C G8X | 1 | Gamesa | C393086
GAMSA-PRT-0496 | BRAKE PAD | 10 | Gamesa | P370104
GAMSA-PRT-0497 | BRAKE PAD WITH THERMISTOR ASSEMBLY | 2 | Gamesa | GP005798
GAMSA-PRT-0498 | SONIC BRACKET G8X | 1 | Gamesa | GP107638
GAMSA-PRT-0499 | NEEDLE VALVE NV1 10 K O | 3 | Gamesa | 565590
GAMSA-PRT-0500 | DOOR SAFETY LOCK, TOP CABINET G8X INGET. | 1 | Gamesa | GP030428
GAMSA-PRT-0501 | GATEWAY PRODUCT | 0 | Gamesa | GP006115
GAMSA-PRT-0502 | SHELL OMALA S4 WE 320 (old named Tivela | 31 | Gamesa | 149107
GAMSA-PRT-0503 | F. A. GENERIC HYDRAULIC GROUP FLUIDS | 40 | Gamesa | GP013211
GAMSA-PRT-0504 | SMART CROWBAR SNUBBER MODULE | 0 | Gamesa | GP091208
GAMSA-PRT-0505 | SMART CROWBAR CONTROL CARD | 0 | Gamesa | GP091205
GAMSA-PRT-0506 | RELAY KR330 RELECO | 2 | Gamesa | GP088288
GAMSA-PRT-0507 | Sens.Balluff 0206D BESM30ML1,10-30Vdc | 2 | Gamesa | P393119
GAMSA-PRT-0508 | CONTACTOR ABB A50-30-00 | 1 | Gamesa | GP022129
GAMSA-PRT-0509 | PITCH BLOCK G9X HINE | 0 | Gamesa | GP137529
GAMSA-PRT-0510 | BOLT RETAINER G9X | 3 | Gamesa | GP121846
GAMSA-PRT-0511 | PROPORTIONAL VALVE KBFDG4V5 VICKERS | 0 | Gamesa | GP118568
GAMSA-PRT-0512 | CONTAC. A40-30-10-230V 50-60HZ | 1 | Gamesa | 93312
GAMSA-PRT-0513 | ABB YAW MOTOR G9X 60HZ C4H | 0 | Gamesa | GP119763
GAMSA-PRT-0514 | SUPPORT ARM FOR ANEMO BRACKET HT | 1 | Gamesa | GP025987
GAMSA-PRT-0515 | IB IL 24 DI 8-T2-PAC | 1 | Gamesa | GP004892