## General Info
Order | Order Type | Bas. start date | Basic fin. date | Description | Turbine | Functional loc. | System status | User status | Changed by
401862384 | ZPM2 | 2015-01-02 | 2015-01-02 | GAM-804 ALARM DIFFERENCE IN BLADES / F | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401863233 | ZPM2 | 2015-01-06 | 2015-01-06 | GAM-PLANNED CORRECTIVE / ON MAINTENANC | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401863238 | ZPM2 | 2015-01-06 | 2015-01-06 | GAM-PLANNED CORRECTIVE / NOTICED LEAKIN | G97 / 78 / 3 - Patton | WF-US-0PA-1121-Y2-A-003 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401864077 | ZPM2 | 2015-01-06 | 2015-01-06 | GAM-PLANNED CORRECTIVE / DISCOVERED EXCE | G97 / 90 / 8 - Patton | WF-US-0PA-1121-Y2-A-007 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401865662 | ZPM2 | 2015-01-08 | 2015-01-08 | GAM-5203 ALARM HEATING/COOLANT THERMAL M | G97 / 78 / 13 - Patton | WF-US-0PA-1121-Y1-A-003 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401868943 | ZPM2 | 2015-01-12 | 2015-01-12 | GAM-205 ALARM LOW HG OIL / WENT UP AND | G97 / 90 / 7 - Patton | WF-US-0PA-1121-Y2-A-011 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401868950 | ZPM2 | 2015-01-12 | 2015-01-12 | GAM-426 ALARM SPEED READING ERROR / WE | G97 / 78 / 3 - Patton | WF-US-0PA-1121-Y2-A-003 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401868953 | ZPM2 | 2015-01-12 | 2015-01-12 | GAM-426 ALARM SPEED READ ERROR / CHANG | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401872279 | ZPM2 | 2015-01-14 | 2015-01-14 | GAM-replace inductive sensor bracket | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | TECO PCNF GMPS NMAT SETC | COMP | CARROYO01
401872286 | ZPM2 | 2015-01-14 | 2015-01-14 | GAM-nacelle inspection | G97 / 90 / 8 - Patton | WF-US-0PA-1121-Y2-A-007 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401876454 | ZPM2 | 2015-01-20 | 2015-01-20 | GAM- PUT THE INSULATED CABLE BACK ON | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401877674 | ZPM2 | 2015-01-21 | 2015-01-21 | GAM-327 LTK CONFIRMATION FAILURE | G97 / 90 / 8 - Patton | WF-US-0PA-1121-Y2-A-007 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401879734 | ZPM2 | 2015-01-23 | 2015-01-23 | Gam- GOT ALARM 2118 INERBUS FAILURE | G97 / 90 / 6 - Patton | WF-US-0PA-1121-Y2-A-006 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401886608 | ZPM2 | 2015-01-23 | 2015-01-23 | GAM- ALARM 410 OGS | G97 / 78 / 3 - Patton | WF-US-0PA-1121-Y2-A-003 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401884474 | ZPM2 | 2015-01-28 | 2015-01-28 | GAM- ALARM 2198 TEMP MEASURE MOD | G97 / 90 / 10 - Patton | WF-US-0PA-1121-Y2-A-010 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401891052 | ZPM2 | 2015-02-03 | 2015-02-03 | GAM-REPLACE BAD 08 FAN | G97 / 90 / 10 - Patton | WF-US-0PA-1121-Y2-A-010 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401891070 | ZPM2 | 2015-02-03 | 2015-02-03 | GAM-troubleshoot low fiber quality | G97 / 90 / 8 - Patton | WF-US-0PA-1121-Y2-A-007 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401891906 | ZPM2 | 2015-02-03 | 2015-02-03 | GAM-326 ALARM LTK FAILURE / TRIPPED BR | G97 / 90 / 5 - Patton | WF-US-0PA-1121-Y2-A-005 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401892513 | ZPM2 | 2015-02-04 | 2015-02-04 | GAM- ALARM 5238 ERROR IN PHASE T | G97 / 90 / 2 - Patton | WF-US-0PA-1121-Y2-A-002 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401893314 | ZPM2 | 2015-02-04 | 2015-02-04 | GAM-700 ALARM PLC/CONVERTER COMM FAILURE | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401896947 | ZPM2 | 2015-02-09 | 2015-02-09 | GAM-PLANNED CORRECTIVE / PREVENTATIVE | G97 / 78 / 13 - Patton | WF-US-0PA-1121-Y1-A-003 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401899235 | ZPM2 | 2015-02-10 | 2015-02-10 | GAM- preventive slip ring maintance | G97 / 90 / 4 - Patton | WF-US-0PA-1121-Y2-A-004 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401899267 | ZPM2 | 2015-02-10 | 2015-02-10 | GAM- preventive slip ring maintance | G97 / 90 / 7 - Patton | WF-US-0PA-1121-Y2-A-011 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
500727770 | ZPM1 | 2015-02-11 | 2015-02-11 | GAM-SLIP RING MAINTENACE | G97 / 90 / 12 - Patton | WF-US-0PA-1121-Y1-A-002 | TECO PCNF GMPS NMAT SETC | COMP | CARROYO01
401904978 | ZPM2 | 2015-02-15 | 2015-02-16 | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401912079 | ZPM2 | 2015-02-15 | 2015-02-21 | GAM- ALARM 426 SPEED READING ERROR | G97 / 90 / 4 - Patton | WF-US-0PA-1121-Y2-A-004 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401904907 | ZPM2 | 2015-02-16 | 2015-02-16 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401904939 | ZPM2 | 2015-02-16 | 2015-02-16 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401905340 | ZPM2 | 2015-02-16 | 2015-02-16 | GAM- ALARM 205 HG OIL LOW | G97 / 90 / 12 - Patton | WF-US-0PA-1121-Y1-A-002 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401912086 | ZPM2 | 2015-02-17 | 2015-02-20 | GAM- ALARM 1825 CICUIT BREAKER NO OK | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401908769 | ZPM2 | 2015-02-18 | 2015-02-18 | GAM- ALARM 2102 PLC MODULE FAILURE | G97 / 90 / 16 - Patton | WF-US-0PA-1121-Y2-A-012 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401912080 | ZPM2 | 2015-02-20 | 2015-02-20 | ALARM 2118 INTERBUS FAILURE | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401912081 | ZPM2 | 2015-02-21 | 2015-02-21 | GAM- ALARM 2118 INTERBUS FAILURE | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401912082 | ZPM2 | 2015-02-21 | 2015-02-21 | GAM- ALARM 2118 INTERBUS FAILURE | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401912083 | ZPM2 | 2015-02-21 | 2015-02-21 | GAM- ALARM 2118 INTERBUS FAILURE | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401912085 | ZPM2 | 2015-02-24 | 2015-02-24 | CLEANED UP AND LOWER TOOLS | G97 / 90 / 4 - Patton | WF-US-0PA-1121-Y2-A-004 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401914298 | ZPM2 | 2015-02-25 | 2015-02-25 | GAM-ALARM 422 GEARBOX ADDITIONAL PUMP CI | G97 / 90 / 6 - Patton | WF-US-0PA-1121-Y2-A-006 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401914836 | ZPM2 | 2015-02-26 | 2015-02-26 | GAM- 2102 PLC MODULE FAILURE REPLACE THE | G97 / 90 / 16 - Patton | WF-US-0PA-1121-Y2-A-012 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401916174 | ZPM2 | 2015-02-27 | 2015-02-27 | GAM- WARNING 422 GEARBOX THERMAL | G97 / 90 / 6 - Patton | WF-US-0PA-1121-Y2-A-006 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401919118 | ZPM2 | 2015-03-03 | 2015-03-03 | GAM- WARNING 422 GEARBOX FILTER PUMP THE | G97 / 90 / 6 - Patton | WF-US-0PA-1121-Y2-A-006 | REL PCNF GMPS NMAT SETC | ACCE | OSB_RFC01
401924002 | ZPM2 | 2015-03-06 | 2015-03-06 | GAM- ALARM 103 CW MOTOR FAILURE | G97 / 90 / 17 - Patton | WF-US-0PA-1121-Y2-A-009 | CLSD PCNF NMAT SETC | COMP | CARROYO01
401924018 | ZPM2 | 2015-03-06 | 2015-03-06 | GAM- ALARM 2118 INTERBUS FAILURE | G97 / 90 / 10 - Patton | WF-US-0PA-1121-Y2-A-010 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401924030 | ZPM2 | 2015-03-08 | 2015-03-08 | GAM- ALARM 2118 INTERBUS FAILURE | G97 / 90 / 10 - Patton | WF-US-0PA-1121-Y2-A-010 | CLSD PCNF GMPS NMAT SETC | COMP | CARROYO01
401925776 | ZPM2 | 2015-03-10 | 2015-03-10 | GAM-ALARM 410 OGS | G97 / 90 / 11 - Patton | WF-US-0PA-1121-Y1-A-001 | REL PCNF NMAT SETC | ACCE | OSB_RFC01

## Hours (labor)
Order | Type | OT Description | WO Description | Turbine Number | Start Date | Sta. Hour | End Date | End Hour | Work Hours | Work type | Pers.No. | Personnel Name | User Statu | Subc | Name 1 | Work description | Posting date
401862384 | ZPM2 | GAM-804 ALARM DIFFERENCE IN BLADES / F | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-01-02 | 12:00:00 | 2015-01-02 | 14:15:00 | 2.25 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES / FOUND BLADE A PROP VALVE NOT FUNCTIONING AND REPLACED / ROBERT COOK 2000541 IS PATTO | 2015-01-02
401862384 | ZPM2 | GAM-804 ALARM DIFFERENCE IN BLADES / F | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-01-02 | 12:00:00 | 2015-01-02 | 14:04:00 | 2.07 | Op regular hours | 2001546 | PATTON TECHNICIAN | Complete | 500504 | GAMESA WIND US | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES / FOUND BLADE A PROP VALVE NOT FUNCTIONING AND REPLACED / ROBERT COOK 2000541 IS PATTO | 2015-01-02
401863233 | ZPM2 | GAM-PLANNED CORRECTIVE / ON MAINTENANC | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-01-06 | 08:00:00 | 2015-01-06 | 11:30:00 | 3.5 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / FOUND GEARBOX PUMP LEAKING DURING MAINTENANCE / CHANGED PUMP ASSEMBLY | 2015-01-06
401879734 | ZPM2 | Gam- GOT ALARM 2118 INERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-01-23 | 07:15:00 | 2015-01-23 | 08:00:00 | 0.75 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM- ALARM 2118 INERBUS FAILURE REPLACED CARD | 2015-01-23
401879734 | ZPM2 | Gam- GOT ALARM 2118 INERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-01-23 | 07:15:00 | 2015-01-23 | 08:00:00 | 0.75 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM- ALARM 2118 INERBUS FAILURE REPLACED CARD | 2015-01-23
401924030 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-03-08 | 06:50:00 | 2015-03-08 | 11:28:00 | 4.63 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND A LTK BAD REPLACED IT | 2015-03-08
401924030 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-03-08 | 06:50:00 | 2015-03-08 | 11:30:00 | 4.67 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND A LTK BAD REPLACED IT | 2015-03-08
401925776 | ZPM2 | GAM-ALARM 410 OGS | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-03-10 | 11:30:00 | 2015-03-10 | 11:42:00 | 0.2 | Op regular hours | 2000507 | Nathan Paul Palko | Accepted | 500504 | GAMESA WIND US | 2000541: RESET | 2015-03-10
401863233 | ZPM2 | GAM-PLANNED CORRECTIVE / ON MAINTENANC | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-01-06 | 08:00:00 | 2015-01-06 | 11:30:00 | 3.5 | Op regular hours | 2001546 | PATTON TECHNICIAN | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / FOUND GEARBOX PUMP LEAKING DURING MAINTENANCE / CHANGED PUMP ASSEMBLY | 2015-01-06
401863238 | ZPM2 | GAM-PLANNED CORRECTIVE / NOTICED LEAKIN | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-06 | 12:30:00 | 2015-01-06 | 14:15:00 | 1.75 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / NOTICIED LEAKING GREASE FITTING WHILE FIXING TURBINE ON CALL OUT / FIXED FITTING AND CLEANED G | 2015-01-06
401863238 | ZPM2 | GAM-PLANNED CORRECTIVE / NOTICED LEAKIN | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-06 | 12:30:00 | 2015-01-06 | 14:15:00 | 1.75 | Op regular hours | 2001546 | PATTON TECHNICIAN | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / NOTICIED LEAKING GREASE FITTING WHILE FIXING TURBINE ON CALL OUT / FIXED FITTING AND CLEANED G | 2015-01-06
401865662 | ZPM2 | GAM-5203 ALARM HEATING/COOLANT THERMAL M | WO Maintenance Small corrective | G97 / 78 / 13 - Patton | 2015-01-08 | 09:00:00 | 2015-01-08 | 10:00:00 | 1 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-5203 ALARM HEATING/COOLANT THERMAL MAGNETIC FAILURE / FOUND TRIPPED BREAKER, TESTED AND RESET / ROBERT COOK 2000541 IS | 2015-01-08
401865662 | ZPM2 | GAM-5203 ALARM HEATING/COOLANT THERMAL M | WO Maintenance Small corrective | G97 / 78 / 13 - Patton | 2015-01-08 | 09:00:00 | 2015-01-08 | 10:00:00 | 1 | Op regular hours | 2001546 | PATTON TECHNICIAN | Complete | 500504 | GAMESA WIND US | 2001212: GAM-5203 ALARM HEATING/COOLANT THERMAL MAGNETIC FAILURE / FOUND TRIPPED BREAKER, TESTED AND RESET / ROBERT COOK 2000541 IS | 2015-01-08
401868950 | ZPM2 | GAM-426 ALARM SPEED READING ERROR / WE | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-12 | 10:30:00 | 2015-01-12 | 11:05:00 | 0.58 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READING ERROR / INSPECTED SENSORS FOUND THEM DIRTY AND CLEANED THEM | 2015-01-12
401868950 | ZPM2 | GAM-426 ALARM SPEED READING ERROR / WE | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-12 | 10:30:00 | 2015-01-12 | 11:05:00 | 0.58 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READING ERROR / INSPECTED SENSORS FOUND THEM DIRTY AND CLEANED THEM | 2015-01-12
401868950 | ZPM2 | GAM-426 ALARM SPEED READING ERROR / WE | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-12 | 10:30:00 | 2015-01-12 | 11:05:00 | 0.58 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READING ERROR / INSPECTED SENSORS FOUND THEM DIRTY AND CLEANED THEM | 2015-01-12
401868953 | ZPM2 | GAM-426 ALARM SPEED READ ERROR / CHANG | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-12 | 11:15:00 | 2015-01-12 | 12:30:00 | 1.25 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READ ERROR / CHANGED SENSOR | 2015-01-12
401868953 | ZPM2 | GAM-426 ALARM SPEED READ ERROR / CHANG | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-12 | 11:15:00 | 2015-01-12 | 12:30:00 | 1.25 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READ ERROR / CHANGED SENSOR | 2015-01-12
401868953 | ZPM2 | GAM-426 ALARM SPEED READ ERROR / CHANG | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-12 | 11:15:00 | 2015-01-12 | 12:30:00 | 1.25 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM-426 ALARM SPEED READ ERROR / CHANGED SENSOR | 2015-01-12
401908769 | ZPM2 | GAM- ALARM 2102 PLC MODULE FAILURE | WO Maintenance Small corrective | G97 / 90 / 16 - Patton | 2015-02-18 | 17:54:00 | 2015-02-18 | 21:00:00 | 3.1 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: WHILE TROUBLE SHOOTING FOUND PROBLEM WITH THE LTK | 2015-02-18
401908769 | ZPM2 | GAM- ALARM 2102 PLC MODULE FAILURE | WO Maintenance Small corrective | G97 / 90 / 16 - Patton | 2015-02-18 | 17:54:00 | 2015-02-18 | 21:00:00 | 3.1 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: WHILE TROUBLE SHOOTING FOUND PROBLEM WITH THE LTK | 2015-02-18
401914836 | ZPM2 | GAM- 2102 PLC MODULE FAILURE REPLACE THE | WO Maintenance Small corrective | G97 / 90 / 16 - Patton | 2015-02-26 | 08:50:00 | 2015-02-26 | 09:53:00 | 1.05 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: DURING THE CLIENTS INSPECTION WE REPLACED THE MULTIPLEXORA | 2015-03-01
401914836 | ZPM2 | GAM- 2102 PLC MODULE FAILURE REPLACE THE | WO Maintenance Small corrective | G97 / 90 / 16 - Patton | 2015-02-26 | 08:50:00 | 2015-02-26 | 09:53:00 | 1.05 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: DURING THE CLIENTS INSPECTION WE REPLACED THE MULTIPLEXORA | 2015-03-01
401916174 | ZPM2 | GAM- WARNING 422 GEARBOX THERMAL | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-02-27 | 08:30:00 | 2015-02-27 | 12:25:00 | 3.92 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: FOUND THAT THERE WAS LOOSE NUT WITH WIRE WICH WAS NOT GIVING A GOOD SIGNAL | 2015-03-01
401916174 | ZPM2 | GAM- WARNING 422 GEARBOX THERMAL | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-02-27 | 08:30:00 | 2015-02-27 | 12:25:00 | 3.92 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: FOUND THAT THERE WAS LOOSE NUT WITH WIRE WICH WAS NOT GIVING A GOOD SIGNAL | 2015-03-01
401925776 | ZPM2 | GAM-ALARM 410 OGS | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-03-10 | 11:30:00 | 2015-03-10 | 11:42:00 | 0.2 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Accepted | 500504 | GAMESA WIND US | 2000541: RESET | 2015-03-10
401868943 | ZPM2 | GAM-205 ALARM LOW HG OIL / WENT UP AND | WO Maintenance Small corrective | G97 / 90 / 7 - Patton | 2015-01-12 | 09:15:00 | 2015-01-12 | 10:30:00 | 1.25 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-205 ALARM HG OIL LEVEL / WENT UP ADDED 8L OIL AND INSPECTED TURBINE FOR LEAKS | 2015-01-12
401876454 | ZPM2 | GAM- PUT THE INSULATED CABLE BACK ON | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-20 | 08:45:00 | 2015-01-20 | 09:00:00 | 0.25 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: installed shielding cable | 2015-01-20
401876454 | ZPM2 | GAM- PUT THE INSULATED CABLE BACK ON | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-20 | 08:45:00 | 2015-01-20 | 09:00:00 | 0.25 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: installed shielding cable | 2015-01-20
401891052 | ZPM2 | GAM-REPLACE BAD 08 FAN | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-02-03 | 10:20:00 | 2015-02-03 | 11:10:00 | 0.83 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: replaced bad FG008 fan | 2015-02-03
401892513 | ZPM2 | GAM- ALARM 5238 ERROR IN PHASE T | WO Maintenance Small corrective | G97 / 90 / 2 - Patton | 2015-02-04 | 11:30:00 | 2015-02-04 | 15:00:00 | 3.5 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: GAM-5238 ALARM ERROR PHASE T PF INVERTER / UPON INSPECTION FOUND SLIP RING DIRTY AND BRUSHES WORN / DECIDED TO DO PREVEN | 2015-02-04
401892513 | ZPM2 | GAM- ALARM 5238 ERROR IN PHASE T | WO Maintenance Small corrective | G97 / 90 / 2 - Patton | 2015-02-04 | 11:15:00 | 2015-02-04 | 15:15:00 | 4 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: GAM-5238 ALARM ERROR PHASE T PF INVERTER / UPON INSPECTION FOUND SLIP RING DIRTY AND BRUSHES WORN / DECIDED TO DO PREVEN | 2015-02-04
401899235 | ZPM2 | GAM- preventive slip ring maintance | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-10 | 11:45:00 | 2015-02-10 | 14:45:00 | 3 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED SLIPRING AND CLEANED TO PREVENT PROBLEMS | 2015-02-10
401899235 | ZPM2 | GAM- preventive slip ring maintance | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-10 | 11:45:00 | 2015-02-10 | 14:45:00 | 3 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED SLIPRING AND CLEANED TO PREVENT PROBLEMS | 2015-02-10
401904907 | ZPM2 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 21:45:00 | 2015-02-16 | 23:03:00 | 1.3 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND A LOSSE WIRE ON BLOCK X10 | 2015-02-16
401904907 | ZPM2 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 21:45:00 | 2015-02-16 | 23:00:00 | 1.25 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND A LOSSE WIRE ON BLOCK X10 | 2015-02-16
401904939 | ZPM2 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 16:26:00 | 2015-02-16 | 18:29:00 | 2.05 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 SWAPED KR919 AND THE KR920 TO SEE IF THE ALARM MOVED | 2015-02-16
401904939 | ZPM2 | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 16:26:00 | 2015-02-16 | 18:29:00 | 2.05 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 SWAPED KR919 AND THE KR920 TO SEE IF THE ALARM MOVED | 2015-02-16
401905340 | ZPM2 | GAM- ALARM 205 HG OIL LOW | WO Maintenance Small corrective | G97 / 90 / 12 - Patton | 2015-02-16 | 14:15:00 | 2015-02-16 | 14:38:00 | 0.38 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | GAM-205 ALARM LOW OIL LEVEL HG / ADDED OIL | 2015-02-16
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-20 | 07:00:00 | 2015-02-20 | 22:00:00 | 15 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-20
401912083 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 16:30:00 | 2015-02-21 | 19:29:00 | 2.98 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND THAT PART WAS BAD FROM WAREHOUSE SELF | 2015-02-21
401924002 | ZPM2 | GAM- ALARM 103 CW MOTOR FAILURE | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-03-06 | 08:45:00 | 2015-03-06 | 09:13:00 | 0.47 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: Alarm 103 WENT TO CHECK FOR A BROKEN YAW GEAR NOTHING FOUND WRONG | 2015-03-06
401924018 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-03-06 | 10:30:00 | 2015-03-06 | 11:40:00 | 1.17 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 CANGEDMTHE PT CARD IN THE HUB | 2015-03-06
401924018 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-03-06 | 10:30:00 | 2015-03-06 | 11:40:00 | 1.17 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 CANGEDMTHE PT CARD IN THE HUB | 2015-03-06
500727770 | ZPM1 | GAM-SLIP RING MAINTENACE | WO Preventive maintenance | G97 / 90 / 12 - Patton | 2015-02-11 | 11:45:00 | 2015-02-11 | 15:00:00 | 3.25 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED THE SLIP RING AND CHANGED BRUSHES TO PREVENT PROBLEMS | 2015-02-11
500727770 | ZPM1 | GAM-SLIP RING MAINTENACE | WO Preventive maintenance | G97 / 90 / 12 - Patton | 2015-02-11 | 11:45:00 | 2015-02-11 | 15:00:00 | 3.25 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED THE SLIP RING AND CHANGED BRUSHES TO PREVENT PROBLEMS | 2015-02-11
401864077 | ZPM2 | GAM-PLANNED CORRECTIVE / DISCOVERED EXCE | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-06 | 13:00:00 | 2015-01-06 | 14:30:00 | 1.5 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / DISCOVERED EXCESS GREASE ON BLADE BEARINGS DURING CALL OUT / CLEANED AND INSPECTED BLADE BEARING | 2015-01-06
401864077 | ZPM2 | GAM-PLANNED CORRECTIVE / DISCOVERED EXCE | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-06 | 13:00:00 | 2015-01-06 | 14:30:00 | 1.5 | Op regular hours | 350800 | Michael Van Williams | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / DISCOVERED EXCESS GREASE ON BLADE BEARINGS DURING CALL OUT / CLEANED AND INSPECTED BLADE BEARING | 2015-01-06
401868943 | ZPM2 | GAM-205 ALARM LOW HG OIL / WENT UP AND | WO Maintenance Small corrective | G97 / 90 / 7 - Patton | 2015-01-12 | 09:15:00 | 2015-01-12 | 10:30:00 | 1.25 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-205 ALARM HG OIL LEVEL / WENT UP ADDED 8L OIL AND INSPECTED TURBINE FOR LEAKS | 2015-01-12
401868943 | ZPM2 | GAM-205 ALARM LOW HG OIL / WENT UP AND | WO Maintenance Small corrective | G97 / 90 / 7 - Patton | 2015-01-12 | 09:15:00 | 2015-01-12 | 10:30:00 | 1.25 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM-205 ALARM HG OIL LEVEL / WENT UP ADDED 8L OIL AND INSPECTED TURBINE FOR LEAKS | 2015-01-12
401872279 | ZPM2 | GAM-replace inductive sensor bracket | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-14 | 10:49:00 | 2015-01-14 | 13:10:00 | 2.35 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: turbine was giving intermitent 426 alarms found sensor bracket to be bent which was causing the fault.changed bracket. also | 2015-01-14
401872279 | ZPM2 | GAM-replace inductive sensor bracket | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-14 | 10:49:00 | 2015-01-14 | 13:10:00 | 2.35 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: turbine was giving intermitent 426 alarms found sensor bracket to be bent which was causing the fault.changed bracket. also | 2015-01-14
401872279 | ZPM2 | GAM-replace inductive sensor bracket | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-01-14 | 10:49:00 | 2015-01-14 | 12:00:00 | 1.18 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: turbine was giving intermitent 426 alarms found sensor bracket to be bent which was causing the fault.changed bracket. also | 2015-01-14
401872286 | ZPM2 | GAM-nacelle inspection | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-14 | 14:00:00 | 2015-01-14 | 15:00:00 | 1 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: went up tower to inspect overall nacelle putting emphasis on locating possible roof leaks. none found | 2015-01-14
401872286 | ZPM2 | GAM-nacelle inspection | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-14 | 14:00:00 | 2015-01-14 | 15:00:00 | 1 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: went up tower to inspect overall nacelle putting emphasis on locating possible roof leaks. none found | 2015-01-14
401877674 | ZPM2 | GAM-327 LTK CONFIRMATION FAILURE | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-21 | 09:40:00 | 2015-01-21 | 11:50:00 | 2.17 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: replaced actuators for ltk louvers | 2015-01-21
401877674 | ZPM2 | GAM-327 LTK CONFIRMATION FAILURE | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-01-21 | 09:40:00 | 2015-01-21 | 11:50:00 | 2.17 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: replaced actuators for ltk louvers | 2015-01-21
401884474 | ZPM2 | GAM- ALARM 2198 TEMP MEASURE MOD | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-01-28 | 10:37:00 | 2015-01-28 | 12:38:00 | 2.02 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: CHANGED THE PT100 SENSOR | 2015-01-28
401884474 | ZPM2 | GAM- ALARM 2198 TEMP MEASURE MOD | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-01-28 | 10:37:00 | 2015-01-28 | 12:38:00 | 2.02 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CHANGED THE PT100 SENSOR | 2015-01-28
401886608 | ZPM2 | GAM- ALARM 410 OGS | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-23 | 10:00:00 | 2015-01-23 | 11:00:00 | 1 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: CHANGED THE OGS SENSOR | 2015-02-01
401886608 | ZPM2 | GAM- ALARM 410 OGS | WO Maintenance Small corrective | G97 / 78 / 3 - Patton | 2015-01-23 | 10:00:00 | 2015-01-23 | 11:00:00 | 1 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CHANGED THE OGS SENSOR | 2015-02-01
401891052 | ZPM2 | GAM-REPLACE BAD 08 FAN | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-02-03 | 10:20:00 | 2015-02-03 | 11:10:00 | 0.83 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: replaced bad FG008 fan | 2015-02-03
401891052 | ZPM2 | GAM-REPLACE BAD 08 FAN | WO Maintenance Small corrective | G97 / 90 / 10 - Patton | 2015-02-03 | 10:20:00 | 2015-02-03 | 11:10:00 | 0.83 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: replaced bad FG008 fan | 2015-02-03
401891070 | ZPM2 | GAM-troubleshoot low fiber quality | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-02-03 | 11:45:00 | 2015-02-03 | 12:25:00 | 0.67 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: trouble shoot low fiber quality replaced cab 2 header warning went away | 2015-02-03
401891070 | ZPM2 | GAM-troubleshoot low fiber quality | WO Maintenance Small corrective | G97 / 90 / 8 - Patton | 2015-02-03 | 11:45:00 | 2015-02-03 | 12:25:00 | 0.67 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: trouble shoot low fiber quality replaced cab 2 header warning went away | 2015-02-03
401891906 | ZPM2 | GAM-326 ALARM LTK FAILURE / TRIPPED BR | WO Maintenance Small corrective | G97 / 90 / 5 - Patton | 2015-02-03 | 13:15:00 | 2015-02-03 | 13:45:00 | 0.5 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM-326 ALARM LTK FAILURE / FOUND FG406 BREAKER TRIPPED AMPEREAGE WAS LOW / ADJUSTED HEATER BREAKERS TO 5amps | 2015-02-03
401891906 | ZPM2 | GAM-326 ALARM LTK FAILURE / TRIPPED BR | WO Maintenance Small corrective | G97 / 90 / 5 - Patton | 2015-02-03 | 13:15:00 | 2015-02-03 | 13:45:00 | 0.5 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-326 ALARM LTK FAILURE / FOUND FG406 BREAKER TRIPPED AMPEREAGE WAS LOW / ADJUSTED HEATER BREAKERS TO 5amps | 2015-02-03
401892513 | ZPM2 | GAM- ALARM 5238 ERROR IN PHASE T | WO Maintenance Small corrective | G97 / 90 / 2 - Patton | 2015-02-04 | 11:30:00 | 2015-02-04 | 15:07:00 | 3.62 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: GAM-5238 ALARM ERROR PHASE T PF INVERTER / UPON INSPECTION FOUND SLIP RING DIRTY AND BRUSHES WORN / DECIDED TO DO PREVEN | 2015-02-04
401893314 | ZPM2 | GAM-700 ALARM PLC/CONVERTER COMM FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-04 | 05:45:00 | 2015-02-04 | 06:30:00 | 0.75 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-700 PLC/CONVERTER COMM ERROR / CALL OUT LOCAL RESET | 2015-02-04
401893314 | ZPM2 | GAM-700 ALARM PLC/CONVERTER COMM FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-04 | 05:45:00 | 2015-02-04 | 06:30:00 | 0.75 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-700 PLC/CONVERTER COMM ERROR / CALL OUT LOCAL RESET | 2015-02-04
401896947 | ZPM2 | GAM-PLANNED CORRECTIVE / PREVENTATIVE | WO Maintenance Small corrective | G97 / 78 / 13 - Patton | 2015-02-09 | 07:30:00 | 2015-02-09 | 11:30:00 | 4 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / PREVENTATIVE SLIP RING CLEANING / CLEANED EXCESS GREASE IN HUB | 2015-02-09
401896947 | ZPM2 | GAM-PLANNED CORRECTIVE / PREVENTATIVE | WO Maintenance Small corrective | G97 / 78 / 13 - Patton | 2015-02-09 | 07:30:00 | 2015-02-09 | 11:30:00 | 4 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / PREVENTATIVE SLIP RING CLEANING / CLEANED EXCESS GREASE IN HUB | 2015-02-09
401896947 | ZPM2 | GAM-PLANNED CORRECTIVE / PREVENTATIVE | WO Maintenance Small corrective | G97 / 78 / 13 - Patton | 2015-02-09 | 07:30:00 | 2015-02-09 | 11:30:00 | 4 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2001212: GAM-PLANNED CORRECTIVE / PREVENTATIVE SLIP RING CLEANING / CLEANED EXCESS GREASE IN HUB | 2015-02-09
401899235 | ZPM2 | GAM- preventive slip ring maintance | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-10 | 11:45:00 | 2015-02-10 | 14:45:00 | 3 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED SLIPRING AND CLEANED TO PREVENT PROBLEMS | 2015-02-10
401899267 | ZPM2 | GAM- preventive slip ring maintance | WO Maintenance Small corrective | G97 / 90 / 7 - Patton | 2015-02-10 | 08:00:00 | 2015-02-10 | 11:30:00 | 3.5 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED SLIP RING AND CHANGED BRUCHES TO PREVENT PROBLEMS | 2015-02-10
401904978 | ZPM2 | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-15 | 18:53:00 | 2015-02-15 | 23:30:00 | 4.62 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 FOUND A BREAKER TRIPPED IN TOP CABINET | 2015-02-15
401904978 | ZPM2 | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-15 | 18:53:00 | 2015-02-15 | 23:30:00 | 4.62 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 FOUND A BREAKER TRIPPED IN TOP CABINET | 2015-02-15
401904978 | ZPM2 | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 07:30:00 | 2015-02-16 | 10:15:00 | 2.75 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 FOUND A BREAKER TRIPPED IN TOP CABINET | 2015-02-16
401904978 | ZPM2 | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-16 | 07:30:00 | 2015-02-16 | 10:15:00 | 2.75 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 FOUND A BREAKER TRIPPED IN TOP CABINET | 2015-02-16
401905340 | ZPM2 | GAM- ALARM 205 HG OIL LOW | WO Maintenance Small corrective | G97 / 90 / 12 - Patton | 2015-02-16 | 14:15:00 | 2015-02-16 | 14:38:00 | 0.38 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | GAM-205 ALARM LOW OIL LEVEL HG / ADDED OIL | 2015-02-16
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-15 | 07:40:00 | 2015-02-15 | 16:30:00 | 8.83 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-15
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-15 | 07:40:00 | 2015-02-15 | 16:30:00 | 8.83 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-15
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-16 | 07:00:00 | 2015-02-16 | 16:00:00 | 9 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-16
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-16 | 07:00:00 | 2015-02-16 | 16:00:00 | 9 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-16
401912083 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 16:30:00 | 2015-02-21 | 19:29:00 | 2.98 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND THAT PART WAS BAD FROM WAREHOUSE SELF | 2015-02-21
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-19 | 10:00:00 | 2015-02-19 | 17:00:00 | 7 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-19
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-17 | 07:00:00 | 2015-02-17 | 16:30:00 | 9.5 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-17
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-17 | 07:00:00 | 2015-02-17 | 16:30:00 | 9.5 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-17
401912085 | ZPM2 | CLEANED UP AND LOWER TOOLS | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-24 | 08:45:00 | 2015-02-24 | 10:55:00 | 2.17 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED UP AND LOWER OLD PARTS AND TOOLS FASTEN THE DOORA TO TOP CABINET | 2015-02-24
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-20 | 07:00:00 | 2015-02-20 | 23:00:00 | 16 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-20
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-19 | 07:00:00 | 2015-02-19 | 15:00:00 | 8 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-19
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-19 | 07:00:00 | 2015-02-19 | 15:00:00 | 8 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-19
401912081 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 08:15:00 | 2015-02-21 | 10:00:00 | 1.75 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 AFTER TROUBLE SHHOTING FOUND THAT THE FOUR PACK AND HUB CARD WAS BAD | 2015-02-21
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-17 | 07:00:00 | 2015-02-17 | 15:30:00 | 8.5 | Op regular hours | 350800 | Michael Van Williams | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-17
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-18 | 10:00:00 | 2015-02-18 | 18:00:00 | 8 | Op regular hours | 350800 | Michael Van Williams | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-18
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-18 | 07:00:00 | 2015-02-18 | 20:00:00 | 13 | Op regular hours | 350800 | Michael Van Williams | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-18
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-20 | 07:00:00 | 2015-02-20 | 23:00:00 | 16 | Op regular hours | 350800 | Michael Van Williams | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-20
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-20 | 07:00:00 | 2015-02-20 | 22:00:00 | 15 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-20
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-21 | 15:50:00 | 2015-02-21 | 23:30:00 | 7.67 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-21
401912079 | ZPM2 | GAM- ALARM 426 SPEED READING ERROR | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-21 | 15:50:00 | 2015-02-21 | 23:30:00 | 7.67 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT | 2015-02-21
401912081 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 08:15:00 | 2015-02-21 | 10:00:00 | 1.75 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 AFTER TROUBLE SHHOTING FOUND THAT THE FOUR PACK AND HUB CARD WAS BAD | 2015-02-21
401912085 | ZPM2 | CLEANED UP AND LOWER TOOLS | WO Maintenance Small corrective | G97 / 90 / 4 - Patton | 2015-02-24 | 08:45:00 | 2015-02-24 | 10:55:00 | 2.17 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: CLEANED UP AND LOWER OLD PARTS AND TOOLS FASTEN THE DOORA TO TOP CABINET | 2015-02-24
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-17 | 07:00:00 | 2015-02-17 | 15:30:00 | 8.5 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-17
401912080 | ZPM2 | ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-20 | 23:00:00 | 2015-02-20 | 23:55:00 | 0.92 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 RESET | 2015-02-20
401912082 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 10:45:00 | 2015-02-21 | 14:59:00 | 4.23 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND THE LTK WORKING INPROPER | 2015-02-21
401912082 | ZPM2 | GAM- ALARM 2118 INTERBUS FAILURE | WO Maintenance Small corrective | G97 / 90 / 11 - Patton | 2015-02-21 | 10:45:00 | 2015-02-21 | 14:59:00 | 4.23 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 2118 FOUND THE LTK WORKING INPROPER | 2015-02-21
401912086 | ZPM2 | GAM- ALARM 1825 CICUIT BREAKER NO OK | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-02-18 | 07:00:00 | 2015-02-18 | 20:00:00 | 13 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT | 2015-02-18
401914298 | ZPM2 | GAM-ALARM 422 GEARBOX ADDITIONAL PUMP CI | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-02-25 | 09:15:00 | 2015-02-25 | 19:18:00 | 10.05 | Op regular hours | 2000541 | Robert Anthony Cook | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 422 FOUND THE AUX PUMP WAS BAD AND THE MAIN PUMP WAS BAD ALSO | 2015-03-01
401914298 | ZPM2 | GAM-ALARM 422 GEARBOX ADDITIONAL PUMP CI | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-02-25 | 09:15:00 | 2015-02-25 | 19:18:00 | 10.05 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Complete | 500504 | GAMESA WIND US | 2000541: ALARM 422 FOUND THE AUX PUMP WAS BAD AND THE MAIN PUMP WAS BAD ALSO | 2015-03-01
401919118 | ZPM2 | GAM- WARNING 422 GEARBOX FILTER PUMP THE | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-03-03 | 08:30:00 | 2015-03-03 | 12:04:00 | 3.57 | Op regular hours | 2000541 | Robert Anthony Cook | Accepted | 500504 | GAMESA WIND US | 2000541: WARNING 422 AFTER REPLACING THE PUMPS FOUND THAT BOTH HOSES WERE CRACKED AND LEAKING | 2015-03-03
401919118 | ZPM2 | GAM- WARNING 422 GEARBOX FILTER PUMP THE | WO Maintenance Small corrective | G97 / 90 / 6 - Patton | 2015-03-03 | 08:30:00 | 2015-03-03 | 12:04:00 | 3.57 | Op regular hours | 2001212 | KEVIN BARCLAY JOHNSON | Accepted | 500504 | GAMESA WIND US | 2000541: WARNING 422 AFTER REPLACING THE PUMPS FOUND THAT BOTH HOSES WERE CRACKED AND LEAKING | 2015-03-03
401924002 | ZPM2 | GAM- ALARM 103 CW MOTOR FAILURE | WO Maintenance Small corrective | G97 / 90 / 17 - Patton | 2015-03-06 | 08:45:00 | 2015-03-06 | 09:13:00 | 0.47 | Op regular hours | 2000507 | Nathan Paul Palko | Complete | 500504 | GAMESA WIND US | 2000541: Alarm 103 WENT TO CHECK FOR A BROKEN YAW GEAR NOTHING FOUND WRONG | 2015-03-06

## Stop Times
Order | Order Type | Plant | UserStatus | WO Description | Functional Location | Descriptn | FunctLocDescrip. | Start Date | Time | End date | Stop time | Total Stop | Remarks
401862384 | ZPM2 | 1320 | COMP | GAM-804 ALARM DIFFERENCE IN BLADES / F | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-01-02 | 06:50:00 | 2015-01-02 | 14:04:00 | 7:14:00 | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES / FOUND BLADE A PROP VALVE NOT FUNCTIONING AND REPLACED / ROBERT COOK 2000541 IS PATTO N TECHNICIAN
401863233 | ZPM2 | 1320 | COMP | GAM-PLANNED CORRECTIVE / ON MAINTENANC | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-01-06 | 08:02:00 | 2015-01-06 | 11:20:00 | 3:18:00 | 2001212: GAM-PLANNED CORRECTIVE / FOUND GEARBOX PUMP LEAKING DURING MAINTENANCE / CHANGED PUMP ASSEMBLY
401863238 | ZPM2 | 1320 | COMP | GAM-PLANNED CORRECTIVE / NOTICED LEAKIN | WF-US-0PA-1121-Y2-A-003 | Patton | G97 / 78 / 3 - Patton | 2015-01-06 | 12:30:00 | 2015-01-06 | 14:05:00 | 1:35:00 | 2001212: GAM-PLANNED CORRECTIVE / NOTICIED LEAKING GREASE FITTING WHILE FIXING TURBINE ON CALL OUT / FIXED FITTING AND CLEANED G REASE
401864077 | ZPM2 | 1320 | COMP | GAM-PLANNED CORRECTIVE / DISCOVERED EXCE | WF-US-0PA-1121-Y2-A-007 | Patton | G97 / 90 / 8 - Patton | 2015-01-06 | 13:12:00 | 2015-01-06 | 14:22:00 | 1:10:00 | 2001212: GAM-PLANNED CORRECTIVE / DISCOVERED EXCESS GREASE ON BLADE BEARINGS DURING CALL OUT / CLEANED AND INSPECTED BLADE BEARING
401865662 | ZPM2 | 1320 | COMP | GAM-5203 ALARM HEATING/COOLANT THERMAL M | WF-US-0PA-1121-Y1-A-003 | Patton | G97 / 78 / 13 - Patton | 2015-01-08 | 08:27:00 | 2015-01-08 | 09:59:00 | 1:32:00 | 2001212: GAM-5203 ALARM HEATING/COOLANT THERMAL MAGNETIC FAILURE / FOUND TRIPPED BREAKER, TESTED AND RESET / ROBERT COOK 2000541 IS PATTON TECHNICIAN.
401868943 | ZPM2 | 1320 | COMP | GAM-205 ALARM LOW HG OIL / WENT UP AND | WF-US-0PA-1121-Y2-A-011 | Patton | G97 / 90 / 7 - Patton | 2015-01-12 | 09:31:00 | 2015-01-12 | 10:17:00 | 0:46:00 | 2001212: GAM-205 ALARM HG OIL LEVEL / WENT UP ADDED 8L OIL AND INSPECTED TURBINE FOR LEAKS
401868950 | ZPM2 | 1320 | COMP | GAM-426 ALARM SPEED READING ERROR / WE | WF-US-0PA-1121-Y2-A-003 | Patton | G97 / 78 / 3 - Patton | 2015-01-12 | 10:33:00 | 2015-01-12 | 11:04:00 | 0:31:00 | 2001212: GAM-426 ALARM SPEED READING ERROR / INSPECTED SENSORS FOUND THEM DIRTY AND CLEANED THEM
401868953 | ZPM2 | 1320 | COMP | GAM-426 ALARM SPEED READ ERROR / CHANG | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-01-12 | 11:17:00 | 2015-01-12 | 12:24:00 | 1:07:00 | 2001212: GAM-426 ALARM SPEED READ ERROR / CHANGED SENSOR
401872279 | ZPM2 | 1320 | COMP | GAM-replace inductive sensor bracket | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-01-14 | 10:49:00 | 2015-01-14 | 13:06:00 | 2:17:00 | 2001212: turbine was giving intermitent 426 alarms found sensor bracket to be bent which was causing the fault.changed bracket. also tightened 2 roof bolt as we noticed possible leakage
401872286 | ZPM2 | 1320 | COMP | GAM-nacelle inspection | WF-US-0PA-1121-Y2-A-007 | Patton | G97 / 90 / 8 - Patton | 2015-01-14 | 14:08:00 | 2015-01-14 | 14:52:00 | 0:44:00 | 2001212: went up tower to inspect overall nacelle putting emphasis on locating possible roof leaks. none found
401876454 | ZPM2 | 1320 | COMP | GAM- PUT THE INSULATED CABLE BACK ON | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-01-20 | 08:46:00 | 2015-01-20 | 09:00:00 | 0:14:00 | 2001212: installed shielding cable
401877674 | ZPM2 | 1320 | COMP | GAM-327 LTK CONFIRMATION FAILURE | WF-US-0PA-1121-Y2-A-007 | Patton | G97 / 90 / 8 - Patton | 2015-01-21 | 09:45:00 | 2015-01-21 | 11:45:00 | 2:00:00 | 2001212: replaced actuators for ltk louvers
401879734 | ZPM2 | 1320 | COMP | Gam- GOT ALARM 2118 INERBUS FAILURE | WF-US-0PA-1121-Y2-A-006 | Patton | G97 / 90 / 6 - Patton | 2015-01-23 | 06:45:00 | 2015-01-23 | 08:00:00 | 1:15:00 | 2001212: GAM- ALARM 2118 INERBUS FAILURE REPLACED CARD
401884474 | ZPM2 | 1320 | COMP | GAM- ALARM 2198 TEMP MEASURE MOD | WF-US-0PA-1121-Y2-A-010 | Patton | G97 / 90 / 10 - Patton | 2015-01-28 | 10:35:00 | 2015-01-28 | 12:35:00 | 2:00:00 | 2000541: CHANGED THE PT100 SENSOR
401886608 | ZPM2 | 1320 | COMP | GAM- ALARM 410 OGS | WF-US-0PA-1121-Y2-A-003 | Patton | G97 / 78 / 3 - Patton | 2015-01-23 | 10:00:00 | 2015-01-23 | 11:00:00 | 1:00:00 | 2000541: CHANGED THE OGS SENSOR
401891052 | ZPM2 | 1320 | COMP | GAM-REPLACE BAD 08 FAN | WF-US-0PA-1121-Y2-A-010 | Patton | G97 / 90 / 10 - Patton | 2015-02-03 | 10:27:00 | 2015-02-03 | 11:06:00 | 0:39:00 | 2001212: replaced bad FG008 fan
401891070 | ZPM2 | 1320 | COMP | GAM-troubleshoot low fiber quality | WF-US-0PA-1121-Y2-A-007 | Patton | G97 / 90 / 8 - Patton | 2015-02-03 | 11:49:00 | 2015-02-03 | 12:20:00 | 0:31:00 | 2001212: trouble shoot low fiber quality replaced cab 2 header warning went away
401891906 | ZPM2 | 1320 | COMP | GAM-326 ALARM LTK FAILURE / TRIPPED BR | WF-US-0PA-1121-Y2-A-005 | Patton | G97 / 90 / 5 - Patton | 2015-02-03 | 13:18:00 | 2015-02-03 | 13:42:00 | 0:24:00 | 2001212: GAM-326 ALARM LTK FAILURE / FOUND FG406 BREAKER TRIPPED AMPEREAGE WAS LOW / ADJUSTED HEATER BREAKERS TO 5amps
401892513 | ZPM2 | 1320 | COMP | GAM- ALARM 5238 ERROR IN PHASE T | WF-US-0PA-1121-Y2-A-002 | Patton | G97 / 90 / 2 - Patton | 2015-02-04 | 11:15:00 | 2015-02-04 | 15:07:00 | 3:52:00 | 2000541: GAM-5238 ALARM ERROR PHASE T PF INVERTER / UPON INSPECTION FOUND SLIP RING DIRTY AND BRUSHES WORN / DECIDED TO DO PREVEN TATIVE ON SLIP RING
401893314 | ZPM2 | 1320 | COMP | GAM-700 ALARM PLC/CONVERTER COMM FAILURE | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-02-04 | 03:28:00 | 2015-02-04 | 06:25:00 | 2:57:00 | 2001212: GAM-700 PLC/CONVERTER COMM ERROR / CALL OUT LOCAL RESET
401896947 | ZPM2 | 1320 | COMP | GAM-PLANNED CORRECTIVE / PREVENTATIVE | WF-US-0PA-1121-Y1-A-003 | Patton | G97 / 78 / 13 - Patton | 2015-02-09 | 07:41:00 | 2015-02-09 | 11:21:00 | 3:40:00 | 2001212: GAM-PLANNED CORRECTIVE / PREVENTATIVE SLIP RING CLEANING / CLEANED EXCESS GREASE IN HUB
401899235 | ZPM2 | 1320 | COMP | GAM- preventive slip ring maintance | WF-US-0PA-1121-Y2-A-004 | Patton | G97 / 90 / 4 - Patton | 2015-02-10 | 11:45:00 | 2015-02-10 | 14:45:00 | 3:00:00 | 2000541: CLEANED SLIPRING AND CLEANED TO PREVENT PROBLEMS
401899267 | ZPM2 | 1320 | COMP | GAM- preventive slip ring maintance | WF-US-0PA-1121-Y2-A-011 | Patton | G97 / 90 / 7 - Patton | 2015-02-10 | 08:00:00 | 2015-02-10 | 11:30:00 | 3:30:00 | 2000541: CLEANED SLIP RING AND CHANGED BRUCHES TO PREVENT PROBLEMS
401904907 | ZPM2 | 1320 | COMP | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-02-16 | 21:45:00 | 2015-02-16 | 23:03:00 | 1:18:00 | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND A LOSSE WIRE ON BLOCK X10
401904939 | ZPM2 | 1320 | COMP | GAM- ALARM 1825 CIRCUIT BREAKERS NOT OK | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-02-16 | 16:25:00 | 2015-02-16 | 18:25:00 | 2:00:00 | 2000541: ALARM 1825 SWAPED KR919 AND THE KR920 TO SEE IF THE ALARM MOVED
401904978 | ZPM2 | 1320 | COMP | GAM- ALARM 1825 CIRUIT BREAKERS NOT OK | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-02-15 | 18:53:00 | 2015-02-16 | 10:15:00 | 15:22:00 | 2000541: ALARM 1825 FOUND A BREAKER TRIPPED IN TOP CABINET
401905340 | ZPM2 | 1320 | COMP | GAM- ALARM 205 HG OIL LOW | WF-US-0PA-1121-Y1-A-002 | Patton | G97 / 90 / 12 - Patton | 2015-02-16 | 13:05:00 | 2015-02-16 | 14:38:00 | 1:33:00 | GAM-205 ALARM LOW OIL LEVEL HG / ADDED OIL
401908769 | ZPM2 | 1320 | COMP | GAM- ALARM 2102 PLC MODULE FAILURE | WF-US-0PA-1121-Y2-A-012 | Patton | G97 / 90 / 16 - Patton | 2015-02-18 | 16:28:00 | 2015-02-18 | 21:00:00 | 4:32:00 | 2000541: WHILE TROUBLE SHOOTING FOUND PROBLEM WITH THE LTK
401912079 | ZPM2 | 1320 | COMP | GAM- ALARM 426 SPEED READING ERROR | WF-US-0PA-1121-Y2-A-004 | Patton | G97 / 90 / 4 - Patton | 2015-02-15 | 05:13:00 | 2015-02-21 | 22:37:00 | 161:24:00 | 2000541: ALARM 426 FOUND THE ZERO MAX FLEW APART HIT THE TOP CABINET HIT THE TOP OF NACELL HIT THE TOP LOUVER VENT HIT THE LOCK OUT PUMP AND LANDED BY THE HYDRALIC UNIT WITH OUT HARM
401912080 | ZPM2 | 1320 | COMP | ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-02-20 | 23:51:00 | 2015-02-20 | 23:53:00 | 0:02:00 | 2000541: ALARM 2118 RESET
401912081 | ZPM2 | 1320 | COMP | GAM- ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-02-20 | 00:47:00 | 2015-02-20 | 10:06:00 | 9:19:00 | 2000541: ALARM 2118 AFTER TROUBLE SHHOTING FOUND THAT THE FOUR PACK AND HUB CARD WAS BAD
401912082 | ZPM2 | 1320 | COMP | GAM- ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-02-21 | 11:15:00 | 2015-02-21 | 14:55:00 | 3:40:00 | 2000541: ALARM 2118 FOUND THE LTK WORKING INPROPER
401912083 | ZPM2 | 1320 | COMP | GAM- ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-02-21 | 17:09:00 | 2015-02-21 | 19:29:00 | 2:20:00 | 2000541: ALARM 2118 FOUND THAT PART WAS BAD FROM WAREHOUSE SELF
401912085 | ZPM2 | 1320 | COMP | CLEANED UP AND LOWER TOOLS | WF-US-0PA-1121-Y2-A-004 | Patton | G97 / 90 / 4 - Patton | 2015-02-24 | 08:55:00 | 2015-02-24 | 10:55:00 | 2:00:00 | 2000541: CLEANED UP AND LOWER OLD PARTS AND TOOLS FASTEN THE DOORA TO TOP CABINET
401912086 | ZPM2 | 1320 | COMP | GAM- ALARM 1825 CICUIT BREAKER NO OK | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-02-17 | 15:42:00 | 2015-02-20 | 21:59:00 | 78:17:00 | 2000541: ALARM 1825 AFTER TROUBLE SHOOTING FOUND WABT HAD A BROKEN WIRE IN IT
401914298 | ZPM2 | 1320 | COMP | GAM-ALARM 422 GEARBOX ADDITIONAL PUMP CI | WF-US-0PA-1121-Y2-A-006 | Patton | G97 / 90 / 6 - Patton | 2015-02-25 | 09:25:00 | 2015-02-25 | 19:18:00 | 9:53:00 | 2000541: ALARM 422 FOUND THE AUX PUMP WAS BAD AND THE MAIN PUMP WAS BAD ALSO
401914836 | ZPM2 | 1320 | COMP | GAM- 2102 PLC MODULE FAILURE REPLACE THE | WF-US-0PA-1121-Y2-A-012 | Patton | G97 / 90 / 16 - Patton | 2015-02-26 | 08:53:00 | 2015-02-26 | 09:53:00 | 1:00:00 | 2000541: DURING THE CLIENTS INSPECTION WE REPLACED THE MULTIPLEXORA
401916174 | ZPM2 | 1320 | COMP | GAM- WARNING 422 GEARBOX THERMAL | WF-US-0PA-1121-Y2-A-006 | Patton | G97 / 90 / 6 - Patton | 2015-02-27 | 08:46:00 | 2015-02-27 | 12:25:00 | 3:39:00 | 2000541: FOUND THAT THERE WAS LOOSE NUT WITH WIRE WICH WAS NOT GIVING A GOOD SIGNAL
401919118 | ZPM2 | 1320 | ACCE | GAM- WARNING 422 GEARBOX FILTER PUMP THE | WF-US-0PA-1121-Y2-A-006 | Patton | G97 / 90 / 6 - Patton | 2015-03-03 | 08:45:00 | 2015-03-03 | 12:05:00 | 3:20:00 | 2000541: WARNING 422 AFTER REPLACING THE PUMPS FOUND THAT BOTH HOSES WERE CRACKED AND LEAKING
401924002 | ZPM2 | 1320 | COMP | GAM- ALARM 103 CW MOTOR FAILURE | WF-US-0PA-1121-Y2-A-009 | Patton | G97 / 90 / 17 - Patton | 2015-03-06 | 08:50:00 | 2015-03-06 | 09:13:00 | 0:23:00 | 2000541: Alarm 103 WENT TO CHECK FOR A BROKEN YAW GEAR NOTHING FOUND WRONG
401924018 | ZPM2 | 1320 | COMP | GAM- ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y2-A-010 | Patton | G97 / 90 / 10 - Patton | 2015-03-06 | 10:37:00 | 2015-03-06 | 11:40:00 | 1:03:00 | 2000541: ALARM 2118 CANGEDMTHE PT CARD IN THE HUB
401924030 | ZPM2 | 1320 | COMP | GAM- ALARM 2118 INTERBUS FAILURE | WF-US-0PA-1121-Y2-A-010 | Patton | G97 / 90 / 10 - Patton | 2015-03-08 | 06:13:00 | 2015-03-08 | 11:28:00 | 5:15:00 | 2000541: ALARM 2118 FOUND A LTK BAD REPLACED IT
401925776 | ZPM2 | 1320 | ACCE | GAM-ALARM 410 OGS | WF-US-0PA-1121-Y1-A-001 | Patton | G97 / 90 / 11 - Patton | 2015-03-10 | 11:41:00 | 2015-03-10 | 11:42:00 | 0:01:00 | 2000541: RESET
500727770 | ZPM1 | 1320 | COMP | GAM-SLIP RING MAINTENACE | WF-US-0PA-1121-Y1-A-002 | Patton | G97 / 90 / 12 - Patton | 2015-02-11 | 11:45:00 | 2015-02-11 | 15:00:00 | 3:15:00 | 2000541: CLEANED THE SLIP RING AND CHANGED BRUSHES TO PREVENT PROBLEMS

## Consumptions
Order | Plnt | SLoc | Material | Material Description | MvT | Movement Type Text | Time | S | Mat. Doc. | Quantity in UnE | BUn | Entry Date | Pstng Date
401912079 | 1311 | 1999 | 109818 | HYDR.PUMP U.HANSA TMPGLDE20-I | 967 | WO mat. Return | 19:56:58 |  | 4913001611 | 1 | ST | 2015-02-24 | 2015-02-24
401912079 | 1320 | 1121 | 109818 | HYDR.PUMP U.HANSA TMPGLDE20-I | 965 | WO mat. consumption | 19:56:57 |  | 4913001610 | -1 | ST | 2015-02-24 | 2015-02-24
401916174 | 1320 | 1121 | 50014 | A9-A40 RC FILTER | 965 | WO mat. consumption | 19:11:39 |  | 4913024791 | -1 | ST | 2015-02-27 | 2015-03-01
401912085 | 1311 | 1999 | 50972 | POWER SUPPLY QUINT-PS-100-240AC-24DC-5A | 967 | WO mat. Return | 19:57:35 |  | 4913001627 | 1 | ST | 2015-02-24 | 2015-02-24
401912085 | 1320 | 1121 | 50972 | POWER SUPPLY QUINT-PS-100-240AC-24DC-5A | 965 | WO mat. consumption | 19:57:34 |  | 4913001626 | -1 | ST | 2015-02-24 | 2015-02-24
401891052 | 1320 | 1121 | AMB0155 | 230V 127W IP44 FAN | 965 | WO mat. consumption | 18:02:18 |  | 4912905278 | -1 | ST | 2015-02-03 | 2015-02-03
401884474 | 1320 | 1121 | AMB0155 | 230V 127W IP44 FAN | 965 | WO mat. consumption | 19:57:02 |  | 4912880511 | -1 | ST | 2015-01-28 | 2015-01-28
401891070 | 1311 | 1999 | GP004888 | IBS IL 24 BK-LK-PAC INTERBUS BUS COUPLER | 967 | WO mat. Return | 18:41:59 |  | 4912905400 | 1 | ST | 2015-02-03 | 2015-02-03
401891070 | 1320 | 1121 | GP004888 | IBS IL 24 BK-LK-PAC INTERBUS BUS COUPLER | 965 | WO mat. consumption | 18:41:57 |  | 4912905399 | -1 | ST | 2015-02-03 | 2015-02-03
401924018 | 1311 | 1999 | GP004895 | IB IL TEMP 2 RTD-PAC | 967 | WO mat. Return | 12:42:19 |  | 4913064537 | 1 | ST | 2015-03-09 | 2015-03-09
401912081 | 1311 | 1999 | GP004895 | IB IL TEMP 2 RTD-PAC | 967 | WO mat. Return | 19:57:19 |  | 4913001620 | 1 | ST | 2015-02-24 | 2015-02-24
401879734 | 1311 | 1999 | GP004895 | IB IL TEMP 2 RTD-PAC | 967 | WO mat. Return | 15:07:16 |  | 4912858142 | 1 | ST | 2015-01-23 | 2015-01-23
401924018 | 1320 | 1121 | GP004895 | IB IL TEMP 2 RTD-PAC | 965 | WO mat. consumption | 12:42:19 |  | 4913064536 | -1 | ST | 2015-03-09 | 2015-03-09
401912081 | 1320 | 1121 | GP004895 | IB IL TEMP 2 RTD-PAC | 965 | WO mat. consumption | 19:57:18 |  | 4913001619 | -1 | ST | 2015-02-24 | 2015-02-24
401879734 | 1320 | 1121 | GP004895 | IB IL TEMP 2 RTD-PAC | 965 | WO mat. consumption | 15:07:15 |  | 4912858141 | -1 | ST | 2015-01-23 | 2015-01-23
401914298 | 1311 | 1999 | GP006039 | OFFLINE FILTER HDU 15-25 PM 0 60Hz | 967 | WO mat. Return | 13:37:03 |  | 4913015227 | 1 | ST | 2015-02-26 | 2015-03-01
401914298 | 1320 | 1121 | GP006039 | OFFLINE FILTER HDU 15-25 PM 0 60Hz | 965 | WO mat. consumption | 13:37:02 |  | 4913015226 | -1 | ST | 2015-02-26 | 2015-03-01
401914836 | 1311 | 1999 | GP006667 | TEMPERATURE MULTIPLEXER CARD AK9984 | 967 | WO mat. Return | 17:42:03 |  | 4913017225 | 1 | ST | 2015-02-26 | 2015-03-01
401914836 | 1320 | 1121 | GP006667 | TEMPERATURE MULTIPLEXER CARD AK9984 | 965 | WO mat. consumption | 17:42:02 |  | 4913017224 | -1 | ST | 2015-02-26 | 2015-03-01
401924030 | 1320 | 1121 | GP009355 | ACTUADOR JOVENTA mod.DAS2.S 8Nm | 965 | WO mat. consumption | 12:52:07 |  | 4913064669 | -1 | ST | 2015-03-09 | 2015-03-09
401912085 | 1320 | 1121 | GP009355 | ACTUADOR JOVENTA mod.DAS2.S 8Nm | 965 | WO mat. consumption | 19:57:38 |  | 4913001629 | -2 | ST | 2015-02-24 | 2015-02-24
401877674 | 1320 | 1121 | GP009355 | ACTUADOR JOVENTA mod.DAS2.S 8Nm | 965 | WO mat. consumption | 18:12:01 |  | 4912847526 | -3 | ST | 2015-01-21 | 2015-01-21
401912079 | 1311 | 1999 | GP010672 | BRAKE POWER SUPPLY SYSTEM SAA001 | 967 | WO mat. Return | 19:57:06 |  | 4913001614 | 1 | ST | 2015-02-24 | 2015-02-24
401912079 | 1320 | 1121 | GP010672 | BRAKE POWER SUPPLY SYSTEM SAA001 | 965 | WO mat. consumption | 19:57:05 |  | 4913001613 | -1 | ST | 2015-02-24 | 2015-02-24
401905340 | 1320 | 1121 | GP013211 | F. A. GENERIC HYDRAULIC GROUP FLUIDS | 965 | WO mat. consumption | 23:36:46 |  | 4912970416 | -12 | L | 2015-02-17 | 2015-02-17
401868943 | 1320 | 1121 | GP013211 | F. A. GENERIC HYDRAULIC GROUP FLUIDS | 965 | WO mat. consumption | 19:17:12 |  | 4912805807 | -8 | L | 2015-01-12 | 2015-01-12
401863233 | 1320 | 1121 | GP013211 | F. A. GENERIC HYDRAULIC GROUP FLUIDS | 965 | WO mat. consumption | 22:01:43 |  | 4912779857 | -20 | L | 2015-01-06 | 2015-01-06
401912086 | 1320 | 1121 | GP020967 | CABLE WABT79 G8X DTC BT | 965 | WO mat. consumption | 19:57:31 |  | 4913001625 | -1 | ST | 2015-02-24 | 2015-02-24
401912079 | 1311 | 1999 | GP049196 | BRAKE DISC-MACHINED G8X | 967 | WO mat. Return | 19:57:10 |  | 4913001616 | 1 | ST | 2015-02-24 | 2015-02-24
401912079 | 1320 | 1121 | GP049196 | BRAKE DISC-MACHINED G8X | 965 | WO mat. consumption | 19:57:10 |  | 4913001615 | -1 | ST | 2015-02-24 | 2015-02-24
500727770 | 1320 | 1121 | GP052263 | BRUSH CANT05 | 965 | WO mat. consumption | 13:36:49 |  | 4912947736 | -1 | ST | 2015-02-12 | 2015-02-12
401899267 | 1320 | 1121 | GP052263 | BRUSH CANT05 | 965 | WO mat. consumption | 13:52:48 |  | 4912941475 | -1 | ST | 2015-02-11 | 2015-02-11
401899235 | 1320 | 1121 | GP052263 | BRUSH CANT05 | 965 | WO mat. consumption | 13:42:00 |  | 4912941362 | -1 | ST | 2015-02-11 | 2015-02-11
401896947 | 1320 | 1121 | GP052263 | BRUSH CANT05 | 965 | WO mat. consumption | 18:46:45 |  | 4912930181 | -1 | ST | 2015-02-09 | 2015-02-09
401914298 | 1311 | 1999 | GP061817 | MOTOPUMP SEIM 60HZ 100L/MIN 3KW_PX045#4A | 967 | WO mat. Return | 13:36:58 |  | 4913015225 | 1 | ST | 2015-02-26 | 2015-03-01
401914298 | 1320 | 1121 | GP061817 | MOTOPUMP SEIM 60HZ 100L/MIN 3KW_PX045#4A | 965 | WO mat. consumption | 13:36:57 |  | 4913015224 | -1 | ST | 2015-02-26 | 2015-03-01
401919118 | 1320 | 1121 | GP062610 | HOSE 421SN-20 STRAIGHT ELBOW90 L720MM | 965 | WO mat. consumption | 19:41:47 |  | 4913039325 | -1 | ST | 2015-03-03 | 2015-03-03
401912079 | 1311 | 1999 | GP064008 | ZEROMAX HSS COUPLING SLEEVEFIX+LIMITER 6 | 967 | WO mat. Return | 19:57:14 |  | 4913001618 | 1 | ST | 2015-02-24 | 2015-02-24
401912079 | 1320 | 1121 | GP064008 | ZEROMAX HSS COUPLING SLEEVEFIX+LIMITER 6 | 965 | WO mat. consumption | 19:57:14 |  | 4913001617 | -1 | ST | 2015-02-24 | 2015-02-24
401912081 | 1311 | 1999 | GP082783 | IB IL TEMP 4\8 RTD\EF-PAC | 967 | WO mat. Return | 19:57:23 |  | 4913001622 | 1 | ST | 2015-02-24 | 2015-02-24
401912081 | 1320 | 1121 | GP082783 | IB IL TEMP 4\8 RTD\EF-PAC | 965 | WO mat. consumption | 19:57:22 |  | 4913001621 | -1 | ST | 2015-02-24 | 2015-02-24
401912086 | 1311 | 1999 | GP096823 | G9X ELECTRIC ROTATING JOINT LT COBHAM | 967 | WO mat. Return | 19:57:27 |  | 4913001624 | 1 | ST | 2015-02-24 | 2015-02-24
401912086 | 1320 | 1121 | GP096823 | G9X ELECTRIC ROTATING JOINT LT COBHAM | 965 | WO mat. consumption | 19:57:27 |  | 4913001623 | -1 | ST | 2015-02-24 | 2015-02-24
401863233 | 1311 | 1999 | GP097008 | MOTOPUMP B-P 60HZ 100L/MIN 3KW_PX045#4A | 967 | WO mat. Return | 22:01:39 |  | 4912779856 | 1 | ST | 2015-01-06 | 2015-01-06
401863233 | 1320 | 1121 | GP097008 | MOTOPUMP B-P 60HZ 100L/MIN 3KW_PX045#4A | 965 | WO mat. consumption | 22:01:38 |  | 4912779855 | -1 | ST | 2015-01-06 | 2015-01-06
401872279 | 1320 | 1121 | GP109629 | ROTOR LOCK LEFT CLOSING PLATE | 965 | WO mat. consumption | 18:46:41 |  | 4912823106 | -1 | ST | 2015-01-15 | 2015-01-15
401862384 | 1311 | 1999 | GP118568 | PROPORTIONAL VALVE KBFDG4V5 VICKERS | 967 | WO mat. Return | 15:57:19 |  | 4912776743 | 1 | ST | 2015-01-05 | 2015-01-05
401862384 | 1320 | 1121 | GP118568 | PROPORTIONAL VALVE KBFDG4V5 VICKERS | 965 | WO mat. consumption | 15:57:17 |  | 4912776742 | -1 | ST | 2015-01-05 | 2015-01-05
401912079 | 1311 | 1999 | P050003 | SMP-8C PREDICTIVE MAINT. SYST. | 967 | WO mat. Return | 21:11:37 |  | 4913010732 | 1 | ST | 2015-02-25 | 2015-03-01
401912079 | 1320 | 1121 | P050003 | SMP-8C PREDICTIVE MAINT. SYST. | 965 | WO mat. consumption | 21:11:36 |  | 4913010731 | -1 | ST | 2015-02-25 | 2015-03-01
401886608 | 1320 | 1121 | P393119 | Sens.Balluff 0206D BESM30ML1,10-30Vdc | 965 | WO mat. consumption | 17:37:22 |  | 4912910816 | -1 | ST | 2015-02-04 | 2015-02-04
401868953 | 1320 | 1121 | P393119 | Sens.Balluff 0206D BESM30ML1,10-30Vdc | 965 | WO mat. consumption | 19:36:35 |  | 4912805779 | -1 | ST | 2015-01-12 | 2015-01-12
401919118 | 1320 | 1121 | P422686 | HOSE 1,25" L=1060 MALE-SWIVEL FEM.90 | 965 | WO mat. consumption | 19:41:43 |  | 4913039324 | -1 | ST | 2015-03-03 | 2015-03-03
401884474 | 1320 | 1121 | R9E1495P01 | PT 100 SENSOR | 965 | WO mat. consumption | 19:56:58 |  | 4912880510 | -1 | ST | 2015-01-28 | 2015-01-28