## Sheet1
ALSTOM 38kV Dead Tank Breakers
Read and record operating counter figures
Check the general visual appearance of switchgear: (corrosion, paint, etc.)
Check the SF6 pressure on density monitor. Top off with gas if necessary.
Check the condition of all external hardware with calibrated torqu wrench according to TS-00007
Check the switch points of the SF6 density monitor and check moisture and acidity of content of gas
Check the resistance of the amin current path
Inspect the bushing insulators/clean and polish
Measure the operating times of poles and auxiliary contacts, at rated voltage and pressure
Clean the inside of the tank of any particles
Change seals, reapply greeases and lubricants
Replace desiccant (and every time a pole is opened)
Replace cabinet seals
Replase the operative mechanism (only done after 10,000 operating cycles)
Call ALSTOM to check the condition of interrupter unit (Only done if electrical wear limit is reached)
ALSTTOM 145kV Dead Tank Breakers
Read and record operating counter figures
Check the general visual appearance of switchgear: (corrosion, paint, etc.)
Check the SF6 pressure on density monitor. Top off with gas if necessary.
Check the condition of all external hardware with calibrated torqu wrench according to TS-00007
Check the switch points of the SF6 density monitor and check moisture and acidity of content of gas
Check the resistance of the amin current path
Inspect the bushing insulators/clean and polish
Measure the operating times of poles and auxiliary contacts, at rated voltage and pressure
Clean the inside of the tank of any particles
Change seals, reapply greeases and lubricants
Replace desiccant (and every time a pole is opened)
Replace cabinet seals
Replase the operative mechanism (only done after 10,000 operating cycles)
Call ALSTOM to check the condition of interrupter unit (Only done if electrical wear limit is reached)
Siemens GSU
Oil sample
Oil Level of conservator
Check Oil level of bushings
Power factor test
Power factor test of bushings
Check proper cooling fan operation
Check and record Winding temp. (current and max Reset)
Check and record oil temp. (current and max Reset)
Visual inspection (leaks, corrosion, etc.)
GSU corrosive sulfur test (request from oil sample lab)
Excitation Test
Insulation Resistence test (core/ground)
Turns ratio test
IR Scan
34.5 kV disconnect switchers
Visual Inspection
Check contacts for proper engagement and surface condition
Clean and re-grease stab and finger contacts
IR Scan
138kV disconnect switches
Visual Inspection
Check contacts for proper engagement and surface condition
Clean and re-grease stab and finger contacts
IR Scan
Neutral Grounding Reactor
Visually inspect for paint deterioration and pollution accumulation
EATON ATS Transfer switch
Visually Inspect
138 kV CCVT's
Visually inspect
Capacitance test
Power Factor test
IR Scan
34.5 kV Voltage Transformers
Visually inspect
Power Factor test
Insulation test
Clean and silicone
Grounding Transformers
Visually inspect
Oil sample
IR Scan
138 kV insulators
Visually inspect
Clean and polish
34.5 kV insulators
Visually inspect
Clean and polish
F-11 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
F-12 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
F-13 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
F-15 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
F-16 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
87T Relay (SEL-387)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
87B Relay (SEL-5872)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
TP Relay (SEL-351)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
Line Relay (SEL-311A)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
Line Relay (SEL-311L)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel
Visually inspect for loose connections (rainbowing)
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2
Battery Bank
Montly battery bank/Pilot cell checks
Quarterly batter bank checks
Annual batter bank checks
Battery Charger
Complete needed checks as per AT10.1 operation manual
Ion Revenue Meter
Caliberate meter
Bus work/Current carrying connections
Visually inspect
IR Scan