## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Asset ID | Vendor ID | Actual Hours | Part ID | Part Quantity | Comments | Original ID
PATTN-WKO-GAM-20140311-01 | gam-inspection of nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/12/2014 | 25.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.1167 |  |  | 2000856: gam-checked the op of the louvers. reset the cams. ran tower | 401584977
PATTN-WKO-GAM-20140311-02 | gam-check nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 2.1333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 2.1333 |  |  | 2000856: gam-check nacelle louvers for proper op, found they were opening backwards. switched wires reset louver cams and ran tower | 401585000
PATTN-WKO-GAM-20140311-03 | gam-naccelle louver inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 1.6 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 1.6 |  |  | 2000856: gam-checked nacelle louvers, found opening backwards, reset cams and switch wires around ran turbine | 401585004
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0196 | 60 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0401 | 30 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0069 | 10 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0413 | 2 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140312-01 | gam-2106 temp fail | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.083333 |  |  | 2000856: gam-2106 reset top cabinet all temps came back ran turbine | 401585166
PATTN-WKO-GAM-20140312-02 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 2.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 2.9 | GAMSA-PRT-0064 | 1 | 2000856: gam-installed north sensor, cleaned out slip ring and changed brushes | 401585267
PATTN-WKO-GAM-20140312-03 | GAM-MODIFIED ROOF AND INSTALLED NORTH SE | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 1.7 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 2.25 | GAMSA-PRT-0064 | 1 | 2001212: GAM-MODIFIED ROOF AND INSTALLED NORTH SENSOR | 401585289
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0426 | 1 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140315-01 | GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADE | Closed | Corrective Maintenance | Forced | 02-High | 3/15/2014 | 3/15/2014 | 3/15/2014 | 5.7 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3.5167 | GAMSA-PRT-0094 | 1 | 2001212: GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADES VERY HIGH / CHANGED BALLUF CABLE | 401590249
PATTN-WKO-GAM-20140317-01 | GAM-800 ALARM PITCH ACTIVATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/17/2014 | 3/17/2014 | 3/17/2014 | 1.75 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.75 |  |  | 2001212: GAM-800 ALARM PITCH ACTIVATION ERROR / CHANGED PROP VALVE ON BLADE C | 401590643
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0398 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140319-01 | GAM-GEAR BOX OIL SAMPLE / REPLACED MIS | Closed | Corrective Maintenance | Forced | 02-High | 3/19/2014 | 3/19/2014 | 3/19/2014 | 0.6 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 0.75 | GAMSA-PRT-0398 | 1 | 2001212: GAM-GEARBOX OIL SAMPLE / REPLACED NUTS ON VICKERS VALVES | 401592858
PATTN-WKO-GAM-20140320-01 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 5.95 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LOCAL RESET | 401593615
PATTN-WKO-GAM-20140320-02 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 1.65 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LANDED GEARBOX SHIELDING | 401594219
PATTN-WKO-GAM-20140320-03 | GAM-426 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 0.88333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 1 | GAMSA-PRT-0381 | 1 | 2001212: GAM-426 ALARM OGS / CHANGED SENSOR | 401594279
PATTN-WKO-GAM-20140321-01 | GAM-327 ALARM LTK CONFIRMATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 0.41667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 0.5 |  |  | 2001212: GAM-327 LTK CONFIRMATION ERROR / CHANGED LOUVERS | 401594941
PATTN-WKO-GAM-20140321-02 | GAM-PLANNED ROOF REPAIR / GREASED YAW | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 4.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 4.5 |  |  | 2001212: GAM-PLANNED ROOF REPAIR / GREASED YAW | 401595371
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0416 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0421 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0427 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0420 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0078 | 3 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0196 | 34 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0069 | 13 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0413 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0416 | 20 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0421 | 9 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0064 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140327-01 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 4 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 1.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / PLANNED INSTALLATION OF KBT YAW DRIVE | 401601799
PATTN-WKO-GAM-20140327-02 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 3.85 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 4 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLATION OF HG YAW DRIVE | 401601823
PATTN-WKO-GAM-20140328-01 | GAM-PLANNED CORRECTIVE / NOTICED SONIC | Closed | Corrective Maintenance | Forced | 02-High | 3/28/2014 | 3/28/2014 | 3/28/2014 | 0.63333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 0.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / ADJUSTED SONIC | 401602119
PATTN-WKO-GAM-20140330-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/30/2014 | 3/30/2014 | 3/30/2014 | 3.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 3.5 | GAMSA-PRT-0386 | 1 | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / CHANGED TRANSFORMER FUSE B | 401603723
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0374 | 5 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0142 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0428 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-02 | GAM-804 ALARM DIFFERENCE BETWEEN BLADES | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 1.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 1.5 |  |  | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES VERY HIGH / CHANGED AO CARD IN HUB CABINET | 401605611
PATTN-WKO-GAM-20140401-01 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.5167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 1.75 | GAMSA-PRT-0429 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHECKED CONVERTER TEMPS, CHANGED SIGHT GLASS ON GEARBOX | 401606444
PATTN-WKO-GAM-20140401-02 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.0333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / WENT UP TO CHECK DIFFERENCES IN CONVERTER TEMPS AT CUSTOMERS REQUEST | 401607123
PATTN-WKO-GAM-20140401-03 | GAM-PLANNED CORRECTIVE / HAD HIGHER TE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 0.8 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSPECTED CONVERTER AT CUSTOMERS REQUEST | 401607130
PATTN-WKO-GAM-20140401-04 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.3833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.083333 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401607137
PATTN-WKO-GAM-20140401-05 | GAM-5200 ALARM MAGNETOTHERMIC TRIP OF TH | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.75 |  |  | 2001212: GAM-5200 ALARM MAGNETOTHERMIC TRIP OF THE LIINE PROTECTION / TRANSFORMER LOUVER CLOSED OVERHEATING CONVERTER | 401607159
PATTN-WKO-GAM-20140402-01 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/2/2014 | 4/2/2014 | 4/2/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.25 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / CHANGED GATEWAY, AND BLED BOTH YAW BRAKE SYSTEM AND ROTOR BRAKE SYSTEM | 401607546
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 7 | GAMSA-PRT-0430 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 7 | GAMSA-PRT-0431 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 0.98333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401609844
PATTN-WKO-GAM-20140404-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 1.4833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 1.75 | GAMSA-PRT-0172 | 2 | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / FOUND 2 BAD ACTUATORS AND CHANGED THEM | 401610176
PATTN-WKO-GAM-20140404-02 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 0.5 | GAMSA-PRT-0288 | 1 | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / TESTED KR330G FOUND BAD RESISTANCE AND CHANGED | 401610307
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 5.2833 | GAMSA-PRT-0066 | 20 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 5.2833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140408-01 | GAM-203 ALARM LOW PRESSURE HG / CHANGE | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/9/2014 | 6.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 4.4833 |  |  | 2001212: GAM-203 ALARM LOW PRESSURE HG / CHANGED BLADE C PITCH BLOCK | 401620946
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0415 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0424 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140411-01 | GAM-1823 ALARM COOLANT CONFIRMATION FAIL | Closed | Corrective Maintenance | Forced | 02-High | 4/11/2014 | 4/11/2014 | 4/11/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 4 | GAMSA-PRT-0172 | 1 | 2001212: GAM-1823 ALARM COOLANT CONFIRMATION FAILURE / FOUND BAD LOUVER AND CHANGED | 401620949
PATTN-WKO-GAM-20140415-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/15/2014 | 4/15/2014 | 4/15/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 2 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CLEANED RADIATORS | 401620950
PATTN-WKO-GAM-20140413-01 | GAM-410 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 4/13/2014 | 4/13/2014 | 4/13/2014 | 1.95 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 1.5 | GAMSA-PRT-0381 | 1 | 2001212: GAM-410 OGS / CHANGED SENSOR | 401620951
PATTN-WKO-GAM-20140416-01 | GAM-2198 ALARM TEMP MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 4/16/2014 | 4/16/2014 | 4/16/2014 | 5.3833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 6 | GAMSA-PRT-0172 | 2 | 2001212: GAM-2198 ALARM TEMP MODULE FAILURE / CHANGED TEMP CARD, GREASED YAW AND BLED SYSTEM, CHANGED 2 LOUVERS | 401621045
PATTN-WKO-GAM-20140419-01 | GAM-401 ALARM LOW PRESSURE GEAR BOX / | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 1.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG07 | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624105
PATTN-WKO-GAM-20140419-02 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.8 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624111
PATTN-WKO-GAM-20140419-03 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.6667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 0.75 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624119
PATTN-WKO-GAM-20140420-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/20/2014 | 5.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 4.5 |  |  | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / LEAK TO GROUND ON YAW MOTOR, CHANGED YAW MOTOR 181A | 401624125
PATTN-WKO-GAM-20140420-02 | GAM-PLANNED CORRECTIVE / INSTALLED YAW | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/21/2014 | 29.2333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 5.5 | GAMSA-PRT-0066 | 10 | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED YAW DRIVE | 401624141
PATTN-WKO-GAM-20140421-01 | GAM-114 ALARM YAW BRAKE LOW PRESSURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 0.61667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 0.75 |  |  | 2001212: GAM-114 ALARM YAW BRAKE LOW PRESSURE / BLED YAW BRAKE SYSTEM | 401624153
PATTN-WKO-GAM-20140421-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 2.55 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 1.75 | GAMSA-PRT-0125 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CARD, GREASED AND BLED YAW CLAMPS | 401624183
PATTN-WKO-GAM-20140422-01 | GAM-PLANNED CORRECTIVE / BLED BRAKE SY | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/22/2014 | 6.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 6 | GAMSA-PRT-0172 | 3 | 2001212: GAM-PLANNED CORRECTIVE / BLED BRAKE SYSTEM, FOUND LOOSE BOLTS ON YAW DRIVES AND TIGHTENED, CLEANED TURBINE | 401625671
PATTN-WKO-GAM-20140423-01 | GAM-5209-coolant circuit falure | Closed | Corrective Maintenance | Forced | 02-High | 4/23/2014 | 4/23/2014 | 4/23/2014 | 0.78333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.78333 |  |  | 2001212: GAM-5219-cooling circuit falure- troubleshoot and tightend wiring | 401626574
PATTN-WKO-GAM-20140422-02 | GAM-107 yaw motor circuit breakers | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/24/2014 | 84.4 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 4.9 | GAMSA-PRT-0172 | 1 | 2001212: GAM-107 yaw motors circuit breakers - call in removed broken left front yaw assembly could not install new assembly due to high winds - returned 24th installed new assembly with new yaw motor also installed new upper ltk louver motor rtsvc | 401627759
PATTN-WKO-GAM-20140424-01 | GAM-721 wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 4/24/2014 | 4/24/2014 | 4/24/2014 | 1.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.1167 |  |  | 2001212: GAM-721 wind vane falure- troubleshoot wind vane | 401627771
PATTN-WKO-GAM-20140425-01 | GAM-PLANNED CORRECTIVE INSTALLED RETRO O | Closed | Corrective Maintenance | Forced | 02-High | 4/25/2014 | 4/25/2014 | 4/25/2014 | 2.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED RETRO ON LIGHTENING SYSTEM FOR ENGINEERS | 401633211
PATTN-WKO-GAM-20140426-01 | GAM-208 ALARM HG FEEDBACK FAILURE / RE | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.3667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0003 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633212
PATTN-WKO-GAM-20140430-01 | GAM-PLANNED CORRECTIVE / OWNER QC WALK | Closed | Corrective Maintenance | Forced | 02-High | 4/30/2014 | 4/30/2014 | 4/30/2014 | 3 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 |  |  | 2001212: GAM-PLANNED CORRECTIVE / OWNER QC WALKDOWN, FOUND FAULTY WIRING IN TOP CABINET ALL OF X4 BLOCK WAS WIRED NEUTRAL TO LINE | 401633213
PATTN-WKO-GAM-20140428-01 | GAM-PLANNED CORRECTIVE / CHANGED MOUNT | Closed | Corrective Maintenance | Forced | 02-High | 4/28/2014 | 4/28/2014 | 4/28/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 1.7667 | GAMSA-PRT-0432 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHANGED MOUNTING POST FOR SONIC | 401633214
PATTN-WKO-GAM-20140501-01 | GAM-2509-comm error | Closed | Corrective Maintenance | Forced | 02-High | 5/1/2014 | 5/1/2014 | 5/1/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.083333 | GAMSA-PRT-0288 | 1 | 2001212: GAM-2509-comm error- installed new kr330 relay kit in base cabinet rtsvc | 401633286
PATTN-WKO-GAM-20140426-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.6167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 |  |  | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633287
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0422 | 40 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0066 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-02 | GAM-327 ALARM LTK CONFIRMATION ERROR / C | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CHANGED JOVENTA DURING THIRD PARTY INSPECTION OF GEARBOX | 401638191
PATTN-WKO-GAM-20140505-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 4.15 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 4.15 |  |  | USI-Borescope EOW Inspections/ Perform EOW Gearbox inspections | 401638556
PATTN-WKO-GAM-20140505-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 3.1333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 3.1333 |  |  | USI-EOW-Gearbox Borescope Inspections/ Perform EOW Gearbox Inspections | 401638557
PATTN-WKO-GAM-20140502-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 4.9167 |  |  | USI-EOW Gearbox Inspections/ Perform Gearbox Inspections | 401638558
PATTN-WKO-GAM-20140509-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.45 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 2.4667 |  |  | USI-EOW Gearbox Borescope Inspections/ Perform Gearbox Inspections | 401640904
PATTN-WKO-GAM-20140509-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.8167 |  |  | USI-EOW-Gearbox Borescope Inspections | 401640905
PATTN-WKO-GAM-20140509-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 3.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 3.1833 |  |  | USI-EOW Gearbox Borescope inspections/perform gearbox inspections | 401640906
PATTN-WKO-GAM-20140509-04 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 2.6667 |  |  | USI-EOW Gearbox Inspections/ Perform Borescope inspections | 401640907
PATTN-WKO-GAM-20140512-01 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 2.4167 |  |  | UPW-5819933-BORESCOPE INSPECTION OF GEAR | 401642558
PATTN-WKO-GAM-20140512-02 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 0 |  |  | USI-EOW Borescope Inspections Gearbox | 401642559
PATTN-WKO-GAM-20140513-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.5 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 2.5 |  |  | USI-EOW-Gearbox Borescope inspections | 401643573
PATTN-WKO-GAM-20140513-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 2.9 |  |  | USI-EOW Gearbox borescope inspections | 401643575
PATTN-WKO-GAM-20140514-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 2.8167 |  |  | USI-EOW Gearbox Borescope Inspections/Perform Borescope Inspections | 401645458
PATTN-WKO-GAM-20140514-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.5833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 2.5833 |  |  | USI-EOW-Gearbox Borescope Inspections/Perform gearbox inspections | 401645460
PATTN-WKO-GAM-20140513-03 | GAM-208-hu feedback error | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 1.5 | GAMSA-PRT-0050 | 1 | 2001223: GAM-208-hu pump drive falure- installed new contactor | 401645583
PATTN-WKO-GAM-20140515-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 2.1667 |  |  | USI-EOW Gearbox Borescope inspections | 401645615
PATTN-WKO-GAM-20140515-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2 |  |  | USI-EOW Borescope inspections Gearbox | 401645616
PATTN-WKO-GAM-20140514-03 | GAM-300-anemometer failure | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/15/2014 | 25.4333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.53333 |  |  | 2001223: GAM-300-anemometer falure- found loose wiring - reconnected rtsvc | 401646567
PATTN-WKO-GAM-20140514-04 | GAM-403-high temp gearbox | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 1.0833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 0.46667 |  |  | 2001223: GAM-403-gearbox high temp | 401646594
PATTN-WKO-GAM-20140515-03 | GAM-721-wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.65 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.65 |  |  | 2001223: GAM-721-wind vane falure- installed new wind vane | 401646689
PATTN-WKO-GAM-20140516-01 | GAM-shim gearbox-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox in accordance with maintenance procedure | 401651187
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2.1667 | GAMSA-PRT-0431 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2.1667 | GAMSA-PRT-0430 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140519-01 | GAM-shim gear box- pending task resoluti | Closed | Corrective Maintenance | Forced | 02-High | 5/19/2014 | 5/19/2014 | 5/19/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox per procedure | 401652551
PATTN-WKO-GAM-20140523-01 | GAM-SHIM GEARBOX-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/23/2014 | 5/23/2014 | 5/23/2014 | 1.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG07 | VEN-165 | 1.9167 |  |  | 2001223: GAM-shimed gearbox per procedure | 401658443
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.75 | GAMSA-PRT-0374 | 5 | GAM-5248-active crowbar igbt errors | 401661282
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.75 | GAMSA-PRT-0142 | 1 | GAM-5248-active crowbar igbt errors | 401661282
PATTN-WKO-GAM-20140508-01 | GAM-18 MONTH Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/9/2014 | 32.4833 | Patton | Planned |  | PMI-003 | PATTN-WTG12 | VEN-165 | 2.5833 | GAMSA-PRT-0401 | 30 | 2001212: GAM-18month minor maint complete per ck list 2001223: 18month maint complete per ck list | 500593590
PATTN-WKO-GAM-20140508-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/16/2014 | 198.7833 | Patton | Planned |  | PMI-003 | PATTN-WTG11 | VEN-165 | 1.6833 | GAMSA-PRT-0401 | 30 | 2001223: GAM-18 month maint complete per ck list | 500593836
PATTN-WKO-GAM-20140523-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/23/2014 | 5/23/2014 | 5/28/2014 | 128 | Patton | Planned |  | PMI-003 | PATTN-WTG01 | VEN-165 | 4.8 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500593839
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 | PATTN-WTG13 | VEN-165 | 3.5167 | GAMSA-PRT-0435 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 | PATTN-WTG13 | VEN-165 | 3.5167 | GAMSA-PRT-0420 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140520-01 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/20/2014 | 5/20/2014 | 5/22/2014 | 55.6667 | Patton | Planned |  | PMI-003 | PATTN-WTG07 | VEN-165 | 4.8667 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500597336
PATTN-WKO-GAM-20140311-05 | gam-inspection of nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/12/2014 | 25.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.1167 |  |  | 2000856: gam-checked the op of the louvers. reset the cams. ran tower | 401584977
PATTN-WKO-GAM-20140311-06 | gam-check nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 2.1333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 2.1333 |  |  | 2000856: gam-check nacelle louvers for proper op, found they were opening backwards. switched wires reset louver cams and ran tower | 401585000
PATTN-WKO-GAM-20140311-07 | gam-naccelle louver inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 1.6 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 1.6 |  |  | 2000856: gam-checked nacelle louvers, found opening backwards, reset cams and switch wires around ran turbine | 401585004
PATTN-WKO-GAM-20140311-08 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0196 | 60 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-08 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0401 | 30 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-08 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0069 | 10 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-08 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.2833 | GAMSA-PRT-0413 | 2 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140312-04 | gam-2106 temp fail | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.083333 |  |  | 2000856: gam-2106 reset top cabinet all temps came back ran turbine | 401585166
PATTN-WKO-GAM-20140312-05 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 2.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 2.9 | GAMSA-PRT-0064 | 1 | 2000856: gam-installed north sensor, cleaned out slip ring and changed brushes | 401585267
PATTN-WKO-GAM-20140312-06 | GAM-MODIFIED ROOF AND INSTALLED NORTH SE | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 1.7 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 2.25 | GAMSA-PRT-0064 | 1 | 2001212: GAM-MODIFIED ROOF AND INSTALLED NORTH SENSOR | 401585289
PATTN-WKO-GAM-20140314-02 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0426 | 1 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-02 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-02 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 5.0833 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140315-02 | GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADE | Closed | Corrective Maintenance | Forced | 02-High | 3/15/2014 | 3/15/2014 | 3/15/2014 | 5.7 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3.5167 | GAMSA-PRT-0094 | 1 | 2001212: GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADES VERY HIGH / CHANGED BALLUF CABLE | 401590249
PATTN-WKO-GAM-20140317-02 | GAM-800 ALARM PITCH ACTIVATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/17/2014 | 3/17/2014 | 3/17/2014 | 1.75 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.75 |  |  | 2001212: GAM-800 ALARM PITCH ACTIVATION ERROR / CHANGED PROP VALVE ON BLADE C | 401590643
PATTN-WKO-GAM-20140318-03 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-03 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0398 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 5.5833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140319-02 | GAM-GEAR BOX OIL SAMPLE / REPLACED MIS | Closed | Corrective Maintenance | Forced | 02-High | 3/19/2014 | 3/19/2014 | 3/19/2014 | 0.6 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 0.75 | GAMSA-PRT-0398 | 1 | 2001212: GAM-GEARBOX OIL SAMPLE / REPLACED NUTS ON VICKERS VALVES | 401592858
PATTN-WKO-GAM-20140320-04 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 5.95 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LOCAL RESET | 401593615
PATTN-WKO-GAM-20140320-05 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 1.65 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LANDED GEARBOX SHIELDING | 401594219
PATTN-WKO-GAM-20140320-06 | GAM-426 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 0.88333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 1 | GAMSA-PRT-0381 | 1 | 2001212: GAM-426 ALARM OGS / CHANGED SENSOR | 401594279
PATTN-WKO-GAM-20140321-03 | GAM-327 ALARM LTK CONFIRMATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 0.41667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 0.5 |  |  | 2001212: GAM-327 LTK CONFIRMATION ERROR / CHANGED LOUVERS | 401594941
PATTN-WKO-GAM-20140321-04 | GAM-PLANNED ROOF REPAIR / GREASED YAW | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 4.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 4.5 |  |  | 2001212: GAM-PLANNED ROOF REPAIR / GREASED YAW | 401595371
PATTN-WKO-GAM-20140324-03 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0416 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-03 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0421 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-03 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0427 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-03 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 8 | GAMSA-PRT-0420 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0078 | 3 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0196 | 34 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0069 | 13 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0413 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-04 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 3 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0416 | 20 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0421 | 9 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0064 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-03 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 5.75 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-04 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-04 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-04 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2.5 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140327-03 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 4 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 1.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / PLANNED INSTALLATION OF KBT YAW DRIVE | 401601799
PATTN-WKO-GAM-20140327-04 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 3.85 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 4 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLATION OF HG YAW DRIVE | 401601823
PATTN-WKO-GAM-20140328-02 | GAM-PLANNED CORRECTIVE / NOTICED SONIC | Closed | Corrective Maintenance | Forced | 02-High | 3/28/2014 | 3/28/2014 | 3/28/2014 | 0.63333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 0.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / ADJUSTED SONIC | 401602119
PATTN-WKO-GAM-20140330-02 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/30/2014 | 3/30/2014 | 3/30/2014 | 3.7833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 3.5 | GAMSA-PRT-0386 | 1 | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / CHANGED TRANSFORMER FUSE B | 401603723
PATTN-WKO-GAM-20140331-03 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0374 | 5 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-03 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0142 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-03 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 6.5 | GAMSA-PRT-0428 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-04 | GAM-804 ALARM DIFFERENCE BETWEEN BLADES | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 1.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 1.5 |  |  | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES VERY HIGH / CHANGED AO CARD IN HUB CABINET | 401605611
PATTN-WKO-GAM-20140401-06 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.5167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 1.75 | GAMSA-PRT-0429 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHECKED CONVERTER TEMPS, CHANGED SIGHT GLASS ON GEARBOX | 401606444
PATTN-WKO-GAM-20140401-07 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.0333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / WENT UP TO CHECK DIFFERENCES IN CONVERTER TEMPS AT CUSTOMERS REQUEST | 401607123
PATTN-WKO-GAM-20140401-08 | GAM-PLANNED CORRECTIVE / HAD HIGHER TE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 0.8 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSPECTED CONVERTER AT CUSTOMERS REQUEST | 401607130
PATTN-WKO-GAM-20140401-09 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.3833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.083333 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401607137
PATTN-WKO-GAM-20140401-10 | GAM-5200 ALARM MAGNETOTHERMIC TRIP OF TH | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 1.75 |  |  | 2001212: GAM-5200 ALARM MAGNETOTHERMIC TRIP OF THE LIINE PROTECTION / TRANSFORMER LOUVER CLOSED OVERHEATING CONVERTER | 401607159
PATTN-WKO-GAM-20140402-02 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/2/2014 | 4/2/2014 | 4/2/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 3.25 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / CHANGED GATEWAY, AND BLED BOTH YAW BRAKE SYSTEM AND ROTOR BRAKE SYSTEM | 401607546
PATTN-WKO-GAM-20140403-03 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 7 | GAMSA-PRT-0430 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-03 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 7 | GAMSA-PRT-0431 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-04 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 0.98333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401609844
PATTN-WKO-GAM-20140404-03 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 1.4833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 1.75 | GAMSA-PRT-0172 | 2 | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / FOUND 2 BAD ACTUATORS AND CHANGED THEM | 401610176
PATTN-WKO-GAM-20140404-04 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 0.5 | GAMSA-PRT-0288 | 1 | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / TESTED KR330G FOUND BAD RESISTANCE AND CHANGED | 401610307
PATTN-WKO-GAM-20140414-02 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 5.2833 | GAMSA-PRT-0066 | 20 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140414-02 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 5.2833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140408-03 | GAM-203 ALARM LOW PRESSURE HG / CHANGE | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/9/2014 | 6.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 4.4833 |  |  | 2001212: GAM-203 ALARM LOW PRESSURE HG / CHANGED BLADE C PITCH BLOCK | 401620946
PATTN-WKO-GAM-20140408-04 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0415 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140408-04 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0424 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140411-02 | GAM-1823 ALARM COOLANT CONFIRMATION FAIL | Closed | Corrective Maintenance | Forced | 02-High | 4/11/2014 | 4/11/2014 | 4/11/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 4 | GAMSA-PRT-0172 | 1 | 2001212: GAM-1823 ALARM COOLANT CONFIRMATION FAILURE / FOUND BAD LOUVER AND CHANGED | 401620949
PATTN-WKO-GAM-20140415-02 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/15/2014 | 4/15/2014 | 4/15/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 2 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CLEANED RADIATORS | 401620950
PATTN-WKO-GAM-20140413-02 | GAM-410 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 4/13/2014 | 4/13/2014 | 4/13/2014 | 1.95 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 1.5 | GAMSA-PRT-0381 | 1 | 2001212: GAM-410 OGS / CHANGED SENSOR | 401620951
PATTN-WKO-GAM-20140416-02 | GAM-2198 ALARM TEMP MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 4/16/2014 | 4/16/2014 | 4/16/2014 | 5.3833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 6 | GAMSA-PRT-0172 | 2 | 2001212: GAM-2198 ALARM TEMP MODULE FAILURE / CHANGED TEMP CARD, GREASED YAW AND BLED SYSTEM, CHANGED 2 LOUVERS | 401621045
PATTN-WKO-GAM-20140419-04 | GAM-401 ALARM LOW PRESSURE GEAR BOX / | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 1.2833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG07 | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624105
PATTN-WKO-GAM-20140419-05 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.8 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624111
PATTN-WKO-GAM-20140419-06 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.6667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 0.75 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624119
PATTN-WKO-GAM-20140420-03 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/20/2014 | 5.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 4.5 |  |  | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / LEAK TO GROUND ON YAW MOTOR, CHANGED YAW MOTOR 181A | 401624125
PATTN-WKO-GAM-20140420-04 | GAM-PLANNED CORRECTIVE / INSTALLED YAW | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/21/2014 | 29.2333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 5.5 | GAMSA-PRT-0066 | 10 | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED YAW DRIVE | 401624141
PATTN-WKO-GAM-20140421-03 | GAM-114 ALARM YAW BRAKE LOW PRESSURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 0.61667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 0.75 |  |  | 2001212: GAM-114 ALARM YAW BRAKE LOW PRESSURE / BLED YAW BRAKE SYSTEM | 401624153
PATTN-WKO-GAM-20140421-04 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 2.55 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 1.75 | GAMSA-PRT-0125 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CARD, GREASED AND BLED YAW CLAMPS | 401624183
PATTN-WKO-GAM-20140422-03 | GAM-PLANNED CORRECTIVE / BLED BRAKE SY | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/22/2014 | 6.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 6 | GAMSA-PRT-0172 | 3 | 2001212: GAM-PLANNED CORRECTIVE / BLED BRAKE SYSTEM, FOUND LOOSE BOLTS ON YAW DRIVES AND TIGHTENED, CLEANED TURBINE | 401625671
PATTN-WKO-GAM-20140423-02 | GAM-5209-coolant circuit falure | Closed | Corrective Maintenance | Forced | 02-High | 4/23/2014 | 4/23/2014 | 4/23/2014 | 0.78333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 0.78333 |  |  | 2001212: GAM-5219-cooling circuit falure- troubleshoot and tightend wiring | 401626574
PATTN-WKO-GAM-20140422-04 | GAM-107 yaw motor circuit breakers | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/24/2014 | 84.4 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 4.9 | GAMSA-PRT-0172 | 1 | 2001212: GAM-107 yaw motors circuit breakers - call in removed broken left front yaw assembly could not install new assembly due to high winds - returned 24th installed new assembly with new yaw motor also installed new upper ltk louver motor rtsvc | 401627759
PATTN-WKO-GAM-20140424-02 | GAM-721 wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 4/24/2014 | 4/24/2014 | 4/24/2014 | 1.1167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 1.1167 |  |  | 2001212: GAM-721 wind vane falure- troubleshoot wind vane | 401627771
PATTN-WKO-GAM-20140425-02 | GAM-PLANNED CORRECTIVE INSTALLED RETRO O | Closed | Corrective Maintenance | Forced | 02-High | 4/25/2014 | 4/25/2014 | 4/25/2014 | 2.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED RETRO ON LIGHTENING SYSTEM FOR ENGINEERS | 401633211
PATTN-WKO-GAM-20140426-03 | GAM-208 ALARM HG FEEDBACK FAILURE / RE | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.3667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 | GAMSA-PRT-0003 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633212
PATTN-WKO-GAM-20140430-02 | GAM-PLANNED CORRECTIVE / OWNER QC WALK | Closed | Corrective Maintenance | Forced | 02-High | 4/30/2014 | 4/30/2014 | 4/30/2014 | 3 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 3 |  |  | 2001212: GAM-PLANNED CORRECTIVE / OWNER QC WALKDOWN, FOUND FAULTY WIRING IN TOP CABINET ALL OF X4 BLOCK WAS WIRED NEUTRAL TO LINE | 401633213
PATTN-WKO-GAM-20140428-02 | GAM-PLANNED CORRECTIVE / CHANGED MOUNT | Closed | Corrective Maintenance | Forced | 02-High | 4/28/2014 | 4/28/2014 | 4/28/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 1.7667 | GAMSA-PRT-0432 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHANGED MOUNTING POST FOR SONIC | 401633214
PATTN-WKO-GAM-20140501-02 | GAM-2509-comm error | Closed | Corrective Maintenance | Forced | 02-High | 5/1/2014 | 5/1/2014 | 5/1/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.083333 | GAMSA-PRT-0288 | 1 | 2001212: GAM-2509-comm error- installed new kr330 relay kit in base cabinet rtsvc | 401633286
PATTN-WKO-GAM-20140426-04 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.6167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.75 |  |  | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633287
PATTN-WKO-GAM-20140502-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0422 | 40 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-04 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 | GAMSA-PRT-0066 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-05 | GAM-327 ALARM LTK CONFIRMATION ERROR / C | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 5.25 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CHANGED JOVENTA DURING THIRD PARTY INSPECTION OF GEARBOX | 401638191
PATTN-WKO-GAM-20140505-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 4.15 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 4.15 |  |  | USI-Borescope EOW Inspections/ Perform EOW Gearbox inspections | 401638556
PATTN-WKO-GAM-20140505-04 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 3.1333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 3.1333 |  |  | USI-EOW-Gearbox Borescope Inspections/ Perform EOW Gearbox Inspections | 401638557
PATTN-WKO-GAM-20140502-06 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 4.9167 |  |  | USI-EOW Gearbox Inspections/ Perform Gearbox Inspections | 401638558
PATTN-WKO-GAM-20140509-05 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.45 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 2.4667 |  |  | USI-EOW Gearbox Borescope Inspections/ Perform Gearbox Inspections | 401640904
PATTN-WKO-GAM-20140509-06 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.8167 |  |  | USI-EOW-Gearbox Borescope Inspections | 401640905
PATTN-WKO-GAM-20140509-07 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 3.1833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG08 | VEN-165 | 3.1833 |  |  | USI-EOW Gearbox Borescope inspections/perform gearbox inspections | 401640906
PATTN-WKO-GAM-20140509-08 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 2.6667 |  |  | USI-EOW Gearbox Inspections/ Perform Borescope inspections | 401640907
PATTN-WKO-GAM-20140512-03 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG01 | VEN-165 | 2.4167 |  |  | UPW-5819933-BORESCOPE INSPECTION OF GEAR | 401642558
PATTN-WKO-GAM-20140512-04 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG12 | VEN-165 | 0 |  |  | USI-EOW Borescope Inspections Gearbox | 401642559
PATTN-WKO-GAM-20140513-04 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.5 | Patton | Unplanned |  | PMI-004 | PATTN-WTG04 | VEN-165 | 2.5 |  |  | USI-EOW-Gearbox Borescope inspections | 401643573
PATTN-WKO-GAM-20140513-05 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.9 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 2.9 |  |  | USI-EOW Gearbox borescope inspections | 401643575
PATTN-WKO-GAM-20140514-06 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG03 | VEN-165 | 2.8167 |  |  | USI-EOW Gearbox Borescope Inspections/Perform Borescope Inspections | 401645458
PATTN-WKO-GAM-20140514-07 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.5833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG06 | VEN-165 | 2.5833 |  |  | USI-EOW-Gearbox Borescope Inspections/Perform gearbox inspections | 401645460
PATTN-WKO-GAM-20140513-06 | GAM-208-hu feedback error | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 1.5 | GAMSA-PRT-0050 | 1 | 2001223: GAM-208-hu pump drive falure- installed new contactor | 401645583
PATTN-WKO-GAM-20140515-04 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG17 | VEN-165 | 2.1667 |  |  | USI-EOW Gearbox Borescope inspections | 401645615
PATTN-WKO-GAM-20140515-05 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG16 | VEN-165 | 2 |  |  | USI-EOW Borescope inspections Gearbox | 401645616
PATTN-WKO-GAM-20140514-08 | GAM-300-anemometer failure | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/15/2014 | 25.4333 | Patton | Unplanned |  | PMI-004 | PATTN-WTG09 | VEN-165 | 0.53333 |  |  | 2001223: GAM-300-anemometer falure- found loose wiring - reconnected rtsvc | 401646567
PATTN-WKO-GAM-20140514-09 | GAM-403-high temp gearbox | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 1.0833 | Patton | Unplanned |  | PMI-004 | PATTN-WTG10 | VEN-165 | 0.46667 |  |  | 2001223: GAM-403-gearbox high temp | 401646594
PATTN-WKO-GAM-20140515-06 | GAM-721-wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.65 | Patton | Unplanned |  | PMI-004 | PATTN-WTG02 | VEN-165 | 2.65 |  |  | 2001223: GAM-721-wind vane falure- installed new wind vane | 401646689
PATTN-WKO-GAM-20140516-03 | GAM-shim gearbox-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox in accordance with maintenance procedure | 401651187
PATTN-WKO-GAM-20140516-04 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2.1667 | GAMSA-PRT-0431 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140516-04 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 | PATTN-WTG13 | VEN-165 | 2.1667 | GAMSA-PRT-0430 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140519-02 | GAM-shim gear box- pending task resoluti | Closed | Corrective Maintenance | Forced | 02-High | 5/19/2014 | 5/19/2014 | 5/19/2014 | 2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG11 | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox per procedure | 401652551
PATTN-WKO-GAM-20140523-03 | GAM-SHIM GEARBOX-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/23/2014 | 5/23/2014 | 5/23/2014 | 1.9167 | Patton | Unplanned |  | PMI-004 | PATTN-WTG07 | VEN-165 | 1.9167 |  |  | 2001223: GAM-shimed gearbox per procedure | 401658443
PATTN-WKO-GAM-20140528-02 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.75 | GAMSA-PRT-0374 | 5 | GAM-5248-active crowbar igbt errors | 401661282
PATTN-WKO-GAM-20140528-02 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 | PATTN-WTG05 | VEN-165 | 0.75 | GAMSA-PRT-0142 | 1 | GAM-5248-active crowbar igbt errors | 401661282
PATTN-WKO-GAM-20140508-03 | GAM-18 MONTH Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/9/2014 | 32.4833 | Patton | Planned |  | PMI-003 | PATTN-WTG12 | VEN-165 | 2.5833 | GAMSA-PRT-0401 | 30 | 2001212: GAM-18month minor maint complete per ck list 2001223: 18month maint complete per ck list | 500593590
PATTN-WKO-GAM-20140508-04 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/16/2014 | 198.7833 | Patton | Planned |  | PMI-003 | PATTN-WTG11 | VEN-165 | 1.6833 | GAMSA-PRT-0401 | 30 | 2001223: GAM-18 month maint complete per ck list | 500593836
PATTN-WKO-GAM-20140523-04 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/23/2014 | 5/23/2014 | 5/28/2014 | 128 | Patton | Planned |  | PMI-003 | PATTN-WTG01 | VEN-165 | 4.8 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500593839
PATTN-WKO-GAM-20140514-10 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 | PATTN-WTG13 | VEN-165 | 3.5167 | GAMSA-PRT-0435 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140514-10 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 | PATTN-WTG13 | VEN-165 | 3.5167 | GAMSA-PRT-0420 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140520-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/20/2014 | 5/20/2014 | 5/22/2014 | 55.6667 | Patton | Planned |  | PMI-003 | PATTN-WTG07 | VEN-165 | 4.8667 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500597336

## Parts
ID | Description | Qty | Vendor | Original ID