## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Asset ID | Vendor ID | Actual Hours | Part ID | Part Quantity | Comments | Original ID
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-01442 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-01441 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00357 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00358 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00645 | 3 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
TWINR-WKO-RPW-20131107-01 | Third day of the 1st annual maintenance per Repower service manual T-2.1-GP.WA.02-A (F)-EN. yearly maintenance safety equipment annual maintenance service agreement testing equipment like chain, fire extinguisher, running, climbing aid, first aid kit, crane and/ or lift inspection The maintenance is now complete on this turbine. | Closed | Maintenance |  |  | 11/7/2013 | 11/7/2013 | 11/7/2013 | 7.8833 | Twin Ridges |  |  |  |  | VEN-252 | 10 | REPWR-PRT-0280 | 2 |  | 60077492
TWINR-WKO-RPW-20140201-01 | T150 500hr. Rotor bolt torque. | Closed | Breakdown |  |  | 2/1/2014 | 2/1/2014 | 2/1/2014 | 2.8333 | Twin Ridges |  |  |  |  | VEN-252 | 4 |  |  |  | 30205423
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0458 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0058 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0172 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0430 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0431 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0459 | 1 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0460 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0461 | 2 |  | 401991109
PATTN-WKO-GAM-20150511-01 | GAM-ALARM 204 LOW HYDRALIC PREESURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/12/2015 | 13.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.4833 | GAMSA-PRT-0462 | 3 |  | 401991109
PATTN-WKO-GAM-20150511-02 | GAM-ALARM 2106 TEMP MEASUREENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/11/2015 | 5/11/2015 | 5/11/2015 | 1.15 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4833 |  |  | 2000541: LOCAL RESET | 401991714
PATTN-WKO-GAM-20150511-03 | GAM-30 Month Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/11/2015 | 5/11/2015 | 5/12/2015 | 12.6667 | Patton | Planned |  | PMI-003 |  | VEN-165 | 10.6667 | GAMSA-PRT-0449 | 20 | 30 month maintance | 500716986
PATTN-WKO-GAM-20150512-01 | GAM- WARNING 404 HIGH GEARBOX TEMP | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 1.5167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.9333 | GAMSA-PRT-0172 | 2 | 2000541: FOUND TWO LOUVERS BURT UP | 401990439
PATTN-WKO-GAM-20150512-02 | GAM- WARNING 114 LOW YAW BRAKE PRESSURE | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 |  |  | 2000541: ADJUSTED THE PRESSURES | 401990443
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0451 | 1 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0452 | 4 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0453 | 4 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0415 | 1 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0454 | 6 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0455 | 6 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150512-03 | GAM- AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2015 | 5/12/2015 | 5/12/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0456 | 2 | 2000541: AUTO LUBBER DM | 401991153
PATTN-WKO-GAM-20150513-01 | GAM-ALARM 403 HIG GEARBOX TEMP | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2015 | 5/13/2015 | 5/13/2015 | 3.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.9167 | GAMSA-PRT-0143 | 1 | 2000541: FOUND THE GEARBOX FAN FAILED REPLACED IT | 401991588
PATTN-WKO-GAM-20150615-01 | GAM-ALARM 2106 T-MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 6/15/2015 | 6/15/2015 | 6/15/2015 | 3.5833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.41667 |  |  | 2000541: LOCAL RESET | 402022836
PATTN-WKO-GAM-20150616-01 | REPLACED THE DECK SUPPORT RODS | Closed | Corrective Maintenance | Forced | 02-High | 6/16/2015 | 6/16/2015 | 6/16/2015 | 2.25 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 | GAMSA-PRT--0045 | 1 |  | 402024751
PATTN-WKO-GAM-20150616-02 | REPLACED THE DECK SUPPORT ROD | Closed | Corrective Maintenance | Forced | 02-High | 6/16/2015 | 6/16/2015 | 6/16/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT--0045 | 1 |  | 402024772
PATTN-WKO-GAM-20150618-01 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0451 | 1 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-01 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0453 | 4 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-01 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0415 | 1 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-01 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0454 | 6 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150618-01 | AUTOLUBBER DM | Closed | Corrective Maintenance | Forced | 02-High | 6/18/2015 | 6/18/2015 | 6/18/2015 | 0.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0455 | 6 | 2000541: AUTOLUBBER DM | 402027021
PATTN-WKO-GAM-20150621-01 | GAM-loal reset | Closed | Corrective Maintenance | Forced | 02-High | 6/21/2015 | 6/21/2015 | 6/21/2015 | 3.55 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.11667 |  |  | 2000541: local reset | 402029646
PATTN-WKO-GAM-20150622-01 | CHECKED THE SLIP RING FOR ARC MARKS | Closed | Corrective Maintenance | Forced | 02-High | 6/22/2015 | 6/22/2015 | 6/22/2015 | 1.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.8333 | GAMSA-PRT-0082 | 1 | 2000541: CHECKED THE SLIP RING FOR ARC MARKS | 402029810
PATTN-WKO-GAM-20140115-01 | gam-205 low hyro level | Closed | Corrective Maintenance | Forced | 02-High | 1/15/2014 | 1/15/2014 | 1/15/2014 | 2.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9167 |  |  | 2000856: gam-turbine low on hydro fluid , level was ok, found bad acc, replaced acc checked for leaks all checked good ran turbine | 401529646
PATTN-WKO-GAM-20140117-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532925
PATTN-WKO-GAM-20140117-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.33333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532953
PATTN-WKO-GAM-20140117-03 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.16667 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532981
PATTN-WKO-GAM-20140117-04 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401532999
PATTN-WKO-GAM-20140117-05 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533008
PATTN-WKO-GAM-20140117-06 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.2667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533033
PATTN-WKO-GAM-20140117-07 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.9833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533048
PATTN-WKO-GAM-20140117-08 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/17/2014 | 1/17/2014 | 1/17/2014 | 2.55 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.23333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533061
PATTN-WKO-GAM-20140118-01 | GAM-700 ALARM PLC/ CONVERTER COMMUNICATI | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 2.7333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMM FAILURE / LOCAL RESET | 401533074
PATTN-WKO-GAM-20140118-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 2.85 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533089
PATTN-WKO-GAM-20140118-03 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/18/2014 | 1/18/2014 | 1/18/2014 | 4.6167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401533109
PATTN-WKO-GAM-20140123-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/23/2014 | 1/23/2014 | 1/23/2014 | 3.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2000856: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401546597
PATTN-WKO-GAM-20140126-01 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/26/2014 | 1/26/2014 | 1/26/2014 | 1.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401546599
PATTN-WKO-GAM-20140126-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 1/26/2014 | 1/26/2014 | 1/26/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / RESET | 401546600
PATTN-WKO-GAM-20140129-01 | gam-107 yaw motor breaker | Closed | Corrective Maintenance | Forced | 02-High | 1/29/2014 | 1/29/2014 | 1/29/2014 | 10.5167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10.5167 |  |  | 2000856: gam-remove motor from yaw drive, removed yaw drive from nacelle | 401548165
PATTN-WKO-GAM-20140130-01 | gam-804 blade error | Closed | Corrective Maintenance | Forced | 02-High | 1/30/2014 | 1/30/2014 | 1/30/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.3167 | GAMSA-PRT-0031 | 1 | 2000856: gam-found elctro valve to be bent, drained pressure back from system and replaced valve | 401549323
PATTN-WKO-GAM-20140131-01 | gam-205 low hydro oil | Closed | Corrective Maintenance | Forced | 02-High | 1/31/2014 | 1/31/2014 | 1/31/2014 | 0.76667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.76667 | GAMSA-PRT-0419 | 1 | 2000856: gam-205 low hyro level found oil level to be ok, found level sensor to be nok changed out sensor alarm cleared ran tower | 401549374
PATTN-WKO-GAM-20140209-01 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 2/9/2014 | 2/9/2014 | 2/9/2014 | 1.6833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.41667 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401554554
PATTN-WKO-GAM-20140210-01 | GAM-2118 ALARM INTERBUS FAILURE / TROU | Closed | Corrective Maintenance | Forced | 02-High | 2/10/2014 | 2/10/2014 | 2/10/2014 | 0.38333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / TROUBLESHOOT / RESET | 401556214
PATTN-WKO-GAM-20140210-02 | GAM-2106 ALARM PREVENTATIVE DESIGN MOD | Closed | Corrective Maintenance | Forced | 02-High | 2/10/2014 | 2/10/2014 | 2/10/2014 | 5.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 |  |  | 2001212: GAM-2106 ALARM PREVENTATIVE DESIGN MOD | 401556232
PATTN-WKO-GAM-20140211-01 | GAM-300 ALARM ANEMOMETER FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 2/11/2014 | 2/11/2014 | 2/11/2014 | 5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 | GAMSA-PRT-0420 | 4 | 2001212: GAM-300 ANEMOMETER FAILURE / REPLACED ANEMOMETER AND WIND VANE, WHICH WERE DAMAGED BY ICE, FOUND GEARBOX PUMP WAS LEAKING AND REPLACED | 401556752
PATTN-WKO-GAM-20140211-02 | GAM-PLANNED INVESTIGATION OF YAW DRIVES | Closed | Corrective Maintenance | Forced | 02-High | 2/11/2014 | 2/11/2014 | 2/11/2014 | 5.3333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.5 |  |  | 2001212: GAM-PLANNED INVESTIGATION OF YAW DRIVES WITH ENGINEERS JUAN REDIN, AND RIGOBERTO MEDENA | 401559219
PATTN-WKO-GAM-20140212-01 | GAM-PLANNED INVESTIGATION OF YAW SYSTEM | Closed | Corrective Maintenance | Forced | 02-High | 2/12/2014 | 2/12/2014 | 2/12/2014 | 2.4833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED INVESTIGATION OF YAW SYSTEM WITH ENGINEERS JUAN REDIN AND RIGOBERTO MEDENA | 401559259
PATTN-WKO-GAM-20140213-01 | GAM-2118 ALARM INTERBUS FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/13/2014 | 0.68333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / INSPECTED FOUND LOOSE CARD | 401559273
PATTN-WKO-GAM-20140218-01 | gam-5237 error on rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/18/2014 | 2/18/2014 | 2/19/2014 | 24.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7667 | GAMSA-PRT-0421 | 9 | 2000856: gam-5237 error on rotor phase S went up tower checked converter all looked good, looked at slip ring found arc marks on all phases of slip ring. removed old slip replaced with new. replaced tape on slip ring knuckles applyed the proper paint to | 401567400
PATTN-WKO-GAM-20140218-01 | gam-5237 error on rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/18/2014 | 2/18/2014 | 2/19/2014 | 24.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7667 | GAMSA-PRT-0416 | 20 | 2000856: gam-5237 error on rotor phase S went up tower checked converter all looked good, looked at slip ring found arc marks on all phases of slip ring. removed old slip replaced with new. replaced tape on slip ring knuckles applyed the proper paint to | 401567400
PATTN-WKO-GAM-20140213-02 | gam-5237 error rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/20/2014 | 35.7167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10 | GAMSA-PRT-0421 | 9 | 2000856: gam-5237-found slip ring bad replaced slip ring | 401567423
PATTN-WKO-GAM-20140213-02 | gam-5237 error rotor phase s | Closed | Corrective Maintenance | Forced | 02-High | 2/13/2014 | 2/13/2014 | 2/20/2014 | 35.7167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 10 | GAMSA-PRT-0416 | 20 | 2000856: gam-5237-found slip ring bad replaced slip ring | 401567423
PATTN-WKO-GAM-20140221-01 | gam-5238-error phase t | Closed | Corrective Maintenance | Forced | 02-High | 2/21/2014 | 2/21/2014 | 2/22/2014 | 16.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8667 | GAMSA-PRT-0416 | 20 |  | 401569549
PATTN-WKO-GAM-20140221-01 | gam-5238-error phase t | Closed | Corrective Maintenance | Forced | 02-High | 2/21/2014 | 2/21/2014 | 2/22/2014 | 16.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8667 | GAMSA-PRT-0421 | 9 |  | 401569549
PATTN-WKO-GAM-20140225-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 2/25/2014 | 2/25/2014 | 2/25/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0421 | 9 | 2000856: gam-cleaned out slip ring, inspected slip ring body all checked ok ran turbine | 401571051
PATTN-WKO-GAM-20140225-02 | gam-slip ring inspection cleaning | Closed | Corrective Maintenance | Forced | 02-High | 2/25/2014 | 2/25/2014 | 2/25/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 |  |  | 2000856: gam-cleaning inspection on slip ring, cleaned out slip ring all checked ok ran turbine | 401573326
PATTN-WKO-GAM-20140224-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 2/24/2014 | 2/24/2014 | 2/24/2014 | 3.0667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5 |  |  | 2000856: gam-inspection of slip ring found to be dirty, cleaned slip ring and replaced brushes | 401573340
PATTN-WKO-GAM-20140303-01 | gam-pitch ram cover dm | Closed | Corrective Maintenance | Forced | 02-High | 3/3/2014 | 3/3/2014 | 3/3/2014 | 0.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.83333 |  |  | 2000856: gam-installed new pitch ram shaft cover | 401576693
PATTN-WKO-GAM-20140306-01 | gam-107 yaw motor circuit breaker | Closed | Corrective Maintenance | Forced | 02-High | 3/6/2014 | 3/6/2014 | 3/6/2014 | 8.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 9.5 |  |  | 2000856: gam-found brokin drive removed yaw replace with new drive checked motor and drive for proper fit all checked ok ran turbine | 401580634
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0031 | 2 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0003 | 1 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0270 | 60 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0064 | 1 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0196 | 10 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140305-01 | gam-punch list item | Closed | Corrective Maintenance | Forced | 02-High | 3/5/2014 | 3/5/2014 | 3/5/2014 | 7.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7.7 | GAMSA-PRT-0401 | 30 | 2000856: gam-punch list item | 401581140
PATTN-WKO-GAM-20140304-01 | gam-118 yaw motor error | Closed | Corrective Maintenance | Forced | 02-High | 3/4/2014 | 3/4/2014 | 3/4/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.2167 | GAMSA-PRT-0401 | 30 |  | 401581174
PATTN-WKO-GAM-20140304-01 | gam-118 yaw motor error | Closed | Corrective Maintenance | Forced | 02-High | 3/4/2014 | 3/4/2014 | 3/4/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.2167 | GAMSA-PRT-0196 | 30 |  | 401581174
PATTN-WKO-GAM-20140307-01 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/7/2014 | 3/7/2014 | 3/7/2014 | 0.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 | GAMSA-PRT-0425 | 1 | 2000677: gam-cleaning slip ring, replace brushes, check for leakes on yaw drive, and cleaning belly | 401582862
PATTN-WKO-GAM-20140310-01 | GAM-404 ALARM HIGH TEMP MAIN BEARING | Closed | Corrective Maintenance | Forced | 02-High | 3/10/2014 | 3/10/2014 | 3/10/2014 | 0.66667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-404 ALARM HIGH TEMP MAINBEARING / CHANGED TEMP CARD | 401583356
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0368 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0326 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140307-02 | GAM-8041201 HYDRAULIC RE-ROUTING | Closed | Retrofit | Forced | 03-Medium | 3/7/2014 | 3/7/2014 | 3/7/2014 | 1 | Patton | Unplanned |  | PMI-002 |  | VEN-165 | 1 | GAMSA-PRT-0333 | 1 | installed hydro dm | 500481492
PATTN-WKO-GAM-20140311-01 | gam-inspection of nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/12/2014 | 25.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.1167 |  |  | 2000856: gam-checked the op of the louvers. reset the cams. ran tower | 401584977
PATTN-WKO-GAM-20140311-02 | gam-check nacelle louvers | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 2.1333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1333 |  |  | 2000856: gam-check nacelle louvers for proper op, found they were opening backwards. switched wires reset louver cams and ran tower | 401585000
PATTN-WKO-GAM-20140311-03 | gam-naccelle louver inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 1.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.6 |  |  | 2000856: gam-checked nacelle louvers, found opening backwards, reset cams and switch wires around ran turbine | 401585004
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0196 | 60 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0401 | 30 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0069 | 10 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140311-04 | gam-punchlist items | Closed | Corrective Maintenance | Forced | 02-High | 3/11/2014 | 3/11/2014 | 3/11/2014 | 3.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.2833 | GAMSA-PRT-0413 | 2 | 2000856: gam-punchlist items | 401585023
PATTN-WKO-GAM-20140312-01 | gam-2106 temp fail | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2000856: gam-2106 reset top cabinet all temps came back ran turbine | 401585166
PATTN-WKO-GAM-20140312-02 | gam-slip ring inspection | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 2.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9 | GAMSA-PRT-0064 | 1 | 2000856: gam-installed north sensor, cleaned out slip ring and changed brushes | 401585267
PATTN-WKO-GAM-20140312-03 | GAM-MODIFIED ROOF AND INSTALLED NORTH SE | Closed | Corrective Maintenance | Forced | 02-High | 3/12/2014 | 3/12/2014 | 3/12/2014 | 1.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.25 | GAMSA-PRT-0064 | 1 | 2001212: GAM-MODIFIED ROOF AND INSTALLED NORTH SENSOR | 401585289
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0426 | 1 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140314-01 | GAM-PUNCHLIST AND TOWER CLEANING | Closed | Corrective Maintenance | Forced | 02-High | 3/14/2014 | 3/14/2014 | 3/14/2014 | 4.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.0833 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PUNCHLIST AND TOWER CLEANING | 401588802
PATTN-WKO-GAM-20140315-01 | GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADE | Closed | Corrective Maintenance | Forced | 02-High | 3/15/2014 | 3/15/2014 | 3/15/2014 | 5.7 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5167 | GAMSA-PRT-0094 | 1 | 2001212: GAM-804 ALARM DIFFERENCE BETWEEN 2 BLADES VERY HIGH / CHANGED BALLUF CABLE | 401590249
PATTN-WKO-GAM-20140317-01 | GAM-800 ALARM PITCH ACTIVATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/17/2014 | 3/17/2014 | 3/17/2014 | 1.75 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-800 ALARM PITCH ACTIVATION ERROR / CHANGED PROP VALVE ON BLADE C | 401590643
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 3.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED TOWER / CLEANED SLIP RING AND CHANGED BRUSH ES | 401592676
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0398 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0427 | 4 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140318-02 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 3/18/2014 | 3/18/2014 | 3/18/2014 | 5.3167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED LOUVER CONTROL / CLEANED SLIP RING AND CHANGED BRUSHES / CHANGED HUB CABINET BUSHINGS | 401592680
PATTN-WKO-GAM-20140319-01 | GAM-GEAR BOX OIL SAMPLE / REPLACED MIS | Closed | Corrective Maintenance | Forced | 02-High | 3/19/2014 | 3/19/2014 | 3/19/2014 | 0.6 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0398 | 1 | 2001212: GAM-GEARBOX OIL SAMPLE / REPLACED NUTS ON VICKERS VALVES | 401592858
PATTN-WKO-GAM-20140320-01 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 5.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LOCAL RESET | 401593615
PATTN-WKO-GAM-20140320-02 | GAM-2106 ALARM TEMP MODULE FAILURE / L | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 1.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-2106 ALARM TEMP MODULE FAILURE / LANDED GEARBOX SHIELDING | 401594219
PATTN-WKO-GAM-20140320-03 | GAM-426 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 3/20/2014 | 3/20/2014 | 3/20/2014 | 0.88333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 | GAMSA-PRT-0381 | 1 | 2001212: GAM-426 ALARM OGS / CHANGED SENSOR | 401594279
PATTN-WKO-GAM-20140321-01 | GAM-327 ALARM LTK CONFIRMATION ERROR | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 0.41667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 |  |  | 2001212: GAM-327 LTK CONFIRMATION ERROR / CHANGED LOUVERS | 401594941
PATTN-WKO-GAM-20140321-02 | GAM-PLANNED ROOF REPAIR / GREASED YAW | Closed | Corrective Maintenance | Forced | 02-High | 3/21/2014 | 3/21/2014 | 3/21/2014 | 4.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.5 |  |  | 2001212: GAM-PLANNED ROOF REPAIR / GREASED YAW | 401595371
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0416 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0421 | 1 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0427 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-01 | GAM-5237 ALARM ERROR IN PHASE S OF THE I | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 10 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 8 | GAMSA-PRT-0420 | 4 | 2001212: GAM-5237 ALARM ERROR IN PHASE S OF THE INVERTER / CHANGED SLIP RING, HUB CABINET BUSHINGS, AND TORQUED YAW STACKS | 401598025
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0078 | 3 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0196 | 34 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0069 | 13 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0413 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140324-02 | GAM-PLANNED CLEANING OF SLIP RING, TORQU | Closed | Corrective Maintenance | Forced | 02-High | 3/24/2014 | 3/24/2014 | 3/24/2014 | 2.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, AND CHANGED HUB CABINET BUSHINGS 2001212: GAM-PLANNED PREVENTATIVE SLIP RING MAINTENANCE, TORQUED AND GREASED YAW STACKS, REPLACED HUB CABINET BUSHINGS. NOTE: ON ALL | 401598067
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0416 | 20 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0421 | 9 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0064 | 1 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-01 | GAM-PLANNED SLIP RING AND YAW INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 5.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.75 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED SLIP RING AND YAW INSPECTION / CLEANED, CHANGED BRUSHES, AND FIXED THERMAL TAPE ON SLIP RING / TORQUED AND GREASED YAW CLAMPS / CHANGED NORTH SENSOR / REPLACED HUB CABINET BUSHINGS | 401599346
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0425 | 1 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0427 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140325-02 | GAM-PLANNED YAW AND SLIP RING INSPECTION | Closed | Corrective Maintenance | Forced | 02-High | 3/25/2014 | 3/25/2014 | 3/25/2014 | 2.35 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 | GAMSA-PRT-0420 | 4 | 2001212: GAM-PLANNED YAW AND SLIP RING INSPECTION / CLEANED AND CHANGED SLIP RING BRUSHES / TORQUED AND GREASED YAW CLAMPS / C HANGED HUB CABINET BUSHINGS | 401599574
PATTN-WKO-GAM-20140327-01 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 4 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / PLANNED INSTALLATION OF KBT YAW DRIVE | 401601799
PATTN-WKO-GAM-20140327-02 | GAM-PLANNED CORRECTIVE / INSTALLATION | Closed | Corrective Maintenance | Forced | 02-High | 3/27/2014 | 3/27/2014 | 3/27/2014 | 3.85 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLATION OF HG YAW DRIVE | 401601823
PATTN-WKO-GAM-20140328-01 | GAM-PLANNED CORRECTIVE / NOTICED SONIC | Closed | Corrective Maintenance | Forced | 02-High | 3/28/2014 | 3/28/2014 | 3/28/2014 | 0.63333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / ADJUSTED SONIC | 401602119
PATTN-WKO-GAM-20140330-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 3/30/2014 | 3/30/2014 | 3/30/2014 | 3.7833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.5 | GAMSA-PRT-0386 | 1 | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / CHANGED TRANSFORMER FUSE B | 401603723
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0374 | 5 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0142 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-01 | GAM-PLANNED CORRECTIVE ON SUPPORT ARM FO | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 6.2167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6.5 | GAMSA-PRT-0428 | 1 | 2001212: GAM-PLANNED CORRECTIVE ON SUPPORT ARM FOR SONIC/ANEMOMETER ASSEMBLY / REPLACED SUPPORT ARM, CLEANED HUB, AND GREASED BLAD ES B AND C 2001212: GAM-PLANNED CORRECTIVE / REPLACED SUPPORT ARM FOR SONIC/ANEMOMETER / GREASED BLADES A AND B / C | 401605583
PATTN-WKO-GAM-20140331-02 | GAM-804 ALARM DIFFERENCE BETWEEN BLADES | Closed | Corrective Maintenance | Forced | 02-High | 3/31/2014 | 3/31/2014 | 3/31/2014 | 1.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 |  |  | 2001212: GAM-804 ALARM DIFFERENCE IN BLADES VERY HIGH / CHANGED AO CARD IN HUB CABINET | 401605611
PATTN-WKO-GAM-20140401-01 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.5167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0429 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHECKED CONVERTER TEMPS, CHANGED SIGHT GLASS ON GEARBOX | 401606444
PATTN-WKO-GAM-20140401-02 | GAM-PLANNED CORRECTIVE / HAD 25 DEGREE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.0333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / WENT UP TO CHECK DIFFERENCES IN CONVERTER TEMPS AT CUSTOMERS REQUEST | 401607123
PATTN-WKO-GAM-20140401-03 | GAM-PLANNED CORRECTIVE / HAD HIGHER TE | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 0.8 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.25 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSPECTED CONVERTER AT CUSTOMERS REQUEST | 401607130
PATTN-WKO-GAM-20140401-04 | GAM-2118 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 1.3833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2118 ALARM INTERBUS FAILURE / LOCAL RESET | 401607137
PATTN-WKO-GAM-20140401-05 | GAM-5200 ALARM MAGNETOTHERMIC TRIP OF TH | Closed | Corrective Maintenance | Forced | 02-High | 4/1/2014 | 4/1/2014 | 4/1/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 |  |  | 2001212: GAM-5200 ALARM MAGNETOTHERMIC TRIP OF THE LIINE PROTECTION / TRANSFORMER LOUVER CLOSED OVERHEATING CONVERTER | 401607159
PATTN-WKO-GAM-20140402-01 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/2/2014 | 4/2/2014 | 4/2/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.25 |  |  | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / CHANGED GATEWAY, AND BLED BOTH YAW BRAKE SYSTEM AND ROTOR BRAKE SYSTEM | 401607546
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7 | GAMSA-PRT-0430 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-01 | GAM-PLANNED CORRECTIVE / REPLACED HALF | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 6.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 7 | GAMSA-PRT-0431 | 4 | 2001212: GAM-PLANNED CORRECTIVE / TOOK MEASUREMENTS AND CHANGED HALF MOONS AND BEARINGS ON PITCH RAMS A AND B | 401609803
PATTN-WKO-GAM-20140403-02 | GAM-2106 ALARM INTERBUS FAILURE / LOCA | Closed | Corrective Maintenance | Forced | 02-High | 4/3/2014 | 4/3/2014 | 4/3/2014 | 0.98333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 |  |  | 2001212: GAM-2106 ALARM INTERBUS FAILURE / LOCAL RESET | 401609844
PATTN-WKO-GAM-20140404-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 1.4833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0172 | 2 | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / FOUND 2 BAD ACTUATORS AND CHANGED THEM | 401610176
PATTN-WKO-GAM-20140404-02 | GAM-700 ALARM PLC/CONVERTER COMMUNICATIO | Closed | Corrective Maintenance | Forced | 02-High | 4/4/2014 | 4/4/2014 | 4/4/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.5 | GAMSA-PRT-0288 | 1 | 2001212: GAM-700 ALARM PLC/CONVERTER COMMUNICATION FAILURE / TESTED KR330G FOUND BAD RESISTANCE AND CHANGED | 401610307
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.2833 | GAMSA-PRT-0066 | 20 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140414-01 | GAM-327-ltk conformation warning | Closed | Corrective Maintenance | Forced | 02-High | 4/14/2014 | 4/14/2014 | 4/14/2014 | 5.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.2833 | GAMSA-PRT-0172 | 1 | 2001212: GAM-troubleshoot and adjusted ltk vent loovers and installed 1 accuator also added oil to yaw gears | 401618608
PATTN-WKO-GAM-20140408-01 | GAM-203 ALARM LOW PRESSURE HG / CHANGE | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/9/2014 | 6.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.4833 |  |  | 2001212: GAM-203 ALARM LOW PRESSURE HG / CHANGED BLADE C PITCH BLOCK | 401620946
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0415 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140408-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/8/2014 | 4/8/2014 | 4/8/2014 | 2.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0424 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CONTACTOR AND RELAY | 401620948
PATTN-WKO-GAM-20140411-01 | GAM-1823 ALARM COOLANT CONFIRMATION FAIL | Closed | Corrective Maintenance | Forced | 02-High | 4/11/2014 | 4/11/2014 | 4/11/2014 | 3.6333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4 | GAMSA-PRT-0172 | 1 | 2001212: GAM-1823 ALARM COOLANT CONFIRMATION FAILURE / FOUND BAD LOUVER AND CHANGED | 401620949
PATTN-WKO-GAM-20140415-01 | GAM-327 ALARM LTK CONFIRMATION ERROR / | Closed | Corrective Maintenance | Forced | 02-High | 4/15/2014 | 4/15/2014 | 4/15/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CLEANED RADIATORS | 401620950
PATTN-WKO-GAM-20140413-01 | GAM-410 ALARM OGS / CHANGED SENSOR | Closed | Corrective Maintenance | Forced | 02-High | 4/13/2014 | 4/13/2014 | 4/13/2014 | 1.95 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 | GAMSA-PRT-0381 | 1 | 2001212: GAM-410 OGS / CHANGED SENSOR | 401620951
PATTN-WKO-GAM-20140416-01 | GAM-2198 ALARM TEMP MEASUREMENT FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 4/16/2014 | 4/16/2014 | 4/16/2014 | 5.3833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6 | GAMSA-PRT-0172 | 2 | 2001212: GAM-2198 ALARM TEMP MODULE FAILURE / CHANGED TEMP CARD, GREASED YAW AND BLED SYSTEM, CHANGED 2 LOUVERS | 401621045
PATTN-WKO-GAM-20140419-01 | GAM-401 ALARM LOW PRESSURE GEAR BOX / | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 1.2833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624105
PATTN-WKO-GAM-20140419-02 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.8 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624111
PATTN-WKO-GAM-20140419-03 | GAM-401 ALARM LOW PRESSURE GEARBOX / A | Closed | Corrective Maintenance | Forced | 02-High | 4/19/2014 | 4/19/2014 | 4/19/2014 | 3.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-401 ALARM LOW PRESSURE GEARBOX / ADJUSTED PRESSURE STAT ON GEARBOX | 401624119
PATTN-WKO-GAM-20140420-01 | GAM-5216 ALARM GRID VOLTAGE FAILURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/20/2014 | 5.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.5 |  |  | 2001212: GAM-5216 ALARM GRID VOLTAGE FAILURE / LEAK TO GROUND ON YAW MOTOR, CHANGED YAW MOTOR 181A | 401624125
PATTN-WKO-GAM-20140420-02 | GAM-PLANNED CORRECTIVE / INSTALLED YAW | Closed | Corrective Maintenance | Forced | 02-High | 4/20/2014 | 4/20/2014 | 4/21/2014 | 29.2333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.5 | GAMSA-PRT-0066 | 10 | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED YAW DRIVE | 401624141
PATTN-WKO-GAM-20140421-01 | GAM-114 ALARM YAW BRAKE LOW PRESSURE / | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 0.61667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-114 ALARM YAW BRAKE LOW PRESSURE / BLED YAW BRAKE SYSTEM | 401624153
PATTN-WKO-GAM-20140421-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/21/2014 | 4/21/2014 | 4/21/2014 | 2.55 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.75 | GAMSA-PRT-0125 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED CARD, GREASED AND BLED YAW CLAMPS | 401624183
PATTN-WKO-GAM-20140422-01 | GAM-PLANNED CORRECTIVE / BLED BRAKE SY | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/22/2014 | 6.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 6 | GAMSA-PRT-0172 | 3 | 2001212: GAM-PLANNED CORRECTIVE / BLED BRAKE SYSTEM, FOUND LOOSE BOLTS ON YAW DRIVES AND TIGHTENED, CLEANED TURBINE | 401625671
PATTN-WKO-GAM-20140423-01 | GAM-5209-coolant circuit falure | Closed | Corrective Maintenance | Forced | 02-High | 4/23/2014 | 4/23/2014 | 4/23/2014 | 0.78333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.78333 |  |  | 2001212: GAM-5219-cooling circuit falure- troubleshoot and tightend wiring | 401626574
PATTN-WKO-GAM-20140422-02 | GAM-107 yaw motor circuit breakers | Closed | Corrective Maintenance | Forced | 02-High | 4/22/2014 | 4/22/2014 | 4/24/2014 | 84.4 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.9 | GAMSA-PRT-0172 | 1 | 2001212: GAM-107 yaw motors circuit breakers - call in removed broken left front yaw assembly could not install new assembly due to high winds - returned 24th installed new assembly with new yaw motor also installed new upper ltk louver motor rtsvc | 401627759
PATTN-WKO-GAM-20140424-01 | GAM-721 wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 4/24/2014 | 4/24/2014 | 4/24/2014 | 1.1167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.1167 |  |  | 2001212: GAM-721 wind vane falure- troubleshoot wind vane | 401627771
PATTN-WKO-GAM-20140425-01 | GAM-PLANNED CORRECTIVE INSTALLED RETRO O | Closed | Corrective Maintenance | Forced | 02-High | 4/25/2014 | 4/25/2014 | 4/25/2014 | 2.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.75 |  |  | 2001212: GAM-PLANNED CORRECTIVE / INSTALLED RETRO ON LIGHTENING SYSTEM FOR ENGINEERS | 401633211
PATTN-WKO-GAM-20140426-01 | GAM-208 ALARM HG FEEDBACK FAILURE / RE | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.3667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0003 | 1 | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633212
PATTN-WKO-GAM-20140430-01 | GAM-PLANNED CORRECTIVE / OWNER QC WALK | Closed | Corrective Maintenance | Forced | 02-High | 4/30/2014 | 4/30/2014 | 4/30/2014 | 3 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3 |  |  | 2001212: GAM-PLANNED CORRECTIVE / OWNER QC WALKDOWN, FOUND FAULTY WIRING IN TOP CABINET ALL OF X4 BLOCK WAS WIRED NEUTRAL TO LINE | 401633213
PATTN-WKO-GAM-20140428-01 | GAM-PLANNED CORRECTIVE / CHANGED MOUNT | Closed | Corrective Maintenance | Forced | 02-High | 4/28/2014 | 4/28/2014 | 4/28/2014 | 1.5667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.7667 | GAMSA-PRT-0432 | 1 | 2001212: GAM-PLANNED CORRECTIVE / CHANGED MOUNTING POST FOR SONIC | 401633214
PATTN-WKO-GAM-20140501-01 | GAM-2509-comm error | Closed | Corrective Maintenance | Forced | 02-High | 5/1/2014 | 5/1/2014 | 5/1/2014 | 0.083333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.083333 | GAMSA-PRT-0288 | 1 | 2001212: GAM-2509-comm error- installed new kr330 relay kit in base cabinet rtsvc | 401633286
PATTN-WKO-GAM-20140426-02 | GAM-208 ALARM HG FEEDBACK FAILURE / CH | Closed | Corrective Maintenance | Forced | 02-High | 4/26/2014 | 4/26/2014 | 4/26/2014 | 1.6167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 |  |  | 2001212: GAM-208 ALARM HG FEEDBACK FAILURE / CHANGED AUX CONTACTOR | 401633287
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0172 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0422 | 40 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-01 | GAM-327 ALARM LTK CONFIRMATION FAILURE | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 | GAMSA-PRT-0066 | 1 | 2001212: GAM-327 ALARM LTK CONFIRMATION FAILURE / CHANGED JOVENTA DURING THIRD PARTY GEARBOX INSPECTION | 401634227
PATTN-WKO-GAM-20140502-02 | GAM-327 ALARM LTK CONFIRMATION ERROR / C | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 5.25 |  |  | 2001212: GAM-327 ALARM LTK CONFIRMATION ERROR / CHANGED JOVENTA DURING THIRD PARTY INSPECTION OF GEARBOX | 401638191
PATTN-WKO-GAM-20140505-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 4.15 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.15 |  |  | USI-Borescope EOW Inspections/ Perform EOW Gearbox inspections | 401638556
PATTN-WKO-GAM-20140505-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/5/2014 | 5/5/2014 | 5/5/2014 | 3.1333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.1333 |  |  | USI-EOW-Gearbox Borescope Inspections/ Perform EOW Gearbox Inspections | 401638557
PATTN-WKO-GAM-20140502-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/2/2014 | 5/2/2014 | 5/2/2014 | 4.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 4.9167 |  |  | USI-EOW Gearbox Inspections/ Perform Gearbox Inspections | 401638558
PATTN-WKO-GAM-20140509-01 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.45 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4667 |  |  | USI-EOW Gearbox Borescope Inspections/ Perform Gearbox Inspections | 401640904
PATTN-WKO-GAM-20140509-02 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8167 |  |  | USI-EOW-Gearbox Borescope Inspections | 401640905
PATTN-WKO-GAM-20140509-03 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 3.1833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 3.1833 |  |  | USI-EOW Gearbox Borescope inspections/perform gearbox inspections | 401640906
PATTN-WKO-GAM-20140509-04 | UPW-BORESCOPE INSPECTION OF GEARBOX-5819 | Closed | Corrective Maintenance | Forced | 02-High | 5/9/2014 | 5/9/2014 | 5/9/2014 | 2.6667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.6667 |  |  | USI-EOW Gearbox Inspections/ Perform Borescope inspections | 401640907
PATTN-WKO-GAM-20140512-01 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.4167 |  |  |  | 401642558
PATTN-WKO-GAM-20140512-02 | UPW-5819933-BORESCOPE INSPECTION OF GEAR | Closed | Corrective Maintenance | Forced | 02-High | 5/12/2014 | 5/12/2014 | 5/12/2014 | 2.4667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0 |  |  | USI-EOW Borescope Inspections Gearbox | 401642559
PATTN-WKO-GAM-20140513-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.5 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5 |  |  | USI-EOW-Gearbox Borescope inspections | 401643573
PATTN-WKO-GAM-20140513-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2.9 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.9 |  |  | USI-EOW Gearbox borescope inspections | 401643575
PATTN-WKO-GAM-20140514-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.8167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.8167 |  |  | USI-EOW Gearbox Borescope Inspections/Perform Borescope Inspections | 401645458
PATTN-WKO-GAM-20140514-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 2.5833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.5833 |  |  | USI-EOW-Gearbox Borescope Inspections/Perform gearbox inspections | 401645460
PATTN-WKO-GAM-20140513-03 | GAM-208-hu feedback error | Closed | Corrective Maintenance | Forced | 02-High | 5/13/2014 | 5/13/2014 | 5/13/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.5 | GAMSA-PRT-0050 | 1 | 2001223: GAM-208-hu pump drive falure- installed new contactor | 401645583
PATTN-WKO-GAM-20140515-01 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 |  |  | USI-EOW Gearbox Borescope inspections | 401645615
PATTN-WKO-GAM-20140515-02 | UPW-5819933-EOW BOROSCOPE GEARBOX INSPEC | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | USI-EOW Borescope inspections Gearbox | 401645616
PATTN-WKO-GAM-20140514-03 | GAM-300-anemometer failure | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/15/2014 | 25.4333 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.53333 |  |  | 2001223: GAM-300-anemometer falure- found loose wiring - reconnected rtsvc | 401646567
PATTN-WKO-GAM-20140514-04 | GAM-403-high temp gearbox | Closed | Corrective Maintenance | Forced | 02-High | 5/14/2014 | 5/14/2014 | 5/14/2014 | 1.0833 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.46667 |  |  | 2001223: GAM-403-gearbox high temp | 401646594
PATTN-WKO-GAM-20140515-03 | GAM-721-wind vane falure | Closed | Corrective Maintenance | Forced | 02-High | 5/15/2014 | 5/15/2014 | 5/15/2014 | 2.65 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.65 |  |  | 2001223: GAM-721-wind vane falure- installed new wind vane | 401646689
PATTN-WKO-GAM-20140516-01 | GAM-shim gearbox-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox in accordance with maintenance procedure | 401651187
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 | GAMSA-PRT-0431 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140516-02 | GAM-replace blade C pitch ram half moons | Closed | Corrective Maintenance | Forced | 02-High | 5/16/2014 | 5/16/2014 | 5/16/2014 | 2.1667 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2.1667 | GAMSA-PRT-0430 | 2 | 2001223: GAM-installed new blade C pitch ram cylinder knuckle - pending task resolution | 401651188
PATTN-WKO-GAM-20140519-01 | GAM-shim gear box- pending task resoluti | Closed | Corrective Maintenance | Forced | 02-High | 5/19/2014 | 5/19/2014 | 5/19/2014 | 2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 2 |  |  | 2001223: GAM-shimed gearbox per procedure | 401652551
PATTN-WKO-GAM-20140523-01 | GAM-SHIM GEARBOX-pending task resolution | Closed | Corrective Maintenance | Forced | 02-High | 5/23/2014 | 5/23/2014 | 5/23/2014 | 1.9167 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 1.9167 |  |  | 2001223: GAM-shimed gearbox per procedure | 401658443
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0374 | 5 |  | 401661282
PATTN-WKO-GAM-20140528-01 | GAM-5248-active crowbar igbt errors | Closed | Corrective Maintenance | Forced | 02-High | 5/28/2014 | 5/28/2014 | 5/28/2014 | 19.2 | Patton | Unplanned |  | PMI-004 |  | VEN-165 | 0.75 | GAMSA-PRT-0142 | 1 |  | 401661282
PATTN-WKO-GAM-20140508-01 | GAM-18 MONTH Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/9/2014 | 32.4833 | Patton | Planned |  | PMI-003 |  | VEN-165 | 2.5833 | GAMSA-PRT-0401 | 30 | 2001212: GAM-18month minor maint complete per ck list 2001223: 18month maint complete per ck list | 500593590
PATTN-WKO-GAM-20140508-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/8/2014 | 5/8/2014 | 5/16/2014 | 198.7833 | Patton | Planned |  | PMI-003 |  | VEN-165 | 1.6833 | GAMSA-PRT-0401 | 30 | 2001223: GAM-18 month maint complete per ck list | 500593836
PATTN-WKO-GAM-20140523-02 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/23/2014 | 5/23/2014 | 5/28/2014 | 128 | Patton | Planned |  | PMI-003 |  | VEN-165 | 4.8 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500593839
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 |  | VEN-165 | 3.5167 | GAMSA-PRT-0435 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140514-05 | GAM-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/14/2014 | 5/14/2014 | 5/16/2014 | 54.05 | Patton | Planned |  | PMI-003 |  | VEN-165 | 3.5167 | GAMSA-PRT-0420 | 1 | 2001223: GAM-18 month maint complete per ck list | 500594107
PATTN-WKO-GAM-20140520-01 | GAM-18-Minor maint. G9X Patton | Closed | Preventive Maintenance | Planned | 03-Medium | 5/20/2014 | 5/20/2014 | 5/22/2014 | 55.6667 | Patton | Planned |  | PMI-003 |  | VEN-165 | 4.8667 | GAMSA-PRT-0435 | 1 | 2001223: 18 month maintenance complete per ck list | 500597336
TWINR-WKO-RPW-20130403-01 | ERROR 1630 Disc filter adaption implausible The poximity sensor on the high speed shaft on the generator side is faulty. We do not have any in our inventory so we will order a new one and it will have to be replaced. The turbine was reset. The turbine is up and operational at this time, but it might go down again. | Closed | Breakdown |  |  | 4/3/2013 | 4/3/2013 | 4/3/2013 | 5.1333 | Twin Ridges |  |  |  |  | VEN-252 | 2 |  |  |  | 30166618
KRAYN-WKO-NDX-20120409-01 | Nordex technicians arrived at tower. | Closed | Un-Planned Work |  |  | 4/9/2012 | 4/9/2012 | 4/9/2012 | 2.5833 | Highland 1 |  |  |  |  | VEN-304 | 2.9167 |  |  | Nordex technicians arrived at tower. Martin climbed tower. Sent down chain hoist. Hoisted tools and equipment. Changed gear oil filter, wiped out housing, installed new filter. | 700074546
KRAYN-WKO-NDX-20120404-01 | Nordex Technicians arrived at tower 13 at appx. | Closed | Un-Planned Work |  |  | 4/4/2012 | 4/4/2012 | 3/26/2012 | 226.7833 | Highland 1 |  |  |  |  | VEN-304 | 11.5 | KRAYN-NDX-PRT-0781 | 2 | Nordex Technicians arrived at tower 13 at appx. 08:00. Remained on hold for appx. 3.5 hours while the crane crew worked out the fault with their equipment. By appx. 11:45, nordex techs began climbing ladder, replacing yaw drives, torquing yaw drives, installing motors, cleaning up. | 600039339
TWINR-WKO-RPW-20140911-01 | annual maintenance | Closed | Maintenance |  |  | 9/11/2014 | 9/11/2014 | 9/11/2014 | 6.46 | Twin Ridges |  |  |  |  | VEN-252 | 8.5 |  |  | Data Entry | temp ID
KRAYN-WKO-NDX-20150107-01 | Check In - NDX - 81854 - Troubleshooting | Closed |  |  |  | 7/1/2015 | 1/7/2015 | 1/7/2015 | 6.0167 | Highland 1 |  |  |  |  | VEN-304 | 13.0167 | KRAYN-NDX-PRT-1124 | 1 | After calling RMC and checking in put tower into manual stop nd disabled switch rights. tower was down on a fm 700 after getting up tower pinned the hub out and shut off all power to the hub off. shut breakers 102f2 and 102f3 and 101f1 and 300f1. Entered the hub and removed slip ring replaced with new one and made all conections. checked work and back to the nacel to clear tower after tower was clear unpinned the hub and let it pin wheel for 10 min and tower was good. went down tower and started turbine. tower is up and running | 700144684
KRAYN-WKO-NDX-20150106-01 | US-HIGHLAND-WEA80826 | Closed |  |  |  | 7/1/2015 | 1/6/2015 | 1/6/2015 | 1.5 | Highland 1 |  |  |  |  | VEN-304 | 5.75 | NORDX-PRT-0001 | 1 | After shutting tower down and putting into a manual stop went up tower to inspect fm172 breaker was tripped breaker did not trip until tower was back up and runnin, removed yaw skirt pieces that was ttore and hanging down. inspeceted around yaw gear and looked for any more loose skirting. went down tower and tower is running | 700144509
KRAYN-WKO-NDX-20140622-01 | FM1141 - 22WEA80830 FM1141 PitchAngle 1 | Closed |  |  |  | 1/7/2014 | 6/22/2014 | 6/23/2014 | 10.4 | Highland 1 |  |  |  |  | VEN-304 | 14.9 |  |  | Went up tower and locked out the rotor. Entered the hub to find a stud in blade 1 had broken in the #8 position. The stud and nutwere found easily. The washer was found after some searching. The internal of the hub was inspected for damage with only cosmetic damge found including chipped paint, dented cabinet doors, and slung grease. We adjusted the RED encoder in blade 1 since it hadbeen knocked out of adjustment. We then returned to the nacelle and unlocked the rotor. We started the turbien to allow for a pitch test which passed. So we manually stopped the turbien and headed down tower. We then started the turbien with no further defects noted at this time. | 800072675

## Parts
ID | Description | Qty | Vendor | Original ID
NORDX-PRT-0001 | spindle for Liftket chain hoist | 1 | Nordex | 24298
GAMSA-PRT--0045 | BOLTS PLATFORMS FLANGE | 2 | Gamesa | GP099847