## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Asset ID | Vendor ID | Actual Hours | Part ID | Part Quantity | Comments | Original ID
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-01442 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-01441 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00357 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00358 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed |  |  |  | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky |  |  |  |  | VEN-257 | 23 | SUZLN-PRT-00645 | 3 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | none
TWINR-WKO-RPW-20131107-01 | Third day of the 1st annual maintenance per Repower service manual T-2.1-GP.WA.02-A (F)-EN. yearly maintenance safety equipment annual maintenance service agreement testing equipment like chain, fire extinguisher, running, climbing aid, first aid kit, crane and/ or lift inspection The maintenance is now complete on this turbine. | Closed | Maintenance | Planned | 03-Medium | 11/7/2013 | 11/7/2013 | 11/7/2013 | 7.8833 | Twin Ridges | Planned |  | MT-113 |  | VEN-252 | 10 | REPWR-PRT-0280 | 2 |  | 60077492
TWINR-WKO-RPW-20140201-01 | T150 500hr. Rotor bolt torque. | Closed | Breakdown | Forced | 02-High | 2/1/2014 | 2/1/2014 | 2/1/2014 | 2.8333 | Twin Ridges | Unplanned | Urgent | MT-032 |  | VEN-252 | 4 |  |  |  | 30205423
TWINR-WKO-RPW-20130403-01 | ERROR 1630 Disc filter adaption implausible The poximity sensor on the high speed shaft on the generator side is faulty. We do not have any in our inventory so we will order a new one and it will have to be replaced. The turbine was reset. The turbine is up and operational at this time, but it might go down again. | Closed | Breakdown | Forced | 02-High | 4/3/2013 | 4/3/2013 | 4/3/2013 | 5.1333 | Twin Ridges | Unplanned | Urgent | MT-032 |  | VEN-252 | 2 |  |  |  | 30166618
TWINR-WKO-RPW-20140911-01 | annual maintenance | Closed | Maintenance | Planned | 03-Medium | 9/11/2014 | 9/11/2014 | 9/11/2014 | 6.46 | Twin Ridges | Planned |  | MT-113 |  | VEN-252 | 8.5 |  |  | Today on the 2nd annual maintenance we completed all the electrical portion of the maintenance, cleaned the naccel and yaw deck, and installed a refurbished autoluber (SN#644-46162-2) that had previously been deemed defective. The maintenance is now complete and the turbine is back in operation. | temp ID
KRAYN-WKO-NDX-20140622-01 | FM1141 - 22WEA80830 FM1141 PitchAngle 1 | Closed |  |  |  | 1/7/2014 | 6/22/2014 | 6/23/2014 | 10.4 | Highland 1 |  |  |  |  | VEN-304 | 14.9 |  |  | Went up tower and locked out the rotor. Entered the hub to find a stud in blade 1 had broken in the #8 position. The stud and nutwere found easily. The washer was found after some searching. The internal of the hub was inspected for damage with only cosmetic damge found including chipped paint, dented cabinet doors, and slung grease. We adjusted the RED encoder in blade 1 since it hadbeen knocked out of adjustment. We then returned to the nacelle and unlocked the rotor. We started the turbien to allow for a pitch test which passed. So we manually stopped the turbien and headed down tower. We then started the turbien with no further defects noted at this time. | 800072675

## Parts
ID | Description | Qty | Vendor | Original ID