## Sheet1
ALSTOM 38kV Dead Tank Breakers | Monthly | 3 month | 6 month | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Read and record operating counter figures | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | IB-DTO9-F1
Check the general visual appearance of switchgear: (corrosion, paint, etc.) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | IB-DTO9-F1
Check the SF6 pressure on density monitor. Top off with gas if necessary. | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | IB-DTO9-F1
Check the condition of all external hardware with calibrated torqu wrench according to TS-00007 | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | IB-DTO9-F1
Check the switch points of the SF6 density monitor and check moisture and acidity of content of gas | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Check the resistance of the amin current path | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Inspect the bushing insulators/clean and polish | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Measure the operating times of poles and auxiliary contacts, at rated voltage and pressure | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Clean the inside of the tank of any particles | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Change seals, reapply greeases and lubricants | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-DTO9-F1
Replace desiccant (and every time a pole is opened) | [22 empty] | X | IB-DTO9-F1
Replace cabinet seals | [22 empty] | X | IB-DTO9-F1
Replase the operative mechanism (only done after 10,000 operating cycles) | [23 empty] | IB-DTO9-F1
Call ALSTOM to check the condition of interrupter unit (Only done if electrical wear limit is reached) | [23 empty] | IB-DTO9-F1
ALSTTOM 145kV Dead Tank Breakers
Read and record operating counter figures | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | ID-DT12-FK
Check the general visual appearance of switchgear: (corrosion, paint, etc.) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | ID-DT12-FK
Check the SF6 pressure on density monitor. Top off with gas if necessary. | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | ID-DT12-FK
Check the condition of all external hardware with calibrated torqu wrench according to TS-00007 | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | ID-DT12-FK
Check the switch points of the SF6 density monitor and check moisture and acidity of content of gas | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Check the resistance of the amin current path | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Inspect the bushing insulators/clean and polish | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Measure the operating times of poles and auxiliary contacts, at rated voltage and pressure | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Clean the inside of the tank of any particles | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Change seals, reapply greeases and lubricants | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ID-DT12-FK
Replace desiccant (and every time a pole is opened) | [22 empty] | X | ID-DT12-FK
Replace cabinet seals | [22 empty] | X | ID-DT12-FK
Replase the operative mechanism (only done after 10,000 operating cycles) | [23 empty] | ID-DT12-FK
Call ALSTOM to check the condition of interrupter unit (Only done if electrical wear limit is reached) | [23 empty] | ID-DT12-FK
Siemens GSU
Oil sample | X |  | X
Oil Level of conservator
Check Oil level of bushings | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Power factor test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Power factor test of bushings | X | [6 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Check proper cooling fan operation | X
Check and record Winding temp. (current and max Reset) | X
Check and record oil temp. (current and max Reset) | X
Visual inspection (leaks, corrosion, etc.)
GSU corrosive sulfur test (request from oil sample lab) | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Excitation Test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Insulation Resistence test (core/ground) | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Turns ratio test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
34.5 kV disconnect switchers
Visual Inspection | X | [22 empty] | IB-AA26-001E
Check contacts for proper engagement and surface condition | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-AA26-001E
Clean and re-grease stab and finger contacts | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-AA26-001E
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
138kV disconnect switches
Visual Inspection | X | [22 empty] | IB-AA26-301L
Check contacts for proper engagement and surface condition | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-AA26-301L
Clean and re-grease stab and finger contacts | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | IB-AA26-301L
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Neutral Grounding Reactor
Visually inspect for paint deterioration and pollution accumulation | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | Alstom manual 11622 4th edition
EATON ATS Transfer switch
Visually Inspect | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | O&M manual for ATC-300 2-Position
138 kV CCVT's
Visually inspect | X
Capacitance test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
Power Factor test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
34.5 kV Voltage Transformers
Visually inspect | X | [22 empty] | Instruction Manual IL-VEFS-R4
Power Factor test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | Instruction Manual IL-VEFS-R5
Insulation test | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | Instruction Manual IL-VEFS-R6
Clean and silicone | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | Instruction Manual IL-VEFS-R7
Grounding Transformers
Visually inspect | X
Oil sample | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
138 kV insulators
Visually inspect | X
Clean and polish | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
34.5 kV insulators
Visually inspect | X
Clean and polish | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X
F-11 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
F-12 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
F-13 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
F-15 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
F-16 Feeder Relay (SEL-351S)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
87T Relay (SEL-387)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
87B Relay (SEL-5872)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
TP Relay (SEL-351)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
Line Relay (SEL-311A)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
Line Relay (SEL-311L)
Visually check LED function/Fault indicators (download any new events)/Clean Front panel | X
Visually inspect for loose connections (rainbowing) | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
Perform inspection and test procedures as per ANSi/NETA MTS-2011 section 7.9.2 | [7 empty] | X |  |  |  |  | X |  |  |  |  | X |  |  |  |  | X | ANSi/NETA MTS-2011 section 7.9.2
Battery Bank
Montly battery bank/Pilot cell checks | X | [22 empty] | See monthly inspection checklist
Quarterly batter bank checks |  | X | [21 empty] | See quarterly inspection checklist
Annual batter bank checks | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | See annual inspection checklist
Battery Charger
Complete needed checks as per AT10.1 operation manual |  |  | X | [20 empty] | AT10.1 series operation manual
Ion Revenue Meter
Caliberate meter | [6 empty] | X |  | X |  | X |  | X |  | X |  | X |  | X |  | X |  | X
Bus work/Current carrying connections
Visually inspect | X
IR Scan | [5 empty] | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X