## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Task Description | Asset ID | Asset Description | Vendor ID | Vendor Name | Actual Hours | Part ID | Part Description | Part Quantity | Comments | Original ID
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG117 | Big Sky WTG-117 | VEN-257 | Suzlon | 23 | SUZLN-PRT-01442 | BALL BEARING INSOCOAT 6328MC3VL2076 SKF | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | None
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG117 | Big Sky WTG-117 | VEN-257 | Suzlon | 23 | SUZLN-PRT-01441 | BALL BEARING INSOCOAT 6332MC3VL2076 SKF | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | None
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG117 | Big Sky WTG-117 | VEN-257 | Suzlon | 23 | SUZLN-PRT-00357 | GR RETAINING DISC DE 6181087 R0 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | None
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG117 | Big Sky WTG-117 | VEN-257 | Suzlon | 23 | SUZLN-PRT-00358 | GR RETAINING DISC NDE 6181093 R0 | 1 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | None
BGSKY-WKO-SUZ-20150701-01 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG117 | Big Sky WTG-117 | VEN-257 | Suzlon | 23 | SUZLN-PRT-00645 | GREASE KLUBERPLEX BEM 41-132 | 3 | Climbed tower and finished up and completed DE and NDE bearings replacement and generator alignment. | None
BGSKY-WKO-SUZ-20150701-02 | Tower faulted on Rep_Pitch_EmergencyRun, we noticed that blade two had hit the one hundred degree switch again. Climbed tower and locked out the rotor. Went to the hub and changed two jumpers inside the encoder box for the limit switches. We also found that the brake cable for blade two was worn through so we replaced that as well. Ran a battery test and returned tower to operation. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG058 | Big Sky WTG-058 | VEN-257 | Suzlon | 11 | SUZLN-PRT-00699 | CABLEPVC 3G16AWG 0011187 OLFL191CY LAPP | 3 | Tower faulted on Rep_Pitch_EmergencyRun, we noticed that blade two had hit the one hundred degree switch again. Climbed tower and locked out the rotor. Went to the hub and changed two jumpers inside the encoder box for the limit switches. We also found that the brake cable for blade two was worn through so we replaced that as well. Ran a battery test and returned tower to operation. | None
BGSKY-WKO-SUZ-20150701-03 | Tower had been faulting on Elec_CutintoG1_TimeOutStop. Went to tower and had EverPower kill the PMT. Once we confirmed there was no voltage in the power cabinet we changed out the softstarter card. Once we finished we had EverPower close the PMT and then ran a motor test and everything seemed normal. Cleared alarms and returned tower to operation. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0.5 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG061 | Big Sky WTG-061 | VEN-257 | Suzlon | 4 | SUZLN-PRT-01153 | CTRL/DRIVER BOARD 1081AE02 S02232 IXYS | 1 | Tower had been faulting on Elec_CutintoG1_TimeOutStop. Went to tower and had EverPower kill the PMT. Once we confirmed there was no voltage in the power cabinet we changed out the softstarter card. Once we finished we had EverPower close the PMT and then ran a motor test and everything seemed normal. Cleared alarms and returned tower to operation. | None
BGSKY-WKO-SUZ-20150701-04 | Turbine faulted on safety chain stop. Went and reset the safety chain down tower and returned the turbine to system ok. | Closed | General Maintenance | Planned | 03-Medium | 7/1/2015 | 7/1/2015 | 7/1/2015 | 0.66667 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG096 | Big Sky WTG-096 | VEN-257 | Suzlon | 4 |  |  |  | Turbine faulted on safety chain stop. Went and reset the safety chain down tower and returned the turbine to system ok. | None
BGSKY-WKO-SUZ-20150702-01 | Cleaned grease ouf of NDE generator bearing cover. Returned the turbine to system ok. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 3 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG010 | Big Sky WTG-010 | VEN-257 | Suzlon | 5 |  |  |  | Cleaned grease ouf of NDE generator bearing cover. Returned the turbine to system ok. | None
BGSKY-WKO-SUZ-20150702-02 | Cleaned grease out of NDE generator bearing cover. Returned the turbine to system ok. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 1.75 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG012 | Big Sky WTG-012 | VEN-257 | Suzlon | 5 |  |  |  | Cleaned grease out of NDE generator bearing cover. Returned the turbine to system ok. | None
BGSKY-WKO-SUZ-20150702-03 | 100% tower torque. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 5 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG015 | Big Sky WTG-015 | VEN-257 | Suzlon | 18 |  |  |  | 100% tower torque. | None
BGSKY-WKO-SUZ-20150702-04 | 100% tower torque. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 1.5833 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG019 | Big Sky WTG-019 | VEN-257 | Suzlon | 18 |  |  |  | 100% tower torque. | None
BGSKY-WKO-SUZ-20150702-05 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 1.25 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG030 | Big Sky WTG-030 | VEN-257 | Suzlon | 4 | SUZLN-PRT-00189 | CAPACITOR CAP TYPE:PHMKPG660.3.22,90 | 42 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | None
BGSKY-WKO-SUZ-20150702-05 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 1.25 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG030 | Big Sky WTG-030 | VEN-257 | Suzlon | 4 | SUZLN-PRT-01138 | FUSE CLASS J 50A/600VAC UL | 1 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | None
BGSKY-WKO-SUZ-20150702-05 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 1.25 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG030 | Big Sky WTG-030 | VEN-257 | Suzlon | 4 | SUZLN-PRT-01280 | FUSE CLASS J 90A/600VAC UL | 1 | Tower had faulted on Elec_ReactivPower_HighStop. Went to tower and opened 8Q2. We then checked all the capacitors and found that all 42 were bad. We also replaced one 90 amp fuse and one 50 amp fuse. We then closed 8Q2 and reset alarms and returned turbine to operation. | None
BGSKY-WKO-SUZ-20150702-06 | Corrected punchlist items from the service last Friday. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 3 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG045 | Big Sky WTG-045 | VEN-257 | Suzlon | 9 | SUZLN-PRT-00062 | FILTER MAT CABINET 221X221MM SK3172.100 | 4 | Corrected punchlist items from the service last Friday. | None
BGSKY-WKO-SUZ-20150702-06 | Corrected punchlist items from the service last Friday. | Closed | General Maintenance | Planned | 03-Medium | 7/2/2015 | 7/2/2015 | 7/2/2015 | 3 | Big Sky | Planned |  | MT-052 | General Maintenance | BGSKY-WTG045 | Big Sky WTG-045 | VEN-257 | Suzlon | 9 | SUZLN-PRT-00926 | TUBE LIGHT 11W120VAC60HZ 02524.0-01STEGO | 2 | Corrected punchlist items from the service last Friday. | None