## Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Task Description | Asset ID | Asset Description | Vendor ID | Vendor Name | Actual Hours | Part ID | Part Description | Part Quantity | Comments | Original ID
TWINR-WKO-RPW-20140829-03 | autoluber investigate | Closed | Warranty Repair | Forced | 03-Medium | 8/29/2014 | 8/29/2014 | 8/29/2014 | 5.09 | Twin Ridges | Planned |  | MT-052 | General Maintenance | TWINR-WTG10 | MM92/80 92212 | VEN-252 | Senvion | 4.5 | REPWR-PRT-0286 | Lubrication plant | 1 | Pitch bearing Autoluber Investigation to indicate problem. Found that the power card was blown, also found that internally the autoluber plunger which applies downforce to the grease in the resirvour was not square. This was allowing the resivour grease to bypass the plunger which is not how the luber is designed. Due to this, it was necessary to replace the faulty Lincoln Pitch bearing autoluber for internal defect. Also replaced the autoluber power card. We replaced the defective autoluber and tested, it is working ok. | None
TWINR-WKO-RPW-20140829-03 | autoluber investigate | Closed | Warranty Repair | Forced | 03-Medium | 8/29/2014 | 8/29/2014 | 8/29/2014 | 5.09 | Twin Ridges | Planned |  | MT-052 | General Maintenance | TWINR-WTG10 | MM92/80 92212 | VEN-252 | Senvion | 4.5 | REPWR-PRT-1513 | power supply card 110-230VAC Lincoln | 1 | Pitch bearing Autoluber Investigation to indicate problem. Found that the power card was blown, also found that internally the autoluber plunger which applies downforce to the grease in the resirvour was not square. This was allowing the resivour grease to bypass the plunger which is not how the luber is designed. Due to this, it was necessary to replace the faulty Lincoln Pitch bearing autoluber for internal defect. Also replaced the autoluber power card. We replaced the defective autoluber and tested, it is working ok. | None

## Flagged Work Orders
ID | Description | Status | Type | Outage Type | Priority | Date Opened | Start Date | Date Done | Down Time | Site | Planning | Unplanned Type | Task ID | Task Description | Asset ID | Asset Description | Vendor ID | Vendor Name | Actual Hours | Part ID | Part Description | Part Quantity | Comments | Original ID
TWINR-WKO-RPW-20140829-02 | heater inspect | Closed | Retrofit | Forced | 03-Medium | 8/29/2014 | 8/29/2014 | 8/29/2014 | 2.24 | Twin Ridges | Planned |  | MT-052 | General Maintenance | TWINR-WTG08 | MM92/80 91934 | VEN-252 | Senvion | 0.5 |  |  |  | WTI431 SSB Pitch box heater inspection - no abnormalities to report, return sheet filed | None
TWINR-WKO-RPW-20140829-01 | hoist replace | Closed | Preventive Maintenance | Planned | 03-Medium | 8/29/2014 | 8/29/2014 | 8/29/2014 | 2.24 | Twin Ridges | Planned |  | MT-113 | Planned Maintenance | TWINR-WTG08 | MM92/80 91934 | VEN-252 | Senvion | 4 | REPWR-PRT-1517 | Pt100 BEARING HSS RS | 1 | Replacement of hoist QM 5048682 | None